SECTION 16141

RECESSED OUTLET POKE-THRU DEVICES

GENERAL

CONDITIONS AND REQUIREMENTS

The General Conditions, Supplementary Conditions, and Division 1 – General Requirements apply.

SECTION INCLUDES

Specifier Note:  Delete items below that are not included in this section.

Recessed outlet poke-thru devices.

[Insert item description.]

RELATED SECTIONS

Specifier Note:  In this article, specify work specified in other sections that is related to work of this section.

Section 07841 - Through-Penetration Firestop Systems.

Section 13700 - Security Access and Surveillance:  Security systems and components.

Division 16 - Electrical:  Electrical systems and components.

Section 16700 - Communications:  Communications systems and components.

Specifier Note:  The following paragraph is a sample that may be used in this article.  Add to or delete from the following as appropriate for the specific project.

Section [xxxxx] – [Section Title]:  [Include brief description of work specified in another section that is related to the work of this section.]

SUBMITTALS

Specifier Note:  In this article, specify various types of data to be furnished by the contractor before, during, or after construction. Topics included in this article are:  product data, shop drawings, samples, design data, test reports, certificates, manufacturers’ instructions, manufacturers’ field reports, qualification statements, and closeout submittals.

Submit under provisions of Section [01330] [______].

Product Data:  Submit for recessed outlet poke-thru systems.

Shop Drawings:  For the following electrical system components.  Include plans, elevations, sections, details, and attachments to other work.

Poke-thru assemblies.

Specifier Note:  Delete one of the options in the following paragraph.

Samples:  Submit [one (1)] [insert quantity] sample(s) with required color and finish.  Show standard color ranges available.

QUALITY ASSURANCE

Specifier Note:  In this article, describe qualifications, regulatory requirements, certifications, field samples, mock-ups, and pre-installation meetings.

Manufacturers:  Firms regularly engaged in manufacture of poke-thru devices and fittings of the types and sizes required, whose products have been in satisfactory use in similar service for not less than 10 years.  Provide poke-thru devices produced by a manufacturer listed in this section.

Source Limitations:  Obtain each type of poke-thru device through one (1) source from a single manufacturer.

Electrical Poke-Thru Devices and Components:  Comply with requirements of applicable local codes, NEC, UL, and NEMA Standards pertaining to poke-thru devices and components.  Listed and labeled in accordance with NFPA 70, Article 100.

Accessibility Compliance:  Design device flange to meet ADA Accessibility Guidelines as to changes in floor and ground surface levels.  Flanges shall be beveled so the slope is no greater than 1:2.

DELIVERY, STORAGE AND HANDLING

Deliver poke-thru devices and components in factory labeled packages.

Store and handle in strict compliance with manufacturer’s written instructions and recommendations.

Protect from damage due to weather, excessive temperature, and construction operations.

PRODUCTS

MANUFACTURERS

Basis-of-Design Product:  The design for recessed outlet poke-thru devices is based on Evolution™ Series Poke-Thru Devices manufactured by Legrand/Wiremold, 60 Woodlawn Street, West Hartford, CT 06110; toll-free 800-621-0049, telephone 860-233-6251, fax 860-232-2062; Web Site: www.legrand.us/wiremold.

Substitutions will be considered under provisions of Section 01635.

RECESSED OUTLET POKE-THRU DEVICES

Specifier Note:  In the following paragraph, retain only those products that are to be incorporated into the project and delete the others.

Recessed Outlet Poke-Thru Devices:  [6AT] [8AT] [10AT] Poke-Thru Devices manufactured by Legrand/Wiremold.

Poke-thru devices provide an interface between power, communication and audio/visual (A/V) cabling in an above grade concrete floor and the workstation or activation location where power, communication and/or A/V device outlets are required.  These devices provide recessed device outlets that will not obstruct the floor area.  Refer to the Drawings for types.

Poke-thru devices shall be compatible with the complete line of Ortronics® workstation connectivity outlets and modular inserts, Wiremold’s CM open system adapters, or a variety of audio/video devices from most manufacturers, and other open system devices.

Specifier Note:  Poke-thru device use is limited by the UL Fire Resistance Directory to a minimum spacing of 2 feet (610mm) on center and not more than one device per 65 square feet (6m2) of floor area in each span.

Classification and Use:  Poke-thru device shall have been examined and tested by Underwriters Laboratories Inc. to comply with UL514A and/or UL514C and Canadian Standard C22.2, No. 18-98 and bear the U.S. and Canadian UL Listing Mark.  Poke-thru device shall also have been tested by UL and classified for fire resistance and bear the U.S. and Canadian UL Classification Mark.  The poke-thru device shall conform to the standards set in the National Electrical Code, Section 300-21.

Poke-thru devices shall be classified for use in 1, 1-1/2, or 2-hour rated floors and 1, 1-1/2, or 2 hour rated floors employing unprotected steel floor units and concrete toppings (D900 Series designs), or concrete floors with suspended ceilings.  Fire resistive designs with suspended ceilings shall have provisions for accessibility in the ceiling below the poke-thru device fittings.

Poke-thru device shall have been evaluated by UL to meet the applicable U.S. and Canadian safety standards for scrub water exclusion when used on tile, terrazzo, wood, and carpet covered floors.

These devices are not suitable for wet or damp locations, or other areas subject to saturation with water or other liquids such as commercial kitchens.

Poke-thru device shall be suitable for use in air handling spaces in accordance with Section 300-22C of the National Electrical Code.

Specifier Note:  In the following paragraph, retain only those products that are to be incorporated into the project and delete the others.

6AT Poke-Thru Assembly:  Poke-thru device assemblies shall consist of an insert and an activation cover.  Assembly length:  16-3/4 inches (425mm).

Insert:  Insert body shall recess the devices a minimum of 2-3/4 inches (69mm) and have a polyester based backing enamel finished interior; ivory color.  Furnish with necessary channels to provide complete separation of power and communication services.  Provide three (3) compartments that allow for up to three (3) duplex receptacles that can be wired as a standard receptacle or isolated ground and/or 12 communication ports and/or 10 Legrand AVIP AV devices or 10 Extron® Electronics MAAP™ and/or two AAP™ devices.

Body consists of an intumescent firestop material to maintain fire rating of the floor slab.  Hold intumescent material securely in place in insert body.  Intumescent material will not have to be adjusted to maintain fire rating of the unit and the floor slab.  Provide insert with a retaining feature to hold the poke-thru device in the floor slab without additional fasteners.  Poke-thru insert shall also consist of a 3/4-inch trade size conduit stub that is connected to the insert body and a 24.5 cu in (402ml) stamped steel junction box for wire splicing and connections.  Stamped steel junction box shall also contain the means necessary to electrically ground the poke-thru device to the system ground.

Specifier Note:  Select either the powder-coated or plated finish in the following subparagraph and delete the other finish.

Activation Cover:  Manufactured of die-cast aluminum alloy; finished in powder-coated [gray] [black] [brass] [nickel] [bronze].  Provide with two (2) gaskets (one (1) for surface and one (1) for flush) to go under the trim flange to maintain scrub water tightness.  Activation cover is 7-1/4 inches (184mm) in diameter.  Provide cover with spring-loaded slides to allow cables to egress out of the unit and maintain as small an egress opening as possible.

Communication Modules Mounting Accessories:  Provide activation unit with three locations to mount communication connectors.  Mount connectors using a mounting bracket capable of accepting up to 12 Ortonics® TracJack™ Category 6 insert modules or TechChoice™ Category 6 discrete keystone connectors.  Also provide unit with two (2) Category 6 discrete keystone connectors and two (2) industry standard keystones and accommodate a mechanism to permit protection of communication cabling.  Fabricate mechanism from stamped steel construction.  Mechanism shall accept both flexible and rigid 3/4-inch, 1-1/4-inch or two-inch trade size conduit.

Specifier Note:  In the following paragraph, retain only those products that are to be incorporated into the project and delete the others.

8AT Poke-Thru Assembly:  Poke-thru device assemblies shall consist of an insert and an activation cover.  Assembly length:  16-3/4 inches (425mm).

Insert:  Insert body shall recess the devices a minimum of 2-3/4 inches (69mm) and have a polyester based backing enamel finished interior; ivory color.  Furnish with necessary channels to provide complete separation of power and communication services.  Provide five (5) compartments that allow for up to five (5) duplex receptacles that can be wired as a standard receptacle or isolated ground and/or 22 communication ports and/or 16 Legrand AVIP AV devices or 16 Extron® Electronics MAAP™ and/or four (4) AAP™ devices.

Body consists of an intumescent firestop material to maintain fire rating of the floor slab.  Hold intumescent material securely in place in insert body.  Intumescent material will not have to be adjusted to maintain fire rating of the unit and the floor slab.  Provide insert with a retaining feature to hold the poke-thru device in the floor slab without additional fasteners.  Poke-thru insert shall also consist of a 3/4-inch trade size conduit stub that is connected to the insert body and a 24.5 cu in (402ml) stamped steel junction box for wire splicing and connections.  Stamped steel junction box shall also contain the means necessary to electrically ground the poke-thru device to the system ground.

Specifier Note:  Select the desired color of powder-coated finish in the following subparagraph and delete the other colors.

Activation Cover:  Manufactured of die-cast aluminum alloy; finished in powder-coated [gray] [black] [brass] [nickel] [bronze].  Provide with two (2) gaskets (one (1) for carpet and one (1) for tile) to go under the trim flange to maintain scrub water tightness.  Activation cover is 9-1/4 inches (235mm) in diameter.  Provide cover with spring-loaded slides to allow cables to egress out of the unit and maintain as small an egress opening as possible.

Communication Modules Mounting Accessories:  Provide activation unit with three locations to mount communication connectors.  Mount connectors using a mounting bracket capable of accepting up to 12 Ortonics® TracJack™ Category 6 insert modules or TechChoice™ Category 6 discrete keystone connectors.  Also provide unit with two (2) Category 6 discrete keystone connectors and two (2) industry standard keystones and accommodate a mechanism to permit protection of communication cabling.  Fabricate mechanism from stamped steel construction.  Mechanism shall accept both flexible and rigid 3/4-inch, 1-1/4-inch or two-inch trade size conduit.

Specifier Note:  In the following paragraph, retain only those products that are to be incorporated into the project and delete the others.

6AFF Poke-Thru Assembly:  Poke-thru device assemblies shall consist of an insert and an activation cover.  Assembly length:  16-3/4 inches (425mm).

Insert:  Insert body shall have the necessary channels to provide complete separation of power and communication services.  Provide two (2) channels that allow up to 10 #10 AWG conductors in the power channel and 28 Category 6A data cables in the communication channel.

Body consists of an intumescent firestop material to maintain fire rating of the floor slab.  Hold intumescent material securely in place in insert body.  Intumescent material will not have to be adjusted to maintain fire rating of the unit and the floor slab.  Provide insert with a retaining feature to hold the poke-thru device in the floor slab without additional fasteners.  Poke-thru insert shall also consist of a 3/4-inch trade size conduit stub that is connected to the insert body and a 24.5 cu in (402ml) stamped steel junction box for wire splicing and connections.  Stamped steel junction box shall also contain the means necessary to electrically ground the poke-thru device to the system ground.

Specifier Note:  Select the desired color of powder-coated finish in the following subparagraph and delete the other colors.

Activation Cover:  Manufactured of die-cast aluminum alloy; finished in powder-coated [gray] [black] [brass] [nickel] [bronze].  Provide with two (2) gaskets (one (1) for carpet and one (1) for tile) to go under the trim flange to maintain scrub water tightness.  Activation cover is 7-3/4 inches (196mm) in diameter.  Provide cover with one (1) 3/4-inch (19.05mm) trade size opening for power and one (1) 1-1/4-inch/2-inch (31.75/50.8mm) combination trade size opening for communications.

Provide surface mounted activation cover that accommodates a carpet floor finish.

Specifier Note:  In the following paragraph, retain only those products that are to be incorporated into the project and delete the others.

10AT Poke-Thru Assembly:  Poke-thru device assemblies shall consist of an insert and an activation cover.  Assembly length:  11-3/4 inches (286mm).

Insert:  Insert body shall recess the devices a minimum of 4-1/2 inches (114mm) and have a polyester based backing enamel finished interior; ivory color.  Furnish with necessary channels to provide complete separation of power, communication, and audio/video (A/V) services.  Provide eight (8) compartments (four (4) internal and four (4) external) that allow for up to eight (8) duplex receptacles that can be wired as a standard receptacle or isolated ground and/or 32 communication ports and/or 24 Legrand AVIP A/V devices or 24 Extron® Electronics MAAP™ and/or eight (8) AAP™ devices.  The four (4) internal compartments shall have a volume of 19 cu in (311ml) each.  The four (4) external compartments shall have a minimum volume of 14 cu in (232ml) each.

Body consists of an intumescent firestop material to maintain fire rating of the floor slab.  Hold intumescent material securely in place in insert body.  Intumescent material will not have to be adjusted to maintain fire rating of the unit and the floor slab.  Provide insert with a retaining feature to hold the poke-thru device in the floor slab without additional fasteners.  Poke-thru insert shall also consist of a 3/4-inch trade size conduit stub that is connected to the insert body to feed the power services.  The intumescent body shall be listed and classified as an electrical enclosure allowing for electrical connections to be made within the poke-thru body without the need for an external junction box.

Specifier Note:  Select either the powder-coated, plated or satin chrome finish in the following subparagraph and delete the other finishes.

Activation Cover:  Manufactured of die-cast aluminum alloy; finished in [powder-coated [gray] [black] [bronze] [brass] [nickel] [aluminum]] [satin brass-plating] [satin chrome-plating].  Provide with two (2) gaskets (one (1) for carpet and one (1) for tile) to go under the trim flange to maintain scrub water tightness.  Activation cover is 11-1/4 inches (283mm) in diameter.  Provide cover with spring-loaded slides to allow cables to egress out of the unit and maintain as small an egress opening as possible.

Specifier Note:  Select either of the following subparagraphs and delete the other one.

[Provide surface mounted activation cover that accommodates a carpet floor finish.]

[Provide flush activation cover that accommodates a tile floor finish.]

Communication Modules Mounting Accessories:  Provide activation unit with three (3) locations to mount communication connectors.  Mount connectors using a mounting bracket capable of accepting up to 32 Ortonics® TracJack™ Category 6 insert modules or TechChoice™ Category 6 discrete keystone connectors.  Also provide unit with two (2) Category 6 discrete keystone connectors and two (2) industry standard keystones and accommodate a mechanism to permit protection of communication cabling.  Fabricate mechanism from stamped steel construction.  Mechanism shall accept both flexible and rigid 3/4-inch, 1-1/4-inch or two-inch trade size conduit.

Copper Wire Cross Sectional Area:

| Copper Cross Sectional Area of Commonly Used Conductors |
| --- |
| Size | Solid or Stranded |
| #24 | .00032 sq in (.206mm2) |
| #22 | .00050 sq in (.322mm2) |
| #14 | .00323 sq in (2.083mm2) |
| #12 | .00512 sq in (3.303mm2) |
| #10 | .00815 sq in (5.258mm2) |
| #8 | .01296 sq in (8.361mm2) |

Maximum copper cross sectional area for 6AT outer compartment only is .0154 sq in (9.9mm2).  Maximum copper cross sectional area for the center compartment only is .0387 sq in (24.9mm2).

Maximum copper cross sectional area for 6ATCFF power compartment only is .0815 sq in (52.6mm2).  Maximum copper cross sectional area for the center communication compartment only is .0686 sq in (44.3mm2).  The maximum copper cross sectional area for the outside communication compartment only is .0187 sq in (12.1mm2).

Maximum copper cross sectional area for 8AT outer compartment only is .0154 sq in (9.9mm2).  Maximum copper cross sectional area for the center compartment only is .0775 sq in (16.6mm2).

Maximum copper cross sectional area for 10AT outer compartment only is .0288 sq in (18.6mm2).  Maximum copper cross sectional area for the center compartment only is .0960 sq in (61.9mm2).

EXECUTION

EXAMINATION

Specifier Note:  Select either option in the following paragraph and delete the other one.

Examine conditions under which poke-thru devices, accessories, and fittings are to be installed.  Notify the [Architect/Engineer] [Construction Manager] in writing of conditions detrimental to proper completion of the work.  Do not proceed with work until unsatisfactory conditions have been corrected.

INSTALLATION

Strictly comply with manufacturer's installation instructions and recommendations and approved shop drawings.  Coordinate installation with adjacent work to ensure proper clearances and to prevent electrical hazards.

Mechanical Security:  Raceway systems shall be mechanically continuous and connected to all electrical outlets, boxes, device mounting brackets, and cabinets, in accordance with manufacturer’s installation sheets.

Electrical Security:  Metal raceway shall be electrically continuous and bonded in accordance with the National Electric Code for proper grounding.

Raceway Support:  Raceway shall be supported at intervals not exceeding 5 feet or in accordance with manufacturer’s installation sheets.

Accessories:  Provide accessories as required for a complete installation, including insulated bushings and inserts where required by manufacturer.

Unused Openings:  Close unused raceway openings using manufacturer's recommended accessories.

Install unit to permit all wiring to be completed at floor level.

Specifier Note:  In the following paragraph, retain products that are to be incorporated into the project and delete the others.

Mount the [6AT and 6ATCFF units in a 6-1/16-inch (154mm) cored hole] [8AT units in an 8-1/16-inch (205mm) cored hole] [10AT units in a 10-1/16-inch (267mm) cored hole].

Complete unit installation by pushing it down into the cored hole.

CLEANING AND PROTECTION

Clean exposed surfaces using non-abrasive materials and methods recommended by manufacturer.

Protect poke-thru devices until acceptance.

END OF SECTION

© 2015 Legrand/Wiremold.  All Rights Reserved.

A copyright license to reproduce this specification is hereby granted

to non-manufacturing engineers, architects and specification writers.

Rev 09/15