www.wattstopper.com

800.879.8585

WS-08-11701

www.wattstopper.com

800.879.8585

## SPECIFICATIONS

UT-300

UT-305

UT-355

- The occupancy sensors shall be capable of detecting presence in the control area via Doppler shifts in transmitted ultrasound.

- Sensors shall use Watt Stopper’s patented ultrasonic diffusion technology that spreads coverage to a wider area.

- Ultrasonic sensing shall be volumetric in coverage with a frequency of 40 KHz. It shall utilize Advance Signal Processing, which automatically adjusts the detection threshold dynamically to compensate for constantly changing levels of activity and airflow throughout controlled space.

- To avoid false on activation and to provide immunity to RFI and EMI, Detection Signature Analysis shall be used to examine the frequency, duration, and amplitude of a signal so as to only respond to those signals caused by human motion.

- Sensors of varying frequencies shall not be allowed so as to prevent sensors from interfering with each other and to assure compatibility in the event more sensors are added.

- UT-300 and UT-305 sensors shall operate at 24 VDC/VAC and half-wave rectified and utilize a Watt Stopper power pack.

- UT-355 shall incorporate a switching power supply for reduced power consumption; operate at 120/230/277/347 VAC, 50/60 HZ; and not require a power pack.

- Detection shall be maintained only when a person of average size and weight moves within a maximum distance of twelve inches horizontally or vertically at the approximate speed of 12 inches per second. The sum of this distance, volume and speed represents the average condition ultrasonic sensors must meet so that the lights not go off when a person is reading or writing while seated at a desk.

- The UT-300 and UT-305 sensors shall have a manual-on function that is facilitated by installing a momentary switch.

- Sensors shall be mounted to the ceiling with a flat, unobtrusive appearance and provide 360° of coverage.

- Sensors shall utilize SmartSetTM technology that automatically adjusts time delay settings to fit occupants’ usage patterns for optimal energy efficiency. SmartSet feature shall be selectable with a DIP switch. Sensor shall have user-adjustable sensitivity setting.

- Sensor shall feature a walk-through mode that turns lights off three minutes after the area is initially occupied if no motion is detected after the first 30 seconds.

- Sensors shall cover 360° and walking motion up to 500 square feet for UT-300-1/UT-305-1/UT-355-1, 1000 square feet for UT-300-2/UT-305-2/UT-355-2, and 2000 square feet for UT-300-3/UT-305-3/UT-355-3.

- Hallway and corridor sensors shall be a UT-300-3/UT-305-3/UT-355-3 and shall cover 45 feet in each direction for a ten-foot wide walled hallway.

- UT-300 sensor shall have an additional single-pole, double throw isolated relay with normally open, normally closed, and common outputs. The isolated relay shall be for use with HVAC control, data logging, and other control options.

- Sensors shall have a DIP switch-adjustable time delay of five to 30 minutes.

- Sensors shall feature terminal style wiring for easier installation.

- The sensor shall have a constantly active LED indicator to verify detection within the control area. Disabling LED for applications that requires less visibility shall be possible.

- To ensure quality and reliability, sensor shall be manufactured by an ISO 9002-certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Sensor shall have standard five-year warranty and shall be UL and CUL listed.

### UT-300 Ultrasonic Occupancy Sensors