www.wattstopper.com

800.879.8585

BZ-50

WS-07-28301

www.wattstopper.com

800.879.8585

## SPECIFICATIONS

- Power pack shall be a self-contained power supply and relay module measuring 1.6" x 2.75" x 1.6" (40.6mm x 69.9mm x 40.6mm) H x W x D.

- For ease and speed of installation, power pack shall have a 1/2" snap-in nipple for 1/2" knockouts and mounting on outside of enclosure.

- Power pack shall have dry contacts capable of switching 20-amp ballast and incandescent load @ 120 VAC, 60 Hz; 20-amp ballast @ 277 VAC, 60 Hz; 1 hp @ 120-250 VAC, 60Hz.

- Power pack shall have primary voltage and frequency inputs of 120/230/277 VAC, 50/60Hz.

- Power pack shall provide a 24 VDC, 225 mA output with the relay connected.

- Power pack shall provide 14 AWG wires for reliable 20A operation.

- Power pack shall be capable of parallel wiring without regard to AC phases on primary.

- Power pack can be used as a stand-alone, low-voltage switch, or can be wired to sensor for auto control.

- Power pack shall have an LED to indicate status of relay.

- Power pack shall have over-current protection if the low voltage current drawn exceeds 225 mA. In the event of an over-current, the low voltage +24VDC output shuts down to prevent permanent damage and the LED will blink continuously to indicate a fault condition.

- Power pack shall be UL 2043 plenum rated and shall have low-voltage Teflon-coated leads rated for 300 volts.

- Power pack shall utilize zero crossing circuitry to protect from the effects of in-rush current and increase product longevity.

- To be environmental friendly, power pack shall use lead-free material and be RoHS- compliant.

- To ensure quality and reliability, power pack shall be manufactured by an ISO 9002-certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Power pack shall have a five-year warranty.

- Power pack shall be UL and CUL listed.

### BZ-50 Universal Voltage Power Pack