www.wattstopper.com

800.879.8585

- The digital time switch shall be programmable to turn lights off after a preset time.

- Time switch shall be a completely self-contained control system that replaces the standard toggle switch. It shall have a ground wire and ground strap for safety. Switching mechanism shall be a latching air gap relay.

- Zero Crossing Circuitry shall be used to increase the relay life, protect from the effects of inrush current, and increase the switch’s longevity.

- Time switch shall be compatible with all electronic ballasts, motor loads, compact fluorescent and inductive loads. Triac and other harmonic generating devices shall not be allowed.

- Time switch shall operate at universal voltages of 100-300 VAC; 50/60 Hz.

- Time switch shall have no minimum load requirement and shall be capable of controlling 0 to 800 watt incandescent, fluorescent @ 100/120 VAC, 50/60 Hz; 0 to 1200 watts fluorescent @ 230/277 VAC, 50/60 Hz; 1/6 hp @ 125 VAC.

- Time scroll feature shall allow manual overriding of the preset time-out period. Selecting time scroll UP shall allow time-out period to scroll up throughout the timer possibilities to the maximum. Time scroll DN (down) shall allow time-out period to scroll down to minimum.

- Time switch shall have the option for a one second light flash warning at five minutes before the timer runs out and twice when the countdown reaches one minute (when used to control lighting loads).

- Time switch shall have the option for a beep warning that shall sound every five seconds once the time switch countdown reaches one minute.

- Time switch shall have manual feature for timer reset where pressing the ON/OFF switch for more than 2 seconds resets the timer to the programmed time-out period.

- Time switch shall have an electroluminescent backlit Liquid Crystal Display that shows the timer’s countdown.

- Time switch shall fit behind a decorator style faceplate. The calibration switch for setting time-out, time scroll, one second light flash, and beep warning shall be concealed to prevent tampering of adjustments and hardware.

- Time-out period shall be adjustable in increments of 5 minutes from 5 minutes to 1 hour, and in increments of 15 minutes from 1 hour to 12 hours.

- Time switch shall be capable of operating as an ON/OFF switch.

- For ease of installation and cleaner wiring, the switch shall utilize terminal style wiring.

- The time switch shall not protrude more than 1/8” from the wall and should blend in aesthetically.

- For safety, the time switch shall have a 100% OFF override switch with no leakage current to the load.

- For safety, in the event there is an open circuit in the AC line such as a ballast or lamp failure, the time switch shall automatically switch to OFF mode.

- To ensure quality and reliability, time switch shall be manufactured by an ISO 9002 certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Time switch shall have 5 year warranty and shall be UL and CUL listed.

www.wattstopper.com

800.879.8585

## SPECIFICATIONS

#### TS-400

#### TS-400 Digital Time Switch

TS4001204