www.wattstopper.com

800.879.8585

www.wattstopper.com

800.879.8585

## SPECIFICATIONS

CI-300

CI-305

CI-355

- The passive infrared sensor shall be capable of detecting presence in the control area by detecting changes in the infrared energy. Small movements shall be detected such as when a person is writing while seated at a desk within an 8 feet radius of the sensor.

- To avoid false ON activations and to provide immunity to RFI and EMI, Digital Signature Analysis shall be used to examine the frequency, duration, and amplitude of a signal, to respond only to those signals caused by human motion.

- Sensors shall utilize SmartSet technology to optimize time delay and sensitivity settings to fit occupants usage patterns. The use of SmartSet shall be selectable with a DIP switch.

- Sensors shall be mounted to the ceiling with a flat, unobtrusive appearance and provide 360° of coverage.

- Sensor shall utilize a temperature compensated dual element sensor and a multi-element Fresnel lens. Fresnel lens shall be a Poly IR 4 based material to offer superior performance in the Infrared wavelengths and filter short wavelength infrared, such as those emitted by the sun and other visible light sources. Lens shall have grooves facing in to avoid dust and residue build up which affects IR reception.

- The sensors shall feature terminal style wiring, which makes installation easier.

- To ensure sensitivity to small motion at the desktop, the sensor shall have a 34 element Extended Range lens (standard) or a 55 element High Density lens.

- Sensor shall cover 360°, up to 1200 square feet of walking motion with the Standard Lens and up to 500 square feet of walking motion with the High Density lens when mounted at a ceiling height of 8 feet.

- CI-300 and CI-305 sensors shall operate at 24 VDC/VAC and half-wave rectified and utilize a Watt Stopper power pack.

- CI-355 shall incorporate a switching power supply for reduced power consumption, shall operate at 120/230/277/347 VAC, 50/60 Hz and shall not require a power pack.

- The CI-300 sensor shall have an additional single-pole, double throw isolated relay with normally open, normally closed, and common outputs. The isolated relay is for use with HVAC control, data logging, and other control options.

- The CI-300 and CI-355 sensors shall have shall have a built-in light level sensor that works from 10 to 300 footcandles.

- Sensors shall have a time delay that is adjusted automatically (with the SmartSet setting) or shall have a fixed time delay of 5 to 30 minutes, set by dip switch.

- Sensor shall feature a walk-through mode, where lights turn off 3 minutes after the area is initially occupied if no motion is detected after the first 30 seconds.

- The CI-300 and CI-305 sensors shall have a manual on function that is facilitated by installing a momentary switch.

- The sensor shall have an LED indicator that remains active at all times in order to verify detection within the area to be controlled. The LED can be disable for applications that requires less visibility.

- To ensure quality and reliability, sensor shall be manufactured by an ISO 9002 certified manufacturing facility and shall have a defect rate of less than 1/3 of 1%.

- Sensors shall have standard 5 year warranty and shall be UL and CUL listed.

### CI-300 360° Passive Infrared Sensor

CI3001204