[image: image1.png]LEVITON



  Specifications
                                                                   ELECTRICITY METERING

SECTION 260913 ELECTRICAL POWER MONITORING

PART 1.0 - GENERAL
1.1      documents

1. Please note: that this section of the Specifications forms part of the Contract Documents and is to be read, interpreted, and coordinated with all other parts listed by the appropriate parties below.
1.2      SYSTEM DESCRIPTION
1. The products specified herein are intended to provide a complete sub-metering solution.  This solution shall be utilized to measure and monitor owner provided utilities including, but not limited to, electricity, gas, water, and steam. System will also allow for compliance with national and local energy codes and provide equipment needed to meet specific LEED M&V credits.
1.3      section includes
1. Electrical sub-metering equipment, data collection systems, and data management software systems including:

a. Standard single point kWh electrical sub-meters

b. Advanced single point kWh electrical sub-meters

c. Multi-point electrical sub-meters

d. Data collection hubs

e. High density pulse modules

f. Open protocol data communication network

g. Wireless communication devices

h. Energy monitoring and tenant billing software

1.4      standards
1. Provide equipment of this Section in full compliance with the following applicable portions of the latest revisions of the following standards:

a. ANSI C12.1 & C12.20 at 0.5 Accuracy Class

b. UL Certified to IEC/EN/UL/CSA 61010-1 2nd Edition.
c. UL916:
i. These requirements cover energy management equipment and associated sensing devices rated 600 volts or less and intended for installation in accordance with the National Electrical Code, NFPA 70.
1.5      shop drawings
1. Installation and Shop Drawings to include the following:

a. Manufacturer’s literature and specification
b. Component connection wiring diagrams

c. Communications system specification

1.6      installation, operation, and maintenance manuals
1. Submit installation, operation, and maintenance manuals for the electrical sub-metering system data collection system, and data management software.
1.7      technical performance
1. Minimum measured technical performance of each piece of installed equipment shall meet the specifications published by the manufacturer.

2. Optimize technical performance of all systems to produce the highest achievable technical performance to the satisfaction of consultant and/or client.

3. Any deficiencies in the system, particularly information communication errors or operational deficiencies, shall be cause for rejection.  Rectify any such deficiencies prior to calling for substantial completion review.
1.8      warranty
1. Manufacturer shall provide a comprehensive warranty for all products.  
2. All electrical sub-meters included in this specification to be free from defects in materials and workmanship from the date of substantial completion for a period of 10 Years.
3. All data collection system components included in this specification to be free from defects in materials and workmanship from the date of substantial completion for a period of 2 Years.
PART 2.0 – PRODUCTS
2.1       acceptable manufacturers

1. Acceptable Manufacturer: Leviton Manufacturing Co. Inc.
2. Basis of Design: Leviton VerifEye metering system.
3. Substitutions [Permitted] [Not Permitted]:
a. Show all substitutions as an add or deduct from base bid pricing.
b. Provide Manufacturer’s reference list.

c. Clearly delineate all propose substitutions as such and submit in writing for approval by the engineer a minimum of 10 working days prior to the bid date
d. Prior to rough-in, provide complete engineered shop drawings, including power wiring, with deviations for the original design highlighted in an alternate color, to the engineer for review and approval.
e. By using pre-approved substitutions, the contractor accepts responsibility and associated costs for all required modifications to circuitry, devices, and wiring.

2.2      meters and current transformers

1. Standard single point metering devices: Leviton Mini-Meters, Series 1000, and Series 2000

2. Advanced single point metering devices: Leviton 3300 and 3500 Series

3. Multipoint metering devices: Leviton 8000 Series.
4. Leviton solid or split core current transformers with full scale output of 0.1A
5. Solid Core current transformers available for 100-400A and split core current transformers available from 100-5,000A.
6. Current transformer secondaries can be extended up to 500 feet.  
2.3      SYSTEM DESCRIPTION – SINGLE POINT METERING DEVICES
1. Provide single point metering devices capable of metering 1PH/2W, 2PH/3W, 3PH/3W, and/or 3PH/4W loads. 

2. Meters must be capable of directly metering North American 120/208/240v and 277/480V. 
3. Metering units must be capable of metering loads between 100A and 5000A. Provide meters specific to each project as indicated on construction drawings.

4. Metering Units must have the capability of paralleling up to 3 (three) sets of CTs per phase.  

5. Must meet all ISO 9001 standards for quality control where all meters test to a minimum of +/- 0.5% accuracy. 
6. The system shall be as described below:

a. To consist of electronic meters with embedded communications capability, and solid or split-core current transformer technology. The current transformers shall have a full scale output of 0.1A outputs and secondary voltage clamps for safety purposes.

b. Meters to be used for Energy Monitoring and Tenant Billing applications


c. The meters will be capable of remote communication from each metering device. 
d. Standard meters shall have isolated pulse output with output ranges from 10Wh to 1kWh. 

e. Advanced meters shall transmit data via one of the following communication protocols:
i. Standard Ethernet interface

f. Systems to have backup storage power to key components so no data is lost during power outages.  Device must be capable of holding 2 years of interval data for a 20 year period. The system shall continue to function after resumption of power.  

g. Failure of the building electrical normal power system shall not result in loss of data and will not require manual restarting of the metering system
7. The electronic energy monitoring system shall be fully automated microprocessor-based electrical energy measurement system for Measurement and Verification and Tenant Billing purposes.  The system shall incorporate complete metering, communications, reporting functions, energy monitoring and threshold limit capabilities. 

2.4      SYSTEM MEASUREMENTS – SINGLE POINT METERING DEVICES

1. Meters to be complete with a Liquid Crystal Display (LCD) to access all energy measurements and phase diagnostics when needed

2. Standard Meter Energy Parameters: 
a. kWh

real consumption
b. kW peak
resettable kW peak (optional)

3. Advanced Meter Energy Parameters:
a. kWh

real consumption
b. kW peak
resettable kW peak
c. kW

instantaneous consumption

d. kVAh

apparent energy consumption

e. kVA

total apparent power

f. kVARh               reactive consumption

g. kVAR                 total reactive power
h. PF                     power Factor Total

i. Maximum kW    peak demand with time and date stamp

j. Line Frequency  Hz                  

4. Advanced Meter Phase Diagnostics: Parameters to be displayed for each individual phase of each metered load:
a. Voltage

Phase to neutral or phase to phase

b. Amps

Instantaneous amperage for each phase

c. kW

Instantaneous real energy
d. PF

Power factor
e. kVA

Instantaneous apparent energy

f. kVAR                Instantaneous reactive energy
2.5      SYSTEM DESCRIPTION – MULITPOINT METERING DEVICES    
1. The system shall be as described below:

a. To consist of electronic multi-meters with embedded communications capability, and solid or split-core current transformer technology. The current transformers shall have a full scale output of 0.1A outputs and secondary voltage clamps for safety purposes.

b. Meters to be used for Energy Monitoring and Tenant Billing applications


c. The meters will be capable of remote communication from each metering device. Each device shall have IP and Modbus sockets to accommodate data transmission via Modbus TCP and standard Ethernet. Data shall be transmitted by one or a combination of the following:
i. Standard Ethernet interface

ii. Ethernet connection to PC or laptop via crossover cable. 

d. Systems to have backup storage power to key components so no data is lost during power outages.  Device must be capable of holding 2 years of interval data for a 20 year period. The system shall continue to function after resumption of power.  

e. Failure of the building electrical normal power system shall not result in loss of data and will not require manual restarting of the metering system
2. The electronic energy monitoring system shall be fully automated microprocessor-based electrical energy measurement system for Measurement and Verification and Tenant Billing purposes.  The system shall incorporate the following:

a.  Complete metering
b. Communications

c. Reporting functions
d. Energy monitoring
e. Threshold limits capabilities. 

3. Meters must be capable of directly metering on board, North American 120/208/240v and 277/480V along with European 240/400v wye services. 

4. Metering Units must have the capability of a Wiring Harness, single incoming cable containing 25 pairs of 22 AWG wire with associated current transformers (CT’s) or optional Terminal Strips, screw terminal connections for CTs.
5. Must meet all ISO 9001 standards for quality control where all meters test to a minimum of +/- 0.5% accuracy. 

6. Metering unit(s) must be configurable to meter 24 single-pole circuits, 12 two-pole circuits, or 8 three-pole circuits
2.6      SYSTEM MEASUREMENTS – MULITPOINT METERING DEVICES     
1. Meters to be complete with a Liquid Crystal Display (LCD) to access energy measurements and phase diagnostics when needed

2. Energy Parameters:

a. kWh

real consumption

b. kW

instantaneous consumption

c. kVAh

apparent consumption

d. kVA

apparent power

e. kVARh               reactive consumption

f. kVAR                 reactive power

3. Phase Diagnostics: Parameters to be displayed for each individual phase of each metered load:

a. Voltage

Phase to neutral or phase to phase

b. Amps

Instantaneous amperage for each phase

c. kW

Instantaneous real energy

d. PF

Power factor

e. PA

Phase angle

f. kVA

Instantaneous apparent energy

g. kVAR                Instantaneous reactive energy

2.7      meters data collection and communication

1. Data acquisition sever: Leviton Energy Monitoring Hub and Hub Lite
2. Pulse data collection: Leviton High Density Pulse Module

3. Wireless data transmission: Leviton Modhopper

2.8      SYSTEM DESCRIPTION METER COMMUNICATIONS AND DATA COLLECTION

1. The system shall be as described below:
a. To consist of energy management hubs, pulse modules, wireless communication devices, and software used to transmit, collect, and display data provided by sub-metering equipment used to capture measurements from utilities that include, but are not limited to, electrical, gas, water, and steam.

b. System to allow all data collected to be connected to IP based applications including Third Party Billing Companies/Software, Enterprise Energy Management Software, Demand Response, and Smart Grid Collection for use in power Measurement and tenant billing.

c. Data collection system shall be all non-proprietary and compatible with industry standard M&V software applications.  Open protocols such as Modbus, pulse outputs, analog, resistive inputs, etc. shall be utilized.  No manufacture specific protocols between meter and data collectors shall be accepted.  
2.9      PRODUCT REQUIREMENTS - DATA AQUISITION SERVER
1. Provide data acquisition servers that measure and verify data from electrical meters and environmental sensors.
2. Server shall comply with the following codes and standards:

a. FCC CFR 47 Part 15, Class A

b. EN 610000

c. EN 61326

d. CE

3. Server shall be equipped with an ARMg embedded CPU, an ARM7 I/O co-processor, 32MB of onboard RAM, 16MB of NOR flash memory, and a USB expansion port.

4. Server shall operate under the following conditions:

a. 32°F to 122°F (0°C to 50°C), 0-90% RH, non-condensing

b. 41°F to 104°F (5°C to 40°C), 0-90% RH, non-condensing

5. Server shall have the capability to collect information at intervals from one (1) to sixty (60) minutes.
6. Server shall timestamp all acquired data and store it in a non-volatile memory.

7. Server shall use modem and/or Ethernet connections for internet access allowing either static IP (internet protocol) or DHCP (Dynamic Host Control Protocol) addressing.

8. Server shall communicate with metering data points via wired or wireless connections over the following protocols:

a. Wired communications:

i. Pulse

ii. Serial Port

1. RS485 Modbus

a. Modbus / RTU

b. Modbus /TCP
2. Modbus devices to be connected via Belden 1120A or equivalent 18g twisted shielded pair.
b. Wireless Communications:

i. Wireless Modbus
9. Server shall communicate with external devices via  wired or wireless connections over the following protocols:

a. Wired communications:

i. Ethernet LAN (Local Area Network) or WAN (Wide Area Network)
1. TCP/IP

2. PPP

3. HTTP/HTML

4. FTP

5. NTP

6. XML

7. SNMP

8. BACnet-Optional Downloaded Module

b. Wireless Communications:

i. GSM (Global System for Mobile Communications)

ii. GPRS (General Packet Radio Service)

iii. PSTN (Public Switched Telephone Network)

Server shall upload data at scheduled intervals via HTTP or FTP and download data in XML or custom formats.

10. Server shall generate alarms for data points including SNMP (Simple Network Management Protocol) traps.

11. Server shall have the following input and output connections:
a. Input:

i. RS485 Modbus serial input capable of supporting 32 external devices.  Input to be expandable at owner’s option.

ii. Eight (8) Flex I/O inputs configurable for the following modes:

1. 0-10VDC

2. 4-20mA

3. Resistive

4. Standard KYZ pulse modes for A or C dry contact relay outputs

5. Status
b. Output:

i. Two (2) opto-FET dry contact relays rated at 30VDC and 150mA maximum
2.10 PRODUCT REQUIREMENTS – HIGH DENSITY PULSE MODULES

1. Provide high density pulse module for collection and distribution of pulse output data generated by electric, gas, water, steam, BTU meters, and environmental sensors (humidity, temperature, etc.).
2. Module shall have on-board, adjustable Modbus addressing via dip switches with addresses from 1-128.
3. Module shall comply with the following codes and standards:
a.  FCC CFR 47 Part 15, Class A emissions standard.

4. Module shall be equipped with an ARM7 I/O processor with field-upgradable firmware.

5. Module shall communicate over a Modbus / RTU RS-485, two wire network with the following network speeds
a. 19200 Baud

b. 9600 Baud

6. Module shall operate under the following conditions
a. -22°F to 158°F (-30°C to 70°C), 0-90% RH, non-condensing
7. Module shall have a 32-bit pulse counter which rolls over at 4.295 billion pulses per channel and store pulse data in a non-volatile memory. Pulse rate shall be user selectable.

.

8. Module shall have the following input and output connections

a. Input

i. Non isolated pulse and power inputs

ii. Modbus RS485 connection

iii. Twenty-three (23) independent pulse count inputs designed for use with dry contact outputs.  The pulse rate shall be user selectable between the following:

1. 10Hz: Minimum pulse width to be 50ms

2. 50Hz: Minimum pulse width to be 10ms

3. 100Hz

2.11 PRODUCT REQUIREMENTS – WIRELESS TRANSCEIVER
1. Provide  OPTIONAL wireless transceiver for collection and distribution of pulse outputs generated by electrical meters and environmental sensors.
2. Transceiver shall comply with the following codes and standards:
a. FCC CFR 47 Part 15, Class A emissions standard.

b. FCC ID to be OUR-9XTREAM

c. Industry Canada ID to be 4214A-9XTREAM

3. Transceiver shall be equipped with a 60 MHz ARM7 embedded CPU.
4. Transceiver firmware to be field upgradable.

5. Transceiver shall communicate over a self-healing, self-optimizing wireless mesh network. Network shall utilize frequency hopping, spread-spectrum radio transmission and reception over 900MHz band.
6. Transceiver shall have a range of 3000 feet  indoors and 14 miles  outdoor line of sight.

7. Transceiver shall transmit data utilizing a  1W signal strength.
8. Transceiver shall operate under the following conditions
b. 32°F to 122°F (0°C to 50°C), 0-90% RH, non-condensing

c. 1.24 miles (2000m) maximum altitude, degree 2 pollution
9. Transceiver shall have a pulse counter with pulse data stored in a non-volatile memory.

.

10. Transceiver shall have the following input and output connections. Modbus addresses to be adjustable via DIP switches with addresses between 1 and 247.

a. Input

i. Two (2) Pulse inputs with user selectable pulse rates of 10, 50, 100, or 250 Hz.

ii. Modbus RS485 input

1. Connect a maximum of 32 Modbus devices to transceiver input
b. Output

i. Modbus RS485 output

1. Outputs to be user selectable between 100 Ohms and 2.5 kOhms.
ii. Two (2) opto-FET dry contact relays rated at 30VDC, 150mA max.

2.12 meter software

1. Enterprise Energy Management Software: Leviton Energy Manager

2. Building Management Software; Leviton BMO 2.0

3. Tennant Billing Software: Leviton BillSuite
2.13 PRODUCT REQUIREMENTS – ENTERPRISE ENERGY MANAGEMENT SOFTWARE

1. Provide a web hosted software platform which is fully functional without software other than standard web browsers including, but not limited to, Microsoft Internet Explorer and Mozilla Firefox.
2. Software shall be used for the collection, analysis, and reporting of energy data from sub-metering equipment used to capture measurements from utilities that include, but are not limited to, electrical, gas, water, and steam.
3. Software shall collect and report data in intervals from one (1) to sixty (60) minutes and illustrate information in real time.

4. Software shall produce customized reports and display data for all energy management components including cost, kW, kVA, kVAR, and power factor

5. Software shall include an automatic reporting system and instant alarm notification system.
2.14 PRODUCT REQUIREMENTS – BUILDING MANAGER SOFTWARE

1. Provide a web hosted software platform which is fully functional without software other than standard web browsers including, but not limited to, Microsoft Internet Explorer and Mozilla Firefox.
2. Software shall be used for the collection, analysis, and reporting of energy data from sub-metering equipment used to capture measurements from utilities that include, but are not limited to, electrical, gas, water, and steam.
3. Software shall collect and report data in intervals from one (1) to sixty (60) minutes and illustrate information in real time.

4. Software shall produce basic charts and graphs for reporting of energy usage trends.

5. Software shall include an automatic reporting system and instant alarm notification system.

6. Software shall be provided at no charge to the customer for the first year.  

2.15 PRODUCT REQUIREMENTS – TENANT BILLING SOFTWARE

1. Provide a PC based stand-alone software to be used for the collection, analysis, and reporting of energy data from sub-metering equipment used to capture measurements from utilities that include, but are not limited to, electrical, gas, water, and steam
2. Software shall be used for automated generation of individual tenant billing invoices utilizing customizable utility rates.
PART 3.0 – EXECUTION
2.1      Wiring and connections

1. All wiring must meet and or exceed local electrical code.
2. Metering points show on submitted drawings only to be connected or installed
3. Install all wiring in conduit.
4. Provide a non-dedicated or Ethernet drop for remote meter reading and diagnostics of the system
5. Perform all necessary system calibration, testing, commissioning, and demonstrations as required
6. Prepare and submit record drawings and installation, operation and maintenance manuals for the energy management system as required. 
2.2      testing and commiissioning

1. Perform final testing, adjustment, and commissioning of the systems, report results to the Consultant, and include the results in the installation, operation, and maintenance manuals.  Provide qualified technicians for testing and commissioning.
2. Perform sufficient technical and operational tests to ensure the technical performance of the system meets the intent of the Contract Documents.  Typical testing to include but not be limited to 
a. Verification of meter readings and proper installation of meter equipment

b. Communication system connectivity

c. Meter communication with all software platforms
3. Provide functional testing including verification that all meters are operating properly.
4. Test every device and control equipment after programming and submit a signed commissioning certificate and report to the Consultant and to the Client. 

5. Demonstrate the operation of the system to the Owner at a time suitable to them. Such demonstration to include product training on how to program the monitoring system.
2.3      field verification, acceptance, and training
1. Provide all “AS BUILT” DRAWINGS and data showing each meter, serial number, address, cross reference, load and CT ratio prior to field verification.

2. Manufacturer’s representative shall verify, adjust and test the system.  Verification of the energy monitoring system is to be carried out with the assistance of an electrical contractor at all times. Upon completion, the manufacturer shall issue a “CERTIFICATE OF ACCEPTANCE” to the owner, electrical consultant, contractor and client.
3. Manufacturer’s representative shall demonstrate operation of the system as follows:
a. Local and remote meter readings

b. Phase diagnostics

c. Provide manual of the installed system

4. Setup of system software as directed by client.
5. Provide training and software manual for owner’s staff to review. 
2.4      field quality control
1. Submit a detailed testing and commissioning procedure to the Consultant and Client for review and approval prior to undertaking this Work.  The procedure shall indicate all test equipment required and acceptance criteria.

2. Upon completion of all testing and commissioning, submit a copy of the test results and certify the system as acceptable for revenue metering purposes.
3. Undertake the testing and commissioning Work with the manufacturer's factory representative(s). 
2.5      instruction to staff
1. Upon completion of the installation, a competent instructor representing the system manufacturer shall provide a lecture to the operating and maintenance staff concerning the intent, use, and operation and maintenance of the system       
2. Staff training shall include a minimum of four hours per shift and training sessions shall be videotaped and turned over to the Owner.  Allow for two shifts of staff training.   
End of Section

Leviton

ELECTRICITY METERING


[image: image1.png]