## Instructions
V2.7 | ATV320 - Communication Parameters
DANGER
UNINTENDED EQUIPMENT OPERATION • Read and understand the programming manual before operating the drive. • Any changes made to the parameter settings must be performed by qualified personnel. Failure to follow these instructions will result in death or serious injury.
WARNING
LOSS OF CONTROL •The designer of any control scheme must - consider the potential failure modes of control paths and, for certain critical control functions, - provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop and overtravel stop. •Separate or redundant control paths must be provided for critical control functions. •System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. (see note a.) Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only . Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual for full information.
This Excel file can be used to carry out searches (e.g. parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the Altivar 12 User Manual, which includes an index of parameter codes.
Additional information can be found in the Altivar 12 Modbus Communication Manual.
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.
EXPLANATORY NOTE
This Excel file is for reference only . Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual for full information.
This Excel file can be used to carry out searches (e.g. parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the Altivar 12 User Manual, which includes an index of parameter codes.
Additional information can be found in the Altivar 12 Modbus Communication Manual.
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index: CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
PROFIBUS index: Address for PROFIBUS
CIP : Address for DeviceNet
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu | Order
CMD | Control word | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 | CMD | Control parameters | R/W | WORD (BitString16) | - |  | - | [Cmd value] (CMd) | [COMMUNICATION MAP] (CMM-) | 1
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 | CMI | Control parameters | R/W | WORD (BitString16) | - |  | - |  |  | 2
RPR | Reset counters command | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] (nO) | - | [Operating t. reset] (rPr) | [MONIT. POWER TIME] (PEt-) | 3
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 | - | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | - |  |  | 4
LFR | Frequency setpoint | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 | - | Setpoint parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [Frequency ref.] (LFr) | [MONITORING] (SUP-) [REFERENCE SWITCH.] (rEF-) [MONITORING] (MOn-) | 5
PISP | PID regulator setpoint | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 | - | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000 |  |  | 6
AIV1 | First virtual AI value | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 | - | Setpoint parameters | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Image input AIV1] (AIU1) | [REFERENCE SWITCH.] (rEF-) [MONITORING] (MOn-) | 7
AIV2 | Second virtual AI value | 16#14A3 = 5283 | 16#2016/54 | 16#7B/01/54 = 123/01/84 | - | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -8192 ... 8192 |  |  | 8
MFR | Multiplying coefficient | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 | - | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFr) | [MONITORING] (SUP-) [REFERENCE SWITCH.] (rEF-) [MONITORING] (MOn-) [SETTINGS] (SEt-) | 9
ETA | Status word | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 | ETA | Status parameters | R | WORD (BitString16) | - |  | - | [ETA state word] (EtA) | [MONITORING] (SUP-) [COMMUNICATION MAP] (CMM-) | 10
HMIS | Drive state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | - |  | - |  |  | 11
NTJ | Transistor alarm counter | 16#0CA9 = 3241 | 16#2002/2A | 16#71/01/2A = 113/01/42 | - | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [IGBT alarm Nb] (ntJ) | [DIAGNOSTICS] (dGt-) [MONITORING] (SUP-) | 12
ETI | Extended status word | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 | ETI | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 13
LRS1 | Extended status word 1 | 16#0CB2 = 3250 | 16#2002/33 | 16#71/01/33 = 113/01/51 | LRS1 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 14
LRS2 | Extended status word 2 | 16#0CB3 = 3251 | 16#2002/34 | 16#71/01/34 = 113/01/52 | LRS2 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 15
LRS3 | Extended status word 3 | 16#0CB4 = 3252 | 16#2002/35 | 16#71/01/35 = 113/01/53 | LRS3 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 16
LRS4 | Extended status word 4 | 16#0CB5 = 3253 | 16#2002/36 | 16#71/01/36 = 113/01/54 | LRS4 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 17
LRS5 | Extended status word 5 | 16#0CB6 = 3254 | 16#2002/37 | 16#71/01/37 = 113/01/55 | LRS5 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 18
LRS6 | Extended status word 6 | 16#0CB7 = 3255 | 16#2002/38 | 16#71/01/38 = 113/01/56 | LRS6 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 19
LRS7 | Extended status word 7 | 16#0CB8 = 3256 | 16#2002/39 | 16#71/01/39 = 113/01/57 | LRS7 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 20
LRS8 | Extended status word 8 | 16#0CB9 = 3257 | 16#2002/3A | 16#71/01/3A = 113/01/58 | LRS8 | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 21
CRC | Active reference channel | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 | CCC | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 22
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 | CCC | Status parameters | R | WORD (BitString16) | - |  | - |  |  | 23
CNFS | Config. active | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  | - | [Config. active] (CnFS) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 24
STUN | Autotune selection result | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] (tAb) | - | [Tune selection] (StUn) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) [SYNCHRONOUS MOTOR] (SYn-) | 25
TUNU | Auto tune usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Status parameters | R/WS | WORD (Enumeration) | - | [Therm mot] (tM) | - | [Auto tuning usage] (tUnU) | [ASYNC. MOTOR] (ASY-) [SYNCHRONOUS MOTOR] (SYn-) | 26
SMOT | Status of tune in term of salliency | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  | - | [Saliency mot. state] (SMOt) | [SYNCHRONOUS MOTOR] (SYn-) | 27
ECSS | EtherCAT slave status | 16#1A22 = 6690 | 16#2024/5B | 16#82/01/5B = 130/01/91 | ETST | Status parameters | R | WORD (Enumeration) | - |  | - | [EthCat slave status] (ECSS) | [COMMUNICATION CARD] (Cbd-) | 28
ECAA | EtherCAT second address actual value | 16#1A24 = 6692 | 16#2024/5D | 16#82/01/5D = 130/01/93 | - | Status parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat addr] (ECAA) | [COMMUNICATION CARD] (Cbd-) | 29
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 | - | Actual values parameters | R | INT (Signed16) | 1 rpm |  | - |  |  | 30
RFR | Output frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 | - | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (rFr) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 31
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 | - | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (Otr) | [MONITORING] (SUP-) [MONIT. MOTOR] (MMO-) | 32
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 | - | Actual values parameters | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A | [Motor current] (LCr) | [MONITORING] (SUP-) [MONIT. MOTOR] (MMO-) | 33
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 | - | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [MONITORING] (SUP-) [MONIT. MOTOR] (MMO-) | 34
OPR | Motor power | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 | - | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor power] (OPr) | [MONITORING] (SUP-) [MONIT. MOTOR] (MMO-) | 35
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 | - | Reference parameters | R | INT (Signed16) | 1 rpm |  | - |  |  | 36
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 | - | Reference parameters | R | INT (Signed16) | 1 rpm |  | - |  |  | 37
FRH | Frequency reference before ramp | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 | - | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -599.0 Hz ... 599.0 Hz | [Frequency ref.] (FrH) | [MONITORING] (SUP-) [REFERENCE SWITCH.] (rEF-) [MONITORING] (MOn-) [COMMUNICATION MAP] (CMM-) | 38
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 | - | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | - |  |  | 39
RPC | PID reference after ramp | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 | - | Reference parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PID reference] (rPC) | [MONITORING] (SUP-) [REFERENCE SWITCH.] (rEF-) [MONIT. PI] (MPI-) | 40
RPF | PID regulator feedback reference | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 | - | Reference parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [PID feedback] (rPF) | [MONITORING] (SUP-) [MONIT. PI] (MPI-) | 41
RPE | PID regulator discrepancy | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 | - | Reference parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767 | [PID error] (rPE) | [MONITORING] (SUP-) [MONIT. PI] (MPI-) | 42
RPO | PID regulator limit output reference | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 | - | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (rPO) | [MONITORING] (SUP-) [MONIT. PI] (MPI-) | 43
ULN | Mains voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 | - | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V | [Mains voltage] (ULn) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 44
APH | Energy consumption | 16#0C9E = 3230 | 16#2002/1F | 16#71/01/1F = 113/01/31 | - | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [Consumption] (APH) | [MONITORING] (SUP-) [MONIT. POWER TIME] (PEt-) | 45
THD | Drive thermal state | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 | - | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drv. thermal state] (tHd) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 46
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 | - | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor thermal state] (tHr) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 47
RTH | Total motor operating time | 16#0C9F = 3231 | 16#2002/20 | 16#71/01/20 = 113/01/32 | - | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [Run time] (rtH) | [MONITORING] (SUP-) [MONIT. POWER TIME] (PEt-) | 48
PTH | Total drive operating time | 16#0CA1 = 3233 | 16#2002/22 | 16#71/01/22 = 113/01/34 | - | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | Refer to programming manual | [Power on time] (PtH) | [MONITORING] (SUP-) [MONIT. POWER TIME] (PEt-) | 49
TAC | IGBT alarm time | 16#0CA3 = 3235 | 16#2002/24 | 16#71/01/24 = 113/01/36 | - | Measurement parameters | R | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s | [IGBT alarm counter] (tAC) | [DIAGNOSTICS] (dGt-) [MONITORING] (SUP-) | 50
TAC2 | Transistor alarm time counter at freq min | 16#0CAA = 3242 | 16#2002/2B | 16#71/01/2B = 113/01/43 | - | Measurement parameters | R | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s | [Min. freq time] (tAC2) | [DIAGNOSTICS] (dGt-) [MONITORING] (SUP-) | 51
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 | IL1I | I/O parameters | R | WORD (BitString16) | - |  | - |  |  | 52
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 | OL1R | I/O parameters | R/W | WORD (BitString16) | - |  | - |  |  | 53
AI1C | Analog input 1 physical value | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 | - | I/O parameters | R | INT (Signed16) | 0.001 V |  | - | [AI1] (AI1C) | [MONITORING] (SUP-) | 54
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 | - | I/O parameters | R | INT (Signed16) | 1 |  | - |  |  | 55
AI2C | Analog input 2 physical value | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 | - | I/O parameters | R | INT (Signed16) | 0.001 V |  | - | [AI2] (AI2C) | [MONITORING] (SUP-) | 56
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 | - | I/O parameters | R | INT (Signed16) | 1 |  | - |  |  | 57
AI3C | Analog input 3 physical value | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 | - | I/O parameters | R | INT (Signed16) | 0.001 mA |  | - | [AI3] (AI3C) | [MONITORING] (SUP-) | 58
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 | - | I/O parameters | R | INT (Signed16) | 1 |  | - |  |  | 59
AO1C | Analog output 1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 | - | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | - | [AO1] (AO1C) | [MONITORING] (SUP-) | 60
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 | - | I/O parameters | R/W | INT (Signed16) | 1 |  | - |  |  | 61
FQS | Pulse input frequency | 16#390B = 14603 | 16#2074/4 | 16#AA/01/04 = 170/01/04 | - | I/O parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 20000 Hz | [Pulse in. work. freq.] (FqS) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 62
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 | ERRD | Fault parameters | R | WORD (BitString16) | - |  | - |  |  | 63
LFT | Altivar fault code | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | - |  | - |  |  | 64
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 | CIC | Fault parameters | R/WS | WORD (BitString16) | - |  | - |  |  | 65
CNF | Network card fault code | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 | - | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Network fault] (CnF) | [COMMUNICATION CARD] (Cbd-) [MORE FAULT INFO] (AFI-) | 66
ILF1 | Option card 1 fault code | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 | - | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Internal link fault 1] (ILF1) | [COMMUNICATION CARD] (Cbd-) [MORE FAULT INFO] (AFI-) | 67
FDRD | Ethernet fault code | 16#FAE9 = 64233 |  | = | - | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [FDR fault] (Fdrd) | [COMMUNICATION CARD] (Cbd-) | 68
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 | - | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 69
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 70
ULP0 | Power supply voltage on last fault | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 71
LCP0 | Motor current on last fault | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 72
RFP0 | Output frequency on last fault | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 73
THP0 | Motor thermal state on last fault | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 74
EP0 | Status word on last fault | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 75
IP0 | Extended status word on last fault | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 76
CMP0 | Command word on last fault | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 77
DCC0 | Command channel active on last fault | 16#FB2C = 64300 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 78
DRC0 | Reference channel active on last fault | 16#FB36 = 64310 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 79
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 80
RTP0 | Motor operating time on last fault | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 81
OTP0 | Estimated motor torque value of actual fault | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 82
TDP0 | Mesured drive thermal state of actual fault | 16#1CAC = 7340 | 16#202B/29 | 16#85/01/8D = 133/01/141 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 83
TJP0 | Estimated TJ value of actual fault | 16#1CB6 = 7350 | 16#202B/33 | 16#85/01/97 = 133/01/151 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 84
SFP0 | Switching frequency really applied by MotorControl of actual fault | 16#1CC0 = 7360 | 16#202B/3D | 16#85/01/A1 = 133/01/161 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 85
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 86
ULP1 | Supply voltage on fault n-1 | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 87
LCP1 | Motor current on fault n-1 | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 88
RFP1 | Output frequency on fault n-1 | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 89
THP1 | Motor thermal state on fault n-1 | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 90
EP1 | Status word on fault n-1 | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 91
IP1 | Extended status word on fault n-1 | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 92
CMP1 | Command word on fault n-1 | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 93
DCC1 | Active command channel on fault n-1 | 16#FB2D = 64301 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 94
DRC1 | Active reference channel on fault n-1 | 16#FB37 = 64311 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 95
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 96
RTP1 | Motor operating time on fault n-1 | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 97
OTP1 | Estimated motor torque value on fault n-1 | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 98
TDP1 | Mesured drive thermal state on fault n-1 | 16#1CAD = 7341 | 16#202B/2A | 16#85/01/8E = 133/01/142 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 99
TJP1 | Estimated TJ value on fault n-1 | 16#1CB7 = 7351 | 16#202B/34 | 16#85/01/98 = 133/01/152 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 100
SFP1 | Switching frequency really applied by MotorControl on fault n-1 | 16#1CC1 = 7361 | 16#202B/3E | 16#85/01/A2 = 133/01/162 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 101
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 102
ULP2 | Supply voltage on fault n-2 | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 103
LCP2 | Motor current on fault n-2 | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 104
RFP2 | Output frequency on fault n-2 | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 105
THP2 | Motor thermal state on fault n-2 | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 106
EP2 | Status word on fault n-2 | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 107
IP2 | Extended status word on fault n-2 | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 108
CMP2 | Command word on fault n-2 | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 109
DCC2 | Active command channel on fault n-2 | 16#FB2E = 64302 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 110
DRC2 | Active reference channel on fault n-2 | 16#FB38 = 64312 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 111
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 112
RTP2 | Motor operating time on fault n-2 | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 113
OTP2 | Estimated motor torque value on fault n-2 | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 114
TDP2 | Mesured drive thermal state on fault n-2 | 16#1CAE = 7342 | 16#202B/2B | 16#85/01/8F = 133/01/143 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 115
TJP2 | Estimated TJ value on fault n-2 | 16#1CB8 = 7352 | 16#202B/35 | 16#85/01/99 = 133/01/153 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 116
SFP2 | Switching frequency really applied by MotorControl on fault n-2 | 16#1CC2 = 7362 | 16#202B/3F | 16#85/01/A3 = 133/01/163 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 117
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 118
ULP3 | Supply voltage on fault n-3 | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 119
LCP3 | Motor current on fault n-3 | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 120
RFP3 | Output frequency on fault n-3 | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 121
THP3 | Motor thermal state on fault n-3 | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 122
EP3 | Status word on fault n-3 | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 123
IP3 | Extended status word on fault n-3 | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 124
CMP3 | Command word on fault n-3 | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 125
DCC3 | Active command channel on fault n-3 | 16#FB2F = 64303 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 126
DRC3 | Active reference channel on fault n-3 | 16#FB39 = 64313 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 127
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 128
RTP3 | Motor operating time on fault n-3 | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 129
OTP3 | Estimated motor torque value on fault n-3 | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 130
TDP3 | Mesured drive thermal state on fault n-3 | 16#1CAF = 7343 | 16#202B/2C | 16#85/01/90 = 133/01/144 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 131
TJP3 | Estimated TJ value on fault n-3 | 16#1CB9 = 7353 | 16#202B/36 | 16#85/01/9A = 133/01/154 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 132
SFP3 | Switching frequency really applied by MotorControl on fault n-3 | 16#1CC3 = 7363 | 16#202B/40 | 16#85/01/A4 = 133/01/164 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 133
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 134
ULP4 | Supply voltage on fault n-4 | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 135
LCP4 | Motor current on fault n-4 | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 136
RFP4 | Output frequency on fault n-4 | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 137
THP4 | Motor thermal state on fault n-4 | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 138
EP4 | Status word on fault n-4 | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 139
IP4 | Extended status word on fault n-4 | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 140
CMP4 | Command word on fault n-4 | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 141
DCC4 | Active command channel on fault n-4 | 16#FB30 = 64304 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 142
DRC4 | Active reference channel on fault n-4 | 16#FB3A = 64314 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 143
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 144
RTP4 | Motor operating time on fault n-4 | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 145
OTP4 | Estimated motor torque value on fault n-4 | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 146
TDP4 | Mesured drive thermal state on fault n-4 | 16#1CB0 = 7344 | 16#202B/2D | 16#85/01/91 = 133/01/145 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 147
TJP4 | Estimated TJ value on fault n-4 | 16#1CBA = 7354 | 16#202B/37 | 16#85/01/9B = 133/01/155 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 148
SFP4 | Switching frequency really applied by MotorControl on fault n-4 | 16#1CC4 = 7364 | 16#202B/41 | 16#85/01/A5 = 133/01/165 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 149
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 150
ULP5 | Supply voltage on fault n-5 | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 151
LCP5 | Motor current on fault n-5 | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 152
RFP5 | Output frequency on fault n-5 | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 153
THP5 | Motor thermal state on fault n-5 | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 154
EP5 | Status word on fault n-5 | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 155
IP5 | Extended status word on fault n-5 | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 156
CMP5 | Command word on fault n-5 | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 157
DCC5 | Active command channel on fault n-5 | 16#FB31 = 64305 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 158
DRC5 | Active reference channel on fault n-5 | 16#FB3B = 64315 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 159
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 160
RTP5 | Motor operating time on fault n-5 | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 161
OTP5 | Estimated motor torque value on fault n-5 | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 162
TDP5 | Mesured drive thermal state on fault n-5 | 16#1CB1 = 7345 | 16#202B/2E | 16#85/01/92 = 133/01/146 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 163
TJP5 | Estimated TJ value on fault n-5 | 16#1CBB = 7355 | 16#202B/38 | 16#85/01/9C = 133/01/156 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 164
SFP5 | Switching frequency really applied by MotorControl on fault n-5 | 16#1CC5 = 7365 | 16#202B/42 | 16#85/01/A6 = 133/01/166 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 165
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 166
ULP6 | Supply voltage on fault n-6 | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 167
LCP6 | Motor current on fault n-6 | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 168
RFP6 | Output frequency on fault n-6 | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 169
THP6 | Motor thermal state on fault n-6 | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 170
EP6 | Status word on fault n-6 | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 171
IP6 | Extended status word on fault n-6 | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 172
CMP6 | Command word on fault n-6 | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 173
DCC6 | Active command channel on fault n-6 | 16#FB32 = 64306 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 174
DRC6 | Active reference channel on fault n-6 | 16#FB3C = 64316 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 175
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 176
RTP6 | Motor operating time on fault n-6 | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 177
OTP6 | Estimated motor torque value on fault n-6 | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 178
TDP6 | Mesured drive thermal state on fault n-6 | 16#1CB2 = 7346 | 16#202B/2F | 16#85/01/93 = 133/01/147 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 179
TJP6 | Estimated TJ value on fault n-6 | 16#1CBC = 7356 | 16#202B/39 | 16#85/01/9D = 133/01/157 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 180
SFP6 | Switching frequency really applied by MotorControl on fault n-6 | 16#1CC6 = 7366 | 16#202B/43 | 16#85/01/A7 = 133/01/167 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 181
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 182
ULP7 | Supply voltage on fault n-7 | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 183
LCP7 | Motor current on fault n-7 | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 184
RFP7 | Output frequency on fault n-7 | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 185
THP7 | Motor thermal state on fault n-7 | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 186
EP7 | Status word on fault n-7 | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 187
IP7 | Extended status word on fault n-7 | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 188
CMP7 | Command word on fault n-7 | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 189
DCC7 | Active command channel on fault n-7 | 16#FB33 = 64307 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 190
DRC7 | Active reference channel on fault n-7 | 16#FB3D = 64317 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 191
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 192
RTP7 | Motor operating time on fault n-7 | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 193
OTP7 | Estimated motor torque value on fault n-7 | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 194
TDP7 | Mesured drive thermal state on fault n-7 | 16#1CB3 = 7347 | 16#202B/30 | 16#85/01/94 = 133/01/148 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 195
TJP7 | Estimated TJ value on fault n-7 | 16#1CBD = 7357 | 16#202B/3A | 16#85/01/9E = 133/01/158 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 196
SFP7 | Switching frequency really applied by MotorControl on fault n-7 | 16#1CC7 = 7367 | 16#202B/44 | 16#85/01/A8 = 133/01/168 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 197
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 198
ULP8 | Supply voltage on fault n-8 | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 | - | History parameters | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 199
LCP8 | Motor current on fault n-8 | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 | - | History parameters | R | INT (Signed16) | 0.1 A |  | -3276.7 A ... 3276.7 A |  |  | 200
RFP8 | Output frequency on fault n-8 | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 | - | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 201
THP8 | Motor thermal state on fault n-8 | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % |  |  | 202
EP8 | Status word on fault n-8 | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 | ETA | History parameters | R | WORD (BitString16) | - |  | - |  |  | 203
IP8 | Extended status word on fault n-8 | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 | ETI | History parameters | R | WORD (BitString16) | - |  | - |  |  | 204
CMP8 | Command word on fault n-8 | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 | CMD | History parameters | R | WORD (BitString16) | - |  | - |  |  | 205
DCC8 | Active command channel on fault n-8 | 16#FB34 = 64308 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 206
DRC8 | Active reference channel on fault n-8 | 16#FB3E = 64318 |  | = | CNL | History parameters | R | WORD (Enumeration) | - |  | - |  |  | 207
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 | CRP0 | History parameters | R | WORD (BitString16) | - |  | - |  |  | 208
RTP8 | Motor operating time on fault n-8 | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 | - | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h |  |  | 209
OTP8 | Estimated motor torque value on fault n-8 | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 | - | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 210
TDP8 | Mesured drive thermal state on fault n-8 | 16#1CB4 = 7348 | 16#202B/31 | 16#85/01/95 = 133/01/149 | - | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % |  |  | 211
TJP8 | Estimated TJ value on fault n-8 | 16#1CBE = 7358 | 16#202B/3B | 16#85/01/9F = 133/01/159 | - | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C |  |  | 212
SFP8 | Switching frequency really applied by MotorControl on fault n-8 | 16#1CC8 = 7368 | 16#202B/45 | 16#85/01/A9 = 133/01/169 | - | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz |  |  | 213
NCV | Drive nominal rating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] (nO) | - |  |  | 214
VCAL | Drive line voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [No] (nO) | - |  |  | 215
INV | Rated drive current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 | - | Identification parameters | R | UINT (Unsigned16) | 0.1 A | Depends of rating | - |  |  | 216
VDP | Drive software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 | - | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 217
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 218
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 219
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 220
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 221
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 222
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 223
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 224
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 225
NC1 | Communication scanner, value of write word 1 | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (nC1) | [COM SCAN OUTPUT MAP] (OSA-) | 226
NC2 | Communication scanner, value of write word 2 | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (nC2) | [COM SCAN OUTPUT MAP] (OSA-) | 227
NC3 | Communication scanner, value of write word 3 | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (nC3) | [COM SCAN OUTPUT MAP] (OSA-) | 228
NC4 | Communication scanner, value of write word 4 | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (nC4) | [COM SCAN OUTPUT MAP] (OSA-) | 229
NC5 | Communication scanner, value of write word 5 | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (nC5) | [COM SCAN OUTPUT MAP] (OSA-) | 230
NC6 | Communication scanner, value of write word 6 | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (nC6) | [COM SCAN OUTPUT MAP] (OSA-) | 231
NC7 | Communication scanner, value of write word 7 | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (nC7) | [COM SCAN OUTPUT MAP] (OSA-) | 232
NC8 | Communication scanner, value of write word 8 | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (nC8) | [COM SCAN OUTPUT MAP] (OSA-) | 233
NM1 | Communication scanner, value of read word 1 | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (nM1) | [COM. SCANNER INPUT MAP] (ISA-) | 234
NM2 | Communication scanner, value of read word 2 | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (nM2) | [COM. SCANNER INPUT MAP] (ISA-) | 235
NM3 | Communication scanner, value of read word 3 | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (nM3) | [COM. SCANNER INPUT MAP] (ISA-) | 236
NM4 | Communication scanner, value of read word 4 | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (nM4) | [COM. SCANNER INPUT MAP] (ISA-) | 237
NM5 | Communication scanner, value of read word 5 | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (nM5) | [COM. SCANNER INPUT MAP] (ISA-) | 238
NM6 | Communication scanner, value of read word 6 | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (nM6) | [COM. SCANNER INPUT MAP] (ISA-) | 239
NM7 | Communication scanner, value of read word 7 | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (nM7) | [COM. SCANNER INPUT MAP] (ISA-) | 240
NM8 | Communication scanner, value of read word 8 | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 | - | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (nM8) | [COM. SCANNER INPUT MAP] (ISA-) | 241
SMAL | Velocity min amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm |  |  | 242
SMIL | Velocity max amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm |  |  | 243
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 1 rpm ... 65535 rpm |  |  | 244
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s |  |  | 245
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 rpm |  | 1 rpm ... 65535 rpm |  |  | 246
SPDT | Deceleration delta time | 16#21A8 = 8616 | 16#2038/11 | 16#8C/01/11 = 140/01/17 | - | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s |  |  | 247
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 | - | CiA 402 settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 65535 |  |  | 248
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 | - | CiA 402 settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 65535 |  |  | 249
DOTD | Disable operation option code | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [Dis. operat opt code] (dOtd) | [STOP CONFIGURATION] (Stt-) | 250
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | (FSt6) | - |  |  | 251
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Saving config.] (SCS) | [FACTORY SETTINGS] (FCS-) | 252
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [NO] (nO) | - | [Restore config.] (FCS) | [FACTORY SETTINGS] (FCS-) | 253
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 | FrY | Configuration management | R/WS | WORD (BitString16) | - | 0 | - |  |  | 254
CHA1 | 2 Parameter sets | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [2 Parameter sets] (CHA1) | [PARAM. SET SWITCHING] (MLP-) | 255
CHA2 | 3 Parameter sets | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [3 Parameter sets] (CHA2) | [PARAM. SET SWITCHING] (MLP-) | 256
CFPS | Active parameter set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  | - | [Utilised param. set] (CFPS) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 257
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1 |  |  | 258
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 259
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 260
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 261
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 262
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 263
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 264
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 265
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 266
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 267
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 268
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 269
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 270
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 271
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 272
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 273
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S101) | [SET 1] (PS1-) | 274
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S102) | [SET 1] (PS1-) | 275
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S103) | [SET 1] (PS1-) | 276
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S104) | [SET 1] (PS1-) | 277
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S105) | [SET 1] (PS1-) | 278
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S106) | [SET 1] (PS1-) | 279
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S107) | [SET 1] (PS1-) | 280
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S108) | [SET 1] (PS1-) | 281
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S109) | [SET 1] (PS1-) | 282
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S110) | [SET 1] (PS1-) | 283
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S111) | [SET 1] (PS1-) | 284
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S112) | [SET 1] (PS1-) | 285
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S113) | [SET 1] (PS1-) | 286
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S114) | [SET 1] (PS1-) | 287
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S115) | [SET 1] (PS1-) | 288
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S201) | [SET 2] (PS2-) | 289
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S202) | [SET 2] (PS2-) | 290
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S203) | [SET 2] (PS2-) | 291
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S204) | [SET 2] (PS2-) | 292
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S205) | [SET 2] (PS2-) | 293
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S206) | [SET 2] (PS2-) | 294
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S207) | [SET 2] (PS2-) | 295
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S208) | [SET 2] (PS2-) | 296
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S209) | [SET 2] (PS2-) | 297
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S210) | [SET 2] (PS2-) | 298
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S211) | [SET 2] (PS2-) | 299
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S212) | [SET 2] (PS2-) | 300
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S213) | [SET 2] (PS2-) | 301
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S214) | [SET 2] (PS2-) | 302
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S215) | [SET 2] (PS2-) | 303
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S301) | [SET 3] (PS3-) | 304
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S302) | [SET 3] (PS3-) | 305
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S303) | [SET 3] (PS3-) | 306
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S304) | [SET 3] (PS3-) | 307
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S305) | [SET 3] (PS3-) | 308
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S306) | [SET 3] (PS3-) | 309
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S307) | [SET 3] (PS3-) | 310
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S308) | [SET 3] (PS3-) | 311
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S309) | [SET 3] (PS3-) | 312
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S310) | [SET 3] (PS3-) | 313
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S311) | [SET 3] (PS3-) | 314
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S312) | [SET 3] (PS3-) | 315
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S313) | [SET 3] (PS3-) | 316
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S314) | [SET 3] (PS3-) | 317
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 | - | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (S315) | [SET 3] (PS3-) | 318
CFG | Macro configuration | 16#0BEC = 3052 | 16#2000/35 | 16#70/01/35 = 112/01/53 | CFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Start/Stop] (StS) | - | [Macro configuration] (CFG) | [CONFIGURATION] (COnF-) [SIMPLY START] (SIM-) | 319
CCFG | Customized macro | 16#0BED = 3053 | 16#2000/36 | 16#70/01/36 = 112/01/54 | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  | - | [Customized macro] (CCFG) | [SIMPLY START] (SIM-) | 320
LSP | Low speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0.0 Hz ... 599.0 Hz | [Low speed] (LSP) | [SIMPLY START] (SIM-) [SETTINGS] (SEt-) | 321
HSP | High speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed] (HSP) | [HSP SWITCHING] (CHS-) [SIMPLY START] (SIM-) [SETTINGS] (SEt-) | 322
HSP2 | High speed 2 | 16#3B06 = 15110 | 16#2079/B | 16#AC/01/6F = 172/01/111 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 2] (HSP2) | [HSP SWITCHING] (CHS-) [SETTINGS] (SEt-) | 323
HSP3 | High speed 3 | 16#3B07 = 15111 | 16#2079/C | 16#AC/01/70 = 172/01/112 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 3] (HSP3) | [HSP SWITCHING] (CHS-) [SETTINGS] (SEt-) | 324
HSP4 | High speed 4 | 16#3B08 = 15112 | 16#2079/D | 16#AC/01/71 = 172/01/113 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [High speed 4] (HSP4) | [HSP SWITCHING] (CHS-) [SETTINGS] (SEt-) | 325
SH2 | 2 HSP assignment | 16#3AFD = 15101 | 16#2079/2 | 16#AC/01/66 = 172/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [2 High speed] (SH2) | [HSP SWITCHING] (CHS-) | 326
SH4 | 4 HSP assignment | 16#3AFE = 15102 | 16#2079/3 | 16#AC/01/67 = 172/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [4 High speed] (SH4) | [HSP SWITCHING] (CHS-) | 327
ITH | Mot. therm. current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | Depends of rating | - | [Mot. therm. current] (ItH) | [SIMPLY START] (SIM-) [SETTINGS] (SEt-) | 328
SPG | Speed prop. gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 329
SPGU | Inertia factor for UF law | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [UF inertia comp.] (SPGU) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 330
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 63 ms | 1 ms ... 65535 ms | [Speed time integral] (SIt) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 331
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 65 | 0 ... 100 | [K speed loop filter] (SFC) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 332
FFH | Frequency to filter the estimated speed | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 6.4 ms | 0.0 ms ... 100.0 ms | [Spd est. filter time] (FFH) | [MOTOR CONTROL] (drC-) | 333
CRTF | Filter time of the current reference filter | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 3.2 ms | 0.0 ms ... 100.0 ms | [Cur. ref. filter time] (CrtF) | [MOTOR CONTROL] (drC-) | 334
CTD | Current threshold | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | INV | 0.0 A ... 6553.5 A | [Current threshold] (Ctd) | [ALARMS SETTING] (ALS-) [SETTINGS] (SEt-) | 335
TTH | High torque thd. | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 | - | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (ttH) | [ALARMS SETTING] (ALS-) [SETTINGS] (SEt-) | 336
TTL | Low torque thd. | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 | - | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (ttL) | [ALARMS SETTING] (ALS-) [SETTINGS] (SEt-) | 337
FQL | Pulse warning thd. | 16#3911 = 14609 | 16#2074/A | 16#AA/01/0A = 170/01/10 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 20000 Hz | [Pulse warning thd.] (FqL) | [ALARMS SETTING] (ALS-) [SETTINGS] (SEt-) | 338
FTD | Freq. threshold | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq. threshold] (Ftd) | [ALARMS SETTING] (ALS-) [SETTINGS] (SEt-) | 339
F2D | Freq. threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Freq. threshold 2] (F2d) | [ALARMS SETTING] (ALS-) [SETTINGS] (SEt-) | 340
JF2 | Skip Frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency 2] (JF2) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 341
JPF | Skip Frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Skip Frequency] (JPF) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 342
JFH | Skip.Freq.Hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip.Freq.Hysteresis] (JFH) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 343
JF3 | 3rd Skip Frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [3rd Skip Frequency] (JF3) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 344
BFR | Standard mot. freq | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | [50Hz IEC] (50) | - | [Standard mot. freq] (bFr) | [SIMPLY START] (SIM-) [MOTOR CONTROL] (drC-) | 345
NPR | Rated motor power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 | - | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | - | [Rated motor power] (nPr) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) | 346
COS | Motor cos phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Depends of rating | 0.50 ... 1.00 | [Motor 1 Cosine Phi] (COS) | [ASYNC. MOTOR] (ASY-) | 347
UNS | Rated motor volt. | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Depends of rating | 100 V ... 690 V | [Rated motor volt.] (UnS) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) | 348
NCR | Rated mot. current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Depends of rating | - | [Rated mot. current] (nCr) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) | 349
FRS | Rated motor freq. | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 800.0 Hz | [Rated motor freq.] (FrS) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) | 350
NSP | Rated motor speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Depends of rating | 0 rpm ... 65535 rpm | [Rated motor speed] (nSP) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) | 351
TFR | Max frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 599.0 Hz | [Max frequency] (tFr) | [SIMPLY START] (SIM-) [MOTOR CONTROL] (drC-) | 352
TUN | Auto tuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] (nO) | - | [Auto tuning] (tUn) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) [SYNCHRONOUS MOTOR] (SYn-) | 353
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [Automatic autotune] (AUt) | [ASYNC. MOTOR] (ASY-) [SYNCHRONOUS MOTOR] (SYn-) | 354
TUS | Auto tuning state | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] (tAb) | - | [Auto tuning state] (tUS) | [SIMPLY START] (SIM-) [ASYNC. MOTOR] (ASY-) [SYNCHRONOUS MOTOR] (SYn-) | 355
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Motor control type] (Ctt) | [MOTOR CONTROL] (drC-) | 356
U1 | U1 | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U1] (U1) | [MOTOR CONTROL] (drC-) | 357
F1 | Freq pt 1on 5pt V/F | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F1] (F1) | [MOTOR CONTROL] (drC-) | 358
U2 | U2 | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U2] (U2) | [MOTOR CONTROL] (drC-) | 359
F2 | F2 | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F2] (F2) | [MOTOR CONTROL] (drC-) | 360
U3 | U3 | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U3] (U3) | [MOTOR CONTROL] (drC-) | 361
F3 | F3 | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F3] (F3) | [MOTOR CONTROL] (drC-) | 362
U4 | U4 | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U4] (U4) | [MOTOR CONTROL] (drC-) | 363
F4 | F4 | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F4] (F4) | [MOTOR CONTROL] (drC-) | 364
U5 | U5 | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U5] (U5) | [MOTOR CONTROL] (drC-) | 365
F5 | F5 | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [F5] (F5) | [MOTOR CONTROL] (drC-) | 366
NCRS | Nominal I sync. | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | Depends of rating | - | [Nominal I sync.] (nCrS) | [SYNCHRONOUS MOTOR] (SYn-) | 367
NSPS | Nom motor spdsync | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Depends of rating | 0 rpm ... 65535 rpm | [Nom motor spdsync] (nSPS) | [SYNCHRONOUS MOTOR] (SYn-) | 368
PPNS | Pole pairs | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Depends of rating | 1 ... 50 | [Pole pairs] (PPnS) | [SYNCHRONOUS MOTOR] (SYn-) | 369
TQS | Nominal motor torque sync | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Nm | Depends of rating | 0.1 Nm ... 6553.5 Nm | [Motor torque] (tqS) | [SYNCHRONOUS MOTOR] (SYn-) | 370
PHS | Syn. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [SYNCHRONOUS MOTOR] (SYn-) | 371
LDS | Autotune L d-axis | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Autotune L d-axis] (LdS) | [SYNCHRONOUS MOTOR] (SYn-) | 372
LQS | Autotune L q-axis | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Autotune L q-axis] (LqS) | [SYNCHRONOUS MOTOR] (SYn-) | 373
RSAS | Cust. stator R syn | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 mOhm | 0 mOhm | 0 mOhm ... 65535 mOhm | [Cust. stator R syn] (rSAS) | [SYNCHRONOUS MOTOR] (SYn-) | 374
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFr) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 375
SLP | Slip compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 376
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 | - | Configuration and settings | R | UINT (Unsigned16) | 1 | Depends of rating | 1 ... 100 | [Poles pair number] (PPn) | [SYNCHRONOUS MOTOR] (SYn-) | 377
RSA | Cust stator resist. | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 mOhm | 0 mOhm | 0 mOhm ... 65535 mOhm | [Cust stator resist.] (rSA) | [SYNCHRONOUS MOTOR] (SYn-) | 378
IDA | Idw | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | 0.0 A | 0.0 A ... 6553.5 A | [Idw] (IdA) | [ASYNC. MOTOR] (ASY-) | 379
LFA | Lfw | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 mH | 0.00 mH | 0.00 mH ... 655.35 mH | [Lfw] (LFA) | [ASYNC. MOTOR] (ASY-) | 380
TRA | Rotor time constant | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 65535 ms | [Cust. rotor t const.] (trA) | [ASYNC. MOTOR] (ASY-) | 381
FRSS | Nominal freq sync. | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 | - | Configuration and settings | R | UINT (Unsigned16) | 0.1 Hz | (NSPS * PPNS / 6) | 10.0 Hz ... 800.0 Hz | [Nominal freq sync.] (FrSS) | [SYNCHRONOUS MOTOR] (SYn-) | 382
SFR | Switching freq. | 16#0C1E = 3102 | 16#2001/3 | 16#70/01/67 = 112/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kHz | 4.0 kHz | 2.0 kHz ... 16.0 kHz | [Switching freq.] (SFr) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 383
CLI | Current Limitation | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (INV * 3 / 2) | - | [Current Limitation] (CLI) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 384
SFT | Switch. freq type | 16#0C1D = 3101 | 16#2001/2 | 16#70/01/66 = 112/01/102 | SFT | Configuration and settings | R/WS | WORD (Enumeration) | - | [SFR type 1] (HF1) | - | [Switch. freq type] (SFt) | [MOTOR CONTROL] (drC-) | 385
NRD | Noise reduction | 16#0C23 = 3107 | 16#2001/8 | 16#70/01/6C = 112/01/108 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Noise reduction] (nrd) | [MOTOR CONTROL] (drC-) | 386
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Dynamic] (dYnA) | - | [Boost activation] (bOA) | [MOTOR CONTROL] (drC-) | 387
SVL | Motor surge limit. | 16#3139 = 12601 | 16#2060/2 | 16#A0/01/02 = 160/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Motor surge limit.] (SUL) | [MOTOR CONTROL] (drC-) | 388
SOP | Volt surge limit. opt | 16#313A = 12602 | 16#2060/3 | 16#A0/01/03 = 160/01/03 | SOP | Configuration and settings | R/WS | WORD (Enumeration) | - | [10 µs] (10) | - | [Volt surge limit. opt] (SOP) | [MOTOR CONTROL] (drC-) | 389
VBR | Braking level | 16#3715 = 14101 | 16#206F/2 | 16#A7/01/66 = 167/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 V | Depends of rating | 335 V ... 995 V | [Braking level] (Ubr) | [MOTOR CONTROL] (drC-) | 390
LBA | Load sharing | 16#37DD = 14301 | 16#2071/2 | 16#A8/01/66 = 168/01/102 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Load sharing] (LbA) | [MOTOR CONTROL] (drC-) | 391
LBC | Load correction | 16#37DE = 14302 | 16#2071/3 | 16#A8/01/67 = 168/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Load correction] (LbC) | [MOTOR CONTROL] (drC-) [SETTINGS] (SEt-) | 392
LBC1 | Correction min spd | 16#37DF = 14303 | 16#2071/4 | 16#A8/01/68 = 168/01/104 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 598.9 Hz | [Correction min spd] (LbC1) | [MOTOR CONTROL] (drC-) | 393
LBC2 | Correction max spd | 16#37E0 = 14304 | 16#2071/5 | 16#A8/01/69 = 168/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.1 Hz | 0.1 Hz ... 599.0 Hz | [Correction max spd] (LbC2) | [MOTOR CONTROL] (drC-) | 394
LBC3 | Torque offset | 16#37E1 = 14305 | 16#2071/6 | 16#A8/01/6A = 168/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Torque offset] (LbC3) | [MOTOR CONTROL] (drC-) | 395
LBF | Sharing filter | 16#37E2 = 14306 | 16#2071/7 | 16#A8/01/6B = 168/01/107 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 0 ms ... 20000 ms | [Sharing filter] (LbF) | [MOTOR CONTROL] (drC-) | 396
FFM | Fan mode | 16#0C3A = 3130 | 16#2001/1F | 16#70/01/83 = 112/01/131 | FFM | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard] (Std) | - | [Fan mode] (FFM) | [SETTINGS] (SEt-) | 397
TCC | 2/3 wire control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2 wire] (2C) | - | [2/3 wire control] (tCC) | [SIMPLY START] (SIM-) [INPUTS / OUTPUTS CFG] (I_O-) | 398
TCT | 2 wire type | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Transition] (trn) | - | [2 wire type] (tCt) | [INPUTS / OUTPUTS CFG] (I_O-) | 399
RRS | Reverse assign. | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Reverse assign.] (rrS) | [INPUTS / OUTPUTS CFG] (I_O-) | 400
BSP | Reference template | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard] (bSd) | - | [Reference template] (bSP) | [INPUTS / OUTPUTS CFG] (I_O-) | 401
AI1T | AI1 Type | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] (10U) | - | [AI1 Type] (AI1t) | [AI1 CONFIGURATION] (AI1-) | 402
UIL1 | AI1 min value | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 min value] (UIL1) | [AI1 CONFIGURATION] (AI1-) | 403
UIH1 | AI1 max value | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 max value] (UIH1) | [AI1 CONFIGURATION] (AI1-) | 404
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1 CONFIGURATION] (AI1-) | 405
AI1E | AI1 Interm. point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point X] (AI1E) | [AI1 CONFIGURATION] (AI1-) | 406
AI1S | AI1 Interm. point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 CONFIGURATION] (AI1-) | 407
AI1L | AI1 range | 16#1182 = 4482 | 16#200E/53 | 16#77/01/53 = 119/01/83 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [0 - 100%] (POS) | - | [AI1 range] (AI1L) | [AI1 CONFIGURATION] (AI1-) | 408
AI2T | AI2 Type | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage +/-] (n10U) | - | [AI2 Type] (AI2t) | [AI2 CONFIGURATION] (AI2-) | 409
UIL2 | AI2 min value | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 min value] (UIL2) | [AI2 CONFIGURATION] (AI2-) | 410
UIH2 | AI2 max value | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 max value] (UIH2) | [AI2 CONFIGURATION] (AI2-) | 411
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2 CONFIGURATION] (AI2-) | 412
AI2L | AI2 range | 16#1183 = 4483 | 16#200E/54 | 16#77/01/54 = 119/01/84 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [0 - 100%] (POS) | - | [AI2 range] (AI2L) | [AI2 CONFIGURATION] (AI2-) | 413
AI2E | AI2 Interm. point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point X] (AI2E) | [AI2 CONFIGURATION] (AI2-) | 414
AI2S | AI2 Interm. point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 CONFIGURATION] (AI2-) | 415
AI3T | AI3 Type | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AI3 Type] (AI3t) | [AI3 CONFIGURATION] (AI3-) | 416
CRL3 | AI3 min. value | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 min. value] (CrL3) | [AI3 CONFIGURATION] (AI3-) | 417
CRH3 | AI3 max. value | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 max. value] (CrH3) | [AI3 CONFIGURATION] (AI3-) | 418
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3 CONFIGURATION] (AI3-) | 419
AI3L | AI3 range | 16#1184 = 4484 | 16#200E/55 | 16#77/01/55 = 119/01/85 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [0 - 100%] (POS) | - | [AI3 range] (AI3L) | [AI3 CONFIGURATION] (AI3-) | 420
AI3E | AI3 Interm. point X | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Interm. point X] (AI3E) | [AI3 CONFIGURATION] (AI3-) | 421
AI3S | AI3 Interm. point Y | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Interm. point Y] (AI3S) | [AI3 CONFIGURATION] (AI3-) | 422
PIL | RP min value | 16#33F6 = 13302 | 16#2067/3 | 16#A3/01/67 = 163/01/103 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 0.00 kHz | 0.00 kHz ... 20.00 kHz | [RP min value] (PIL) | [LI5 CONFIGURATION] (L5-) | 423
PFR | RP max value | 16#33F7 = 13303 | 16#2067/4 | 16#A3/01/68 = 163/01/104 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 20.00 kHz | 0.00 kHz ... 20.00 kHz | [RP max value] (PFr) | [LI5 CONFIGURATION] (L5-) | 424
PFI | RP filter | 16#33F8 = 13304 | 16#2067/5 | 16#A3/01/69 = 163/01/105 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [RP filter] (PFI) | [LI5 CONFIGURATION] (L5-) | 425
LO1 | LO1 assignment | 16#1391 = 5009 | 16#2014/A | 16#7A/01/0A = 122/01/10 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [LO1 assignment] (LO1) | [LO1 CONFIGURATION] (LO1-) | 426
LO1D | LO1 delay time | 16#1099 = 4249 | 16#200C/32 | 16#76/01/32 = 118/01/50 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [LO1 delay time] (LO1d) | [LO1 CONFIGURATION] (LO1-) | 427
LO1S | LO1 active at | 16#1071 = 4209 | 16#200C/A | 16#76/01/0A = 118/01/10 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [LO1 active at] (LO1S) | [LO1 CONFIGURATION] (LO1-) | 428
LO1H | LO1 holding time | 16#1085 = 4229 | 16#200C/1E | 16#76/01/1E = 118/01/30 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [LO1 holding time] (LO1H) | [LO1 CONFIGURATION] (LO1-) | 429
DO1 | DO1 assignment | 16#13A7 = 5031 | 16#2014/20 | 16#7A/01/20 = 122/01/32 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [DO1 assignment] (dO1) | [DO1 CONFIGURATION] (dO1-) | 430
DO1D | DO1 delay time | 16#10B9 = 4281 | 16#200C/52 | 16#76/01/52 = 118/01/82 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DO1 delay time] (dO1d) | [DO1 CONFIGURATION] (dO1-) | 431
DO1H | DO1 holding time | 16#10AF = 4271 | 16#200C/48 | 16#76/01/48 = 118/01/72 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DO1 holding time] (dO1H) | [DO1 CONFIGURATION] (dO1-) | 432
DO1S | DO1 active at | 16#10A5 = 4261 | 16#200C/3E | 16#76/01/3E = 118/01/62 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [DO1 active at] (dO1S) | [DO1 CONFIGURATION] (dO1-) | 433
AO1 | AO1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [AO1 assignment] (AO1) | [AO1 CONFIGURATION] (AO1-) | 434
AO1T | AO1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] (0A) | - | [AO1 Type] (AO1t) | [AO1 CONFIGURATION] (AO1-) | 435
AOL1 | AO1 min output | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AO1 min output] (AOL1) | [AO1 CONFIGURATION] (AO1-) | 436
AOH1 | AO1 max output | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AO1 max output] (AOH1) | [AO1 CONFIGURATION] (AO1-) | 437
UOL1 | AO1 min Output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AO1 min Output] (UOL1) | [AO1 CONFIGURATION] (AO1-) | 438
UOH1 | AO1 max Output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AO1 max Output] (UOH1) | [AO1 CONFIGURATION] (AO1-) | 439
ASL1 | Scaling AO1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AO1 min] (ASL1) | [AO1 CONFIGURATION] (AO1-) | 440
ASH1 | Scaling AO1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AO1 max] (ASH1) | [AO1 CONFIGURATION] (AO1-) | 441
AO1F | AO1 Filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AO1 Filter] (AO1F) | [AO1 CONFIGURATION] (AO1-) | 442
FR1 | Ref.1 channel | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Ref.1 channel] (Fr1) | [COMMAND] (CtL-) | 443
RIN | RV Inhibition | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [RV Inhibition] (rIn) | [COMMAND] (CtL-) | 444
PST | Stop Key priority | 16#FA02 = 64002 |  | = | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Stop Key priority] (PSt) | [COMMAND] (CtL-) | 445
CHCF | Profile | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not separ.] (SIM) | - | [Profile] (CHCF) | [COMMAND] (CtL-) | 446
CCS | Cmd switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [ch1 active] (Cd1) | - | [Cmd switching] (CCS) | [COMMAND] (CtL-) | 447
CD1 | Cmd channel 1 | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminals] (tEr) | - | [Cmd channel 1] (Cd1) | [COMMAND] (CtL-) | 448
CD2 | Cmd channel 2 | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus] (Mdb) | - | [Cmd channel 2] (Cd2) | [COMMAND] (CtL-) | 449
RFC | Ref. 2 switching | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Ref. 2 switching] (rFC) | [COMMAND] (CtL-) | 450
FR2 | Ref.2 channel | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Ref.2 channel] (Fr2) | [COMMAND] (CtL-) | 451
COP | Copy channel 1<>2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Copy channel 1<>2] (COP) | [COMMAND] (CtL-) | 452
FN1 | F1 key assignment | 16#34BD = 13501 | 16#2069/2 | 16#A4/01/66 = 164/01/102 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F1 key assignment] (Fn1) | [COMMAND] (CtL-) | 453
FN2 | F2 key assignment | 16#34BE = 13502 | 16#2069/3 | 16#A4/01/67 = 164/01/103 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F2 key assignment] (Fn2) | [COMMAND] (CtL-) | 454
FN3 | F3 key assignment | 16#34BF = 13503 | 16#2069/4 | 16#A4/01/68 = 164/01/104 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F3 key assignment] (Fn3) | [COMMAND] (CtL-) | 455
FN4 | F4 key assignment | 16#34C0 = 13504 | 16#2069/5 | 16#A4/01/69 = 164/01/105 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [F4 key assignment] (Fn4) | [COMMAND] (CtL-) | 456
BMP | HMI cmd. | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop] (StOP) | - | [HMI cmd.] (bMP) | [COMMAND] (CtL-) | 457
RCB | Ref 1B switching | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [ch1 active] (Fr1) | - | [Ref 1B switching] (rCb) | [REFERENCE SWITCH.] (rEF-) | 458
FR1B | Ref.1B channel | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Ref.1B channel] (Fr1b) | [REFERENCE SWITCH.] (rEF-) | 459
SA2 | Summing ref. 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Summing ref. 2] (SA2) | [REF. OPERATIONS] (OAI-) | 460
SA3 | Summing ref. 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Summing ref. 3] (SA3) | [REF. OPERATIONS] (OAI-) | 461
DA2 | Assignment of substract setpoint 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Subtract ref. 2] (dA2) | [REF. OPERATIONS] (OAI-) | 462
DA3 | Assignment of substract setpoint 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Subtract ref. 3] (dA3) | [REF. OPERATIONS] (OAI-) | 463
MA2 | Multiplier ref. 2 | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Multiplier ref. 2] (MA2) | [REF. OPERATIONS] (OAI-) | 464
MA3 | Multiplier ref. 3 | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Multiplier ref. 3] (MA3) | [REF. OPERATIONS] (OAI-) | 465
RPT | Ramp type | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear] (LIn) | - | [Ramp type] (rPt) | [RAMP] (rPt-) | 466
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [0.1] (0.1) | - | [Ramp increment] (Inr) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 467
ACC | Acceleration | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Acceleration] (ACC) | [RAMP] (rPt-) [SIMPLY START] (SIM-) [SETTINGS] (SEt-) | 468
DEC | Deceleration | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Deceleration] (dEC) | [RAMP] (rPt-) [SIMPLY START] (SIM-) [SETTINGS] (SEt-) | 469
TA1 | Begin Acc round | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Acc round] (tA1) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 470
TA2 | End Acc round | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Acc round] (tA2) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 471
TA3 | Begin Dec round | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Dec round] (tA3) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 472
TA4 | End Dec round | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Dec round] (tA4) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 473
FRT | Ramp 2 threshold | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Ramp 2 threshold] (Frt) | [RAMP] (rPt-) | 474
RPS | Ramp switch assignment | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Ramp switch ass.] (rPS) | [RAMP] (rPt-) | 475
AC2 | Acceleration 2 | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Acceleration 2] (AC2) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 476
DE2 | Deceleration 2 | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Deceleration 2] (dE2) | [RAMP] (rPt-) [SETTINGS] (SEt-) | 477
BRA | Dec ramp adapt. | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Dec ramp adapt.] (brA) | [RAMP] (rPt-) | 478
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [Type of stop] (Stt) | [STOP CONFIGURATION] (Stt-) | 479
FFT | Freewheel stop Thd | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | (Max (((call NominalMotorFrequency []) / 250), 2)) | 0.2 Hz ... 599.0 Hz | [Freewheel stop Thd] (FFt) | [STOP CONFIGURATION] (Stt-) [SETTINGS] (SEt-) | 480
NST | Freewheel stop ass. | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Freewheel stop ass.] (nSt) | [STOP CONFIGURATION] (Stt-) | 481
FST | Fast stop assign. | 16#2BC4 = 11204 | 16#2052/5 | 16#99/01/05 = 153/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Fast stop assign.] (FSt) | [STOP CONFIGURATION] (Stt-) | 482
DCF | Ramp divider | 16#2BDE = 11230 | 16#2052/1F | 16#99/01/1F = 153/01/31 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 4 | 0 ... 10 | [Ramp divider] (dCF) | [STOP CONFIGURATION] (Stt-) [SETTINGS] (SEt-) | 483
DCI | DC injection assign. | 16#2BC3 = 11203 | 16#2052/4 | 16#99/01/04 = 153/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [DC injection assign.] (dCI) | [STOP CONFIGURATION] (Stt-) | 484
IDC | DC inject. level 1 | 16#2BCA = 11210 | 16#2052/B | 16#99/01/0B = 153/01/11 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (INV * 16 / 25) | - | [DC inject. level 1] (IdC) | [STOP CONFIGURATION] (Stt-) [SETTINGS] (SEt-) | 485
TDI | DC injection time 1 | 16#2BCD = 11213 | 16#2052/E | 16#99/01/0E = 153/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC injection time 1] (tdI) | [STOP CONFIGURATION] (Stt-) [SETTINGS] (SEt-) | 486
IDC2 | DC inject. level 2 | 16#2BCC = 11212 | 16#2052/D | 16#99/01/0D = 153/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (INV / 2) | - | [DC inject. level 2] (IdC2) | [STOP CONFIGURATION] (Stt-) [SETTINGS] (SEt-) | 487
TDC | DC injection time 2 | 16#2BCB = 11211 | 16#2052/C | 16#99/01/0C = 153/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC injection time 2] (tdC) | [AUTO DC INJECTION] (AdC-) [SETTINGS] (SEt-) | 488
ADC | Auto DC injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual | - | [Auto DC injection] (AdC) | [CANopen] (CnO-) | 489
SDC1 | Auto DC inj. level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (INV * 7 / 10) | - | [Auto DC inj. level 1] (SdC1) | [AUTO DC INJECTION] (AdC-) [SETTINGS] (SEt-) | 490
TDC1 | Auto DC inj. time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC inj. time 1] (tdC1) | [AUTO DC INJECTION] (AdC-) [SETTINGS] (SEt-) | 491
SDC2 | Auto DC inj. level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (INV / 2) | - | [Auto DC inj. level 2] (SdC2) | [AUTO DC INJECTION] (AdC-) [SETTINGS] (SEt-) | 492
TDC2 | Auto DC inj. time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC inj. time 2] (tdC2) | [AUTO DC INJECTION] (AdC-) [SETTINGS] (SEt-) | 493
JOG | JOG | 16#2B66 = 11110 | 16#2051/B | 16#98/01/6F = 152/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [JOG] (JOG) | [JOG] (JOG-) | 494
JGF | Jog frequency | 16#2B67 = 11111 | 16#2051/C | 16#98/01/70 = 152/01/112 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 10.0 Hz | [Jog frequency] (JGF) | [SETTINGS] (SEt-) | 495
JGT | Jog delay | 16#2B68 = 11112 | 16#2051/D | 16#98/01/71 = 152/01/113 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 2.0 s | [Jog delay] (JGt) | [SETTINGS] (SEt-) | 496
PS2 | 2 preset speeds | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [2 preset speeds] (PS2) | [PRESET SPEEDS] (PSS-) | 497
PS4 | 4 preset speeds | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [4 preset speeds] (PS4) | [PRESET SPEEDS] (PSS-) | 498
PS8 | 8 preset speeds | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [8 preset speeds] (PS8) | [PRESET SPEEDS] (PSS-) | 499
PS16 | 16 preset speeds | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [16 preset speeds] (PS16) | [PRESET SPEEDS] (PSS-) | 500
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 2] (SP2) | [SETTINGS] (SEt-) | 501
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 3] (SP3) | [SETTINGS] (SEt-) | 502
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 4] (SP4) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 503
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 5] (SP5) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 504
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 6] (SP6) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 505
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 7] (SP7) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 506
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 8] (SP8) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 507
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 9] (SP9) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 508
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 10] (SP10) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 509
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 11] (SP11) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 510
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 12] (SP12) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 511
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 13] (SP13) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 512
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 14] (SP14) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 513
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 15] (SP15) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 514
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 599.0 Hz | [Preset speed 16] (SP16) | [PRESET SPEEDS] (PSS-) [SETTINGS] (SEt-) | 515
USP | + speed assignment | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [+ speed assignment] (USP) | [+/- SPEED] (UPd-) | 516
DSP | -Speed assignment | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [-Speed assignment] (dSP) | [+/- SPEED] (UPd-) | 517
STR | Reference saved | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Reference saved] (Str) | [IGBT TESTS] (tIt-) | 518
USI | + Speed assignment | 16#2D00 = 11520 | 16#2055/15 | 16#9A/01/79 = 154/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [+ speed assignment] (USI) | [+/-SPEED AROUND REF.] (SrE-) | 519
DSI | -Speed assignment | 16#2D01 = 11521 | 16#2055/16 | 16#9A/01/7A = 154/01/122 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [-Speed assignment] (dSI) | [+/-SPEED AROUND REF.] (SrE-) | 520
SRP | +/-Speed limitation | 16#2CF1 = 11505 | 16#2055/6 | 16#9A/01/6A = 154/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 50 % | [+/-Speed limitation] (SrP) | [+/-SPEED AROUND REF.] (SrE-) [SETTINGS] (SEt-) | 521
SPM | Ref. memo ass. | 16#212B = 8491 | 16#2036/5C | 16#8B/01/5C = 139/01/92 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Ref. memo ass.] (SPM) | [MEMO REFERENCE] (SPM-) | 522
FLU | Motor fluxing | 16#364E = 13902 | 16#206D/3 | 16#A6/01/67 = 166/01/103 | FLU | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (FnO) | - | [Motor fluxing] (FLU) | [FLUXING BY LI] (FLI-) [ASYNC. MOTOR] (ASY-) [SETTINGS] (SEt-) | 523
FLI | Fluxing assignment | 16#364D = 13901 | 16#206D/2 | 16#A6/01/66 = 166/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Fluxing assignment] (FLI) | [FLUXING BY LI] (FLI-) | 524
AST | Auto angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [PSIO align.] (PSIO) | - | [Angle setting type] (ASt) | [FLUXING BY LI] (FLI-) [SYNCHRONOUS MOTOR] (SYn-) | 525
HFI | Activation of HF injection in RUN | 16#3CF0 = 15600 | 16#207E/1 | 16#AF/01/01 = 175/01/01 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [HF inj. activation] (HFI) | [SYNCHRONOUS MOTOR] (SYn-) | 526
HIR | Ratio for the current level of the HF injection signal | 16#3CF2 = 15602 | 16#207E/3 | 16#AF/01/03 = 175/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 200 % | [HF current level] (HIr) | [SYNCHRONOUS MOTOR] (SYn-) | 527
SPB | Bandwidth of the stator frequency Pll | 16#3CF3 = 15603 | 16#207E/4 | 16#AF/01/04 = 175/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 25 Hz | 0 Hz ... 100 Hz | [HF pll bandwidth] (SPb) | [SYNCHRONOUS MOTOR] (SYn-) | 528
ILR | Ratio of In for the Id current level | 16#3CF5 = 15605 | 16#207E/6 | 16#AF/01/06 = 175/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 200 % | [Injection level align.] (ILr) | [SYNCHRONOUS MOTOR] (SYn-) | 529
SIR | Ratio of In for the start up injected current | 16#3CF6 = 15606 | 16#207E/7 | 16#AF/01/07 = 175/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [Boost level align.] (SIr) | [SYNCHRONOUS MOTOR] (SYn-) | 530
MCR | Ratio of In for the maximum current | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | [Auto] (AUtO) | [Auto] (AUtO) ... 300 % | [PSI align curr. max] (MCr) | [SYNCHRONOUS MOTOR] (SYn-) | 531
PEC | Position error compensation | 16#3CF8 = 15608 | 16#207E/9 | 16#AF/01/09 = 175/01/09 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 500 % | [Angle error Comp.] (PEC) | [SYNCHRONOUS MOTOR] (SYn-) | 532
BLC | Brake assignment | 16#2711 = 10001 | 16#2046/2 | 16#93/01/02 = 147/01/02 | BLC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Brake assignment] (bLC) | [BRAKE LOGIC CONTROL] (bLC-) | 533
BST | Movement type | 16#2718 = 10008 | 16#2046/9 | 16#93/01/09 = 147/01/09 | BST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Hoisting] (UEr) | - | [Movement type] (bSt) | [BRAKE LOGIC CONTROL] (bLC-) | 534
BCI | Brake contact | 16#2719 = 10009 | 16#2046/A | 16#93/01/0A = 147/01/10 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Brake contact] (bCI) | [BRAKE LOGIC CONTROL] (bLC-) | 535
BIP | Brake impulse | 16#2717 = 10007 | 16#2046/8 | 16#93/01/08 = 147/01/08 | BIP | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual | - | [Brake impulse] (bIP) | [BRAKE LOGIC CONTROL] (bLC-) | 536
IBR | Brake release I FW | 16#2716 = 10006 | 16#2046/7 | 16#93/01/07 = 147/01/07 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | - | [Brake release I FW] (Ibr) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 537
IRD | Brake release I Rev | 16#271B = 10011 | 16#2046/C | 16#93/01/0C = 147/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | - | [Brake release I Rev] (Ird) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 538
BRT | Brake Release time | 16#2714 = 10004 | 16#2046/5 | 16#93/01/05 = 147/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake Release time] (brt) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 539
BIR | Brake release freq | 16#271C = 10012 | 16#2046/D | 16#93/01/0D = 147/01/13 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | [Auto] (AUtO) ... 10.0 Hz | [Brake release freq] (bIr) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 540
BEN | Brake engage freq | 16#2713 = 10003 | 16#2046/4 | 16#93/01/04 = 147/01/04 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | [Auto] (AUtO) | [Auto] (AUtO) ... 10.0 Hz | [Brake engage freq] (bEn) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 541
TBE | Brake engage delay | 16#271A = 10010 | 16#2046/B | 16#93/01/0B = 147/01/11 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage delay] (tbE) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 542
BET | Brake engage time | 16#2715 = 10005 | 16#2046/6 | 16#93/01/06 = 147/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage time] (bEt) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 543
BED | Engage at reversal | 16#2724 = 10020 | 16#2046/15 | 16#93/01/15 = 147/01/21 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [Engage at reversal] (bEd) | [BRAKE LOGIC CONTROL] (bLC-) | 544
JDC | Jump at reversal | 16#271D = 10013 | 16#2046/E | 16#93/01/0E = 147/01/14 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | [Auto] (AUtO) ... 10.0 Hz | [Jump at reversal] (JdC) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 545
TTR | Time to restart | 16#2726 = 10022 | 16#2046/17 | 16#93/01/17 = 147/01/23 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 15.00 s | [Time to restart] (ttr) | [BRAKE LOGIC CONTROL] (bLC-) [SETTINGS] (SEt-) | 546
BRH | Brake configuration | 16#2742 = 10050 | 16#2046/33 | 16#93/01/33 = 147/01/51 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 547
BRR | Current ramp time | 16#271F = 10015 | 16#2046/10 | 16#93/01/10 = 147/01/16 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Current ramp time] (brr) | [BRAKE LOGIC CONTROL] (bLC-) | 548
PES | Weight sensor ass. | 16#2756 = 10070 | 16#2046/47 | 16#93/01/47 = 147/01/71 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Weight sensor ass.] (PES) | [EXTERNAL WEIGHT MEAS.] (ELM-) | 549
LP1 | Point 1 X | 16#2757 = 10071 | 16#2046/48 | 16#93/01/48 = 147/01/72 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 0.00 % | 0.00 % ... 99.99 % | [Point 1 X] (LP1) | [EXTERNAL WEIGHT MEAS.] (ELM-) | 550
CP1 | Point 1Y | 16#2758 = 10072 | 16#2046/49 | 16#93/01/49 = 147/01/73 | - | Configuration and settings | R/WS | INT (Signed16) | 0.1 A | (INV * -1) | -3276.7 A ... 3276.7 A | [Point 1Y] (CP1) | [EXTERNAL WEIGHT MEAS.] (ELM-) | 551
LP2 | Point 2 X | 16#2759 = 10073 | 16#2046/4A | 16#93/01/4A = 147/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 % | 50.00 % | 0.01 % ... 100.00 % | [Point 2 X] (LP2) | [EXTERNAL WEIGHT MEAS.] (ELM-) | 552
CP2 | Point 2Y | 16#275A = 10074 | 16#2046/4B | 16#93/01/4B = 147/01/75 | - | Configuration and settings | R/WS | INT (Signed16) | 0.1 A | 0.0 A | -3276.7 A ... 3276.7 A | [Point 2Y] (CP2) | [EXTERNAL WEIGHT MEAS.] (ELM-) | 553
IBRA | Ibr 4-20 mA loss | 16#275B = 10075 | 16#2046/4C | 16#93/01/4C = 147/01/76 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | 0.0 A | - | [Ibr 4-20 mA loss] (IbrA) | [EXTERNAL WEIGHT MEAS.] (ELM-) | 554
HSO | High speed hoisting | 16#300D = 12301 | 16#205D/2 | 16#9E/01/66 = 158/01/102 | HSO | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [High speed hoisting] (HSO) | [HIGH SPEED HOISTING] (HSH-) | 555
COF | Motor speed coeff. | 16#300F = 12303 | 16#205D/4 | 16#9E/01/68 = 158/01/104 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 100 % | [Motor speed coeff.] (COF) | [HIGH SPEED HOISTING] (HSH-) | 556
COR | Gen. speed coeff | 16#3010 = 12304 | 16#205D/5 | 16#9E/01/69 = 158/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 100 % | [Gen. speed coeff] (COr) | [HIGH SPEED HOISTING] (HSH-) | 557
TOS | Load measuring tm. | 16#3013 = 12307 | 16#205D/8 | 16#9E/01/6C = 158/01/108 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.50 s | 0.10 s ... 65.00 s | [Load measuring tm.] (tOS) | [HIGH SPEED HOISTING] (HSH-) | 558
OSP | Measurement spd | 16#3011 = 12305 | 16#205D/6 | 16#9E/01/6A = 158/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [Measurement spd] (OSP) | [HIGH SPEED HOISTING] (HSH-) | 559
CLO | High speed I Limit | 16#300E = 12302 | 16#205D/3 | 16#9E/01/67 = 158/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (call INV_DefaultValue []) | - | [High speed I Limit] (CLO) | [HIGH SPEED HOISTING] (HSH-) | 560
SCL | I Limit. frequency | 16#3012 = 12306 | 16#205D/7 | 16#9E/01/6B = 158/01/107 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 599.0 Hz | [I Limit. frequency] (SCL) | [HIGH SPEED HOISTING] (HSH-) | 561
RSD | Rope slack config. | 16#3021 = 12321 | 16#205D/16 | 16#9E/01/7A = 158/01/122 | RSD | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Rope slack config.] (rSd) | [HIGH SPEED HOISTING] (HSH-) | 562
RSTL | Rope slack trq level | 16#3022 = 12322 | 16#205D/17 | 16#9E/01/7B = 158/01/123 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Rope slack trq level] (rStL) | [HIGH SPEED HOISTING] (HSH-) | 563
PIF | PID feedback ass. | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [PID feedback ass.] (PIF) | [PID REGULATOR] (PId-) | 564
PIF1 | Min PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | 0 ... 32767 | [Min PID feedback] (PIF1) | [PID REGULATOR] (PId-) | 565
PIF2 | Max PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1000 | 0 ... 32767 | [Max PID feedback] (PIF2) | [PID REGULATOR] (PId-) | 566
PIP1 | Min PID reference | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 150 | 0 ... 32767 | [Min PID reference] (PIP1) | [PID REGULATOR] (PId-) | 567
PIP2 | Max PID reference | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 900 | 0 ... 32767 | [Max PID reference] (PIP2) | [PID REGULATOR] (PId-) | 568
PII | Act. internal PID ref. | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Act. internal PID ref.] (PII) | [PID REGULATOR] (PId-) | 569
RPI | Internal PID ref. | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 150 | 0 ... 32767 | [Internal PID ref.] (rPI) | [PID REGULATOR] (PId-) [MONITORING] (SUP-) [REFERENCE SWITCH.] (rEF-) [MONIT. PI] (MPI-) | 570
RPG | PID prop. gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID prop. gain] (rPG) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 571
RIG | PID integral gain | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID integral gain] (rIG) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 572
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (rdG) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 573
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PrP) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 574
PIC | PID correct. reverse | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [PID correct. reverse] (PIC) | [PID REGULATOR] (PId-) | 575
POL | Min PID output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -599.0 Hz ... 599.0 Hz | [Min PID output] (POL) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 576
POH | Max PID output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 | - | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 599.0 Hz | [Max PID output] (POH) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 577
PAL | Min fbk alarm | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | - | [Min fbk alarm] (PAL) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 578
PAH | Max fbk alarm | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1000 | - | [Max fbk alarm] (PAH) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 579
PER | PID error Alarm | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 100 | - | [PID error Alarm] (PEr) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 580
PIS | PID integral reset | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [PID integral reset] (PIS) | [PID REGULATOR] (PId-) | 581
FPI | Speed ref. assign. | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Speed ref. assign.] (FPI) | [PID REGULATOR] (PId-) | 582
PSR | Speed input % | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSr) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 583
PAU | Auto/Manual assign. | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Auto/Manual assign.] (PAU) | [PID REGULATOR] (PId-) | 584
PIM | Manual reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Manual reference] (PIM) | [PID REGULATOR] (PId-) | 585
TLS | Low speed time out | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low speed time out] (tLS) | [PID REGULATOR] (PId-) [SETTINGS] (SEt-) | 586
RSL | PID wake up thresh. | 16#2EB8 = 11960 | 16#2059/3D | 16#9C/01/A1 = 156/01/161 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 | 0.0 | 0.0 ... 100.0 | [PID wake up thresh.] (rSL) | [PID REGULATOR] (PId-) | 587
PR2 | 2 preset PID ref. | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [2 preset PID ref.] (Pr2) | [PID PRESET REFERENCES] (PrI-) | 588
PR4 | 4 preset PID ref. | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [4 preset PID ref.] (Pr4) | [PID PRESET REFERENCES] (PrI-) | 589
RP2 | Preset ref. PID 2 | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 300 | 0 ... 32767 | [Preset ref. PID 2] (rP2) | [SETTINGS] (SEt-) | 590
RP3 | Preset ref. PID 3 | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 600 | 0 ... 32767 | [Preset ref. PID 3] (rP3) | [PDO3 IMAGE] (P03-) | 591
RP4 | Preset ref. PID 4 | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 900 | 0 ... 32767 | [Preset ref. PID 4] (rP4) | [PID PRESET REFERENCES] (PrI-) [SETTINGS] (SEt-) | 592
TLA | Torque limit. activ. | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Torque limit. activ.] (tLA) | [TORQUE LIMITATION] (tOL-) | 593
INTP | Torque limitation unit | 16#23FF = 9215 | 16#203E/10 | 16#8F/01/10 = 143/01/16 | INCPER | Configuration and settings | R/WS | WORD (Enumeration) | - | [1%] (1) | - | [Torque increment] (IntP) | [TORQUE LIMITATION] (tOL-) | 594
TLIM | Motoring torque lim | 16#23FB = 9211 | 16#203E/C | 16#8F/01/0C = 143/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Motoring torque lim] (tLIM) | [TORQUE LIMITATION] (tOL-) [SETTINGS] (SEt-) | 595
TLIG | Gen. torque lim | 16#23FC = 9212 | 16#203E/D | 16#8F/01/0D = 143/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | Refer to programming manual | [Gen. torque lim] (tLIG) | [TORQUE LIMITATION] (tOL-) [SETTINGS] (SEt-) | 596
TAA | Torque ref. assign. | 16#23FE = 9214 | 16#203E/F | 16#8F/01/0F = 143/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Torque ref. assign.] (tAA) | [TORQUE LIMITATION] (tOL-) | 597
TLC | Analog limit. act. | 16#23FD = 9213 | 16#203E/E | 16#8F/01/0E = 143/01/14 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Analog limit. act.] (tLC) | [TORQUE LIMITATION] (tOL-) | 598
LC2 | Current limit 2 | 16#23F2 = 9202 | 16#203E/3 | 16#8F/01/03 = 143/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Current limit 2] (LC2) | [2nd CURRENT LIMIT.] (CLI-) | 599
CL2 | I Limit. 2 value | 16#23F3 = 9203 | 16#203E/4 | 16#8F/01/04 = 143/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 A | (INV * 3 / 2) | - | [I Limit. 2 value] (CL2) | [2nd CURRENT LIMIT.] (CLI-) [SETTINGS] (SEt-) | 600
LLC | Line contactor ass. | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [Line contactor ass.] (LLC) | [LINE Contactor Command] (LLC-) | 601
LES | Drive lock | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Drive lock] (LES) | [LINE Contactor Command] (LLC-) | 602
LCT | Mains V. time out | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 5 s ... 999 s | [Mains V. time out] (LCt) | [LINE Contactor Command] (LLC-) | 603
OCC | Out. contactor ass. | 16#3330 = 13104 | 16#2065/5 | 16#A2/01/69 = 162/01/105 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [Out. contactor ass.] (OCC) | [OUTPUT CONTACTOR CMD] (OCC-) | 604
RCA | Output contact. fdbk | 16#332F = 13103 | 16#2065/4 | 16#A2/01/68 = 162/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Output contact. fdbk] (rCA) | [OUTPUT CONTACTOR CMD] (OCC-) | 605
DBS | Delay to motor run | 16#332D = 13101 | 16#2065/2 | 16#A2/01/66 = 162/01/102 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.15 s | 0.05 s ... 60.00 s | [Delay to motor run] (dbS) | [OUTPUT CONTACTOR CMD] (OCC-) | 606
DAS | Delay to open cont. | 16#332E = 13102 | 16#2065/3 | 16#A2/01/67 = 162/01/103 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 5.00 s | [Delay to open cont.] (dAS) | [OUTPUT CONTACTOR CMD] (OCC-) | 607
SAF | Stop FW limit sw. | 16#30D5 = 12501 | 16#205F/2 | 16#9F/01/66 = 159/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Stop FW limit sw.] (SAF) | [POSITIONING BY SENSORS] (LPO-) | 608
SAR | Stop RV limit sw. | 16#30D6 = 12502 | 16#205F/3 | 16#9F/01/67 = 159/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Stop RV limit sw.] (SAr) | [POSITIONING BY SENSORS] (LPO-) | 609
SAL | Stop limit config. | 16#30DC = 12508 | 16#205F/9 | 16#9F/01/6D = 159/01/109 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active low] (LO) | - | [Stop limit config.] (SAL) | [POSITIONING BY SENSORS] (LPO-) | 610
DAF | Assignment of slowdown forward | 16#30D7 = 12503 | 16#205F/4 | 16#9F/01/68 = 159/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Slowdown forward] (dAF) | [POSITIONING BY SENSORS] (LPO-) | 611
DAR | Assignment of slowdown reverse | 16#30D8 = 12504 | 16#205F/5 | 16#9F/01/69 = 159/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Slowdown reverse] (dAr) | [POSITIONING BY SENSORS] (LPO-) | 612
DAL | Slowdown limit cfg. | 16#30DD = 12509 | 16#205F/A | 16#9F/01/6E = 159/01/110 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active low] (LO) | - | [Slowdown limit cfg.] (dAL) | [POSITIONING BY SENSORS] (LPO-) | 613
CLS | Disable limit sw. | 16#30DB = 12507 | 16#205F/8 | 16#9F/01/6C = 159/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Disable limit sw.] (CLS) | [POSITIONING BY SENSORS] (LPO-) | 614
PAS | Stop type | 16#30DA = 12506 | 16#205F/7 | 16#9F/01/6B = 159/01/107 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] (rMP) | - | [Stop type] (PAS) | [POSITIONING BY SENSORS] (LPO-) | 615
DSF | Deceleration type | 16#30D9 = 12505 | 16#205F/6 | 16#9F/01/6A = 159/01/106 | DSF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] (Std) | - | [Deceleration type] (dSF) | [POSITIONING BY SENSORS] (LPO-) | 616
STD | Stop distance | 16#30E9 = 12521 | 16#205F/16 | 16#9F/01/7A = 159/01/122 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m | [No] (nO) | [No] (nO) ... 10.00 m | [Stop distance] (Std) | [POSITIONING BY SENSORS] (LPO-) | 617
NLS | Rated linear speed | 16#30DF = 12511 | 16#205F/C | 16#9F/01/70 = 159/01/112 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 m/s | 1.00 m/s | 0.20 m/s ... 5.00 m/s | [Rated linear speed] (nLS) | [POSITIONING BY SENSORS] (LPO-) | 618
SFD | Stop corrector | 16#30EA = 12522 | 16#205F/17 | 16#9F/01/7B = 159/01/123 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 50 % ... 200 % | [Stop corrector] (SFd) | [POSITIONING BY SENSORS] (LPO-) | 619
CHM | Multimotors | 16#1F59 = 8025 | 16#2032/1A | 16#89/01/1A = 137/01/26 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Multimotors] (CHM) | [MULTIMOTORS/CONFIG.] (MMC-) | 620
CNF1 | 2 Configurations | 16#1F55 = 8021 | 16#2032/16 | 16#89/01/16 = 137/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [2 Configurations] (CnF1) | [MULTIMOTORS/CONFIG.] (MMC-) | 621
CNF2 | 3 Configurations | 16#1F56 = 8022 | 16#2032/17 | 16#89/01/17 = 137/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [3 Configurations] (CnF2) | [MULTIMOTORS/CONFIG.] (MMC-) | 622
TUL | Auto-tune assign. | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Auto-tune assign.] (tUL) | [AUTO TUNING BY LI] (tnL-) | 623
SDS | USPL/USPH scale factor | 16#2EE1 = 12001 | 16#205A/2 | 16#9D/01/02 = 157/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 30.0 | 0.1 ... 200.0 | [Scale factor display] (SdS) | [SETTINGS] (SEt-) | 624
SPD1 | Customer unit 1 | 16#2EE8 = 12008 | 16#205A/9 | 16#9D/01/09 = 157/01/09 | - | Configuration and settings | R | UINT (Unsigned16) | 0.01 |  | - | [Cust. output value] (SPd1) | [MONITORING] (MOn-) | 625
SPD2 | Customer unit 2 | 16#2EE9 = 12009 | 16#205A/A | 16#9D/01/0A = 157/01/10 | - | Configuration and settings | R | UINT (Unsigned16) | 0.1 |  | - | [Cust. output value] (SPd2) | [MONITORING] (MOn-) | 626
SPD3 | Customer unit 3 | 16#2EEA = 12010 | 16#205A/B | 16#9D/01/0B = 157/01/11 | - | Configuration and settings | R | UINT (Unsigned16) | 1 |  | - | [Cust. output value] (SPd3) | [MONITORING] (MOn-) | 627
TRC | Yarn control | 16#2FA9 = 12201 | 16#205C/2 | 16#9E/01/02 = 158/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Yarn control] (trC) | [TRAVERSE CONTROL] (tr0-) | 628
TRH | Traverse frequency high | 16#2FAA = 12202 | 16#205C/3 | 16#9E/01/03 = 158/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 10.0 Hz | [Traverse freq. high] (trH) | [TRAVERSE CONTROL] (tr0-) [SETTINGS] (SEt-) | 629
TRL | Traverse frequency low | 16#2FAB = 12203 | 16#205C/4 | 16#9E/01/04 = 158/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 4.0 Hz | 0.0 Hz ... 10.0 Hz | [Traverse Freq. Low] (trL) | [TRAVERSE CONTROL] (tr0-) [SETTINGS] (SEt-) | 630
QSH | Quick step High | 16#2FAC = 12204 | 16#205C/5 | 16#9E/01/05 = 158/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [Quick step High] (qSH) | [TRAVERSE CONTROL] (tr0-) [SETTINGS] (SEt-) | 631
QSL | Quick step Low | 16#2FAD = 12205 | 16#205C/6 | 16#9E/01/06 = 158/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [Quick step Low] (qSL) | [TRAVERSE CONTROL] (tr0-) [SETTINGS] (SEt-) | 632
TUP | Traverse ctrl. accel. | 16#2FAE = 12206 | 16#205C/7 | 16#9E/01/07 = 158/01/07 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 4.0 s | 0.1 s ... 999.9 s | [Traverse ctrl. accel.] (tUP) | [TRAVERSE CONTROL] (tr0-) | 633
TDN | Traverse ctrl. decel | 16#2FAF = 12207 | 16#205C/8 | 16#9E/01/08 = 158/01/08 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 4.0 s | 0.1 s ... 999.9 s | [Traverse ctrl. decel] (tdn) | [TRAVERSE CONTROL] (tr0-) | 634
TBO | Reel time | 16#2FB0 = 12208 | 16#205C/9 | 16#9E/01/09 = 158/01/09 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 9999 min | [Reel time] (tbO) | [TRAVERSE CONTROL] (tr0-) | 635
EBO | End reel | 16#2FB5 = 12213 | 16#205C/E | 16#9E/01/0E = 158/01/14 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [End reel] (EbO) | [TRAVERSE CONTROL] (tr0-) | 636
SNC | Counter wobble | 16#2FB4 = 12212 | 16#205C/D | 16#9E/01/0D = 158/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Counter wobble] (SnC) | [TRAVERSE CONTROL] (tr0-) | 637
TSY | Sync. wobble | 16#2FB6 = 12214 | 16#205C/F | 16#9E/01/0F = 158/01/15 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  | - | [Sync. wobble] (tSY) | [TRAVERSE CONTROL] (tr0-) | 638
DTF | Decrease ref. speed | 16#2FB3 = 12211 | 16#205C/C | 16#9E/01/0C = 158/01/12 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Decrease ref. speed] (dtF) | [TRAVERSE CONTROL] (tr0-) | 639
RTR | Init. traverse ctrl | 16#2FB2 = 12210 | 16#205C/B | 16#9E/01/0B = 158/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Init. traverse ctrl] (rtr) | [TRAVERSE CONTROL] (tr0-) | 640
PTCL | LI6 = PTC probe | 16#3393 = 13203 | 16#2066/4 | 16#A3/01/04 = 163/01/04 | PTCX | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [LI6 = PTC probe] (PtCL) | [PTC MANAGEMENT] (PtC-) | 641
RSF | Fault reset | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Fault reset] (rSF) | [FAULT RESET] (rSt-) | 642
RP | Product reset | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Product reset] (rP) | [FAULT RESET] (rSt-) | 643
RPA | Product reset assig. | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Product reset assig.] (rPA) | [FAULT RESET] (rSt-) | 644
ATR | Automatic restart | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Automatic restart] (Atr) | [AUTOMATIC RESTART] (Atr-) | 645
TAR | Max. restart time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] (5) | - | [Max. restart time] (tAr) | [AUTOMATIC RESTART] (Atr-) | 646
FLR | Catch on the fly | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Catch on the fly] (FLr) | [CATCH ON THE FLY] (FLr-) | 647
THT | Motor protect. type | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Self cooled] (ACL) | - | [Motor protect. type] (tHt) | [MOTOR THERMAL PROT.] (tHt-) | 648
TTD | Motor therm. level | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor therm. level] (ttd) | [MOTOR THERMAL PROT.] (tHt-) [THERMAL ALARM STOP] (SAt-) [SETTINGS] (SEt-) | 649
TTD2 | Motor2 therm. level | 16#2AFE = 11006 | 16#2050/7 | 16#98/01/07 = 152/01/07 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor2 therm. level] (ttd2) | [MOTOR THERMAL PROT.] (tHt-) [THERMAL ALARM STOP] (SAt-) | 650
TTD3 | Motor3 therm. level | 16#2AFF = 11007 | 16#2050/8 | 16#98/01/08 = 152/01/08 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor3 therm. level] (ttd3) | [MOTOR THERMAL PROT.] (tHt-) [THERMAL ALARM STOP] (SAt-) | 651
OLL | Overload fault mgt | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Overload fault mgt] (OLL) | [MOTOR THERMAL PROT.] (tHt-) | 652
OPL | Output Phase Loss | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Output Phase Loss] (OPL) | [OUTPUT PHASE LOSS] (OPL-) | 653
ODT | OutPh time detect | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPh time detect] (Odt) | [OUTPUT PHASE LOSS] (OPL-) | 654
IPL | Input phase loss | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Input phase loss] (IPL) | [INPUT PHASE LOSS] (IPL-) | 655
OHL | Overtemp fault mgt | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Overtemp fault mgt] (OHL) | [DRIVE OVERHEAT] (OHL-) | 656
THA | Drv therm. state al | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Drv therm. state al] (tHA) | [DRIVE OVERHEAT] (OHL-) [THERMAL ALARM STOP] (SAt-) | 657
SAT | Thermal alarm stop | 16#2B0D = 11021 | 16#2050/16 | 16#98/01/16 = 152/01/22 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Thermal alarm stop] (SAt) | [THERMAL ALARM STOP] (SAt-) | 658
ETF | External fault ass. | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [External fault ass.] (EtF) | [EXTERNAL FAULT] (EtF-) | 659
LET | External fault config | 16#1BB2 = 7090 | 16#2028/5B | 16#84/01/5B = 132/01/91 | L_H | Configuration and settings | R/WS | WORD (Enumeration) | - | [Active high] (HIG) | - | [External fault config] (LEt) | [EXTERNAL FAULT] (EtF-) | 660
EPL | External fault mgt | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [External fault mgt] (EPL) | [EXTERNAL FAULT] (EtF-) | 661
USB | UnderV. fault mgt | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Std fault] (0) | - | [UnderV. fault mgt] (USb) | [UNDERVOLTAGE MGT] (USb-) | 662
URES | Rated mains voltage | 16#35E9 = 13801 | 16#206C/2 | 16#A6/01/02 = 166/01/02 | URES | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Mains voltage] (UrES) | [UNDERVOLTAGE MGT] (USb-) | 663
USL | Undervoltage level | 16#35EA = 13802 | 16#206C/3 | 16#A6/01/03 = 166/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | (call USL_Max []) | 100 V ... 304 V | [Undervoltage level] (USL) | [UNDERVOLTAGE MGT] (USb-) | 664
UST | Undervolt. time out | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [Undervolt. time out] (USt) | [UNDERVOLTAGE MGT] (USb-) | 665
STP | UnderV. prevention | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [UnderV. prevention] (StP) | [UNDERVOLTAGE MGT] (USb-) | 666
TSM | UnderV. restart tm | 16#35F5 = 13813 | 16#206C/E | 16#A6/01/0E = 166/01/14 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 999.9 s | [UnderV. restart tm] (tSM) | [UNDERVOLTAGE MGT] (USb-) | 667
UPL | Prevention level | 16#35F3 = 13811 | 16#206C/C | 16#A6/01/0C = 166/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | (call USH_Max []) | 141 V ... 368 V | [Prevention level] (UPL) | [UNDERVOLTAGE MGT] (USb-) | 668
SDD | Anti veering configuration | 16#1B5D = 7005 | 16#2028/6 | 16#84/01/06 = 132/01/06 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Load slip detection] (Sdd) | [ENCODER FAULT] (Sdd-) | 669
STM | Max stop time | 16#35F6 = 13814 | 16#206C/F | 16#A6/01/0F = 166/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.01 s ... 60.00 s | [Max stop time] (StM) | [UNDERVOLTAGE MGT] (USb-) | 670
TBS | DC bus maintain tm | 16#35F4 = 13812 | 16#206C/D | 16#A6/01/0D = 166/01/13 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 9999 s | 1 s ... 9999 s | [DC bus maintain tm] (tbS) | [UNDERVOLTAGE MGT] (USb-) | 671
STRT | IGBT test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [IGBT test] (Strt) | [IGBT TESTS] (tIt-) | 672
LFL3 | AI3 4-20mA loss | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [AI3 4-20mA loss] (LFL3) | [4-20mA LOSS] (LFL-) | 673
INH | Fault inhibit assign. | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Fault inhibit assign.] (InH) | [FAULT INHIBITION] (InH-) | 674
CLL | Network fault mgt | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Network fault mgt] (CLL) | [COM. FAULT MANAGEMENT] (CLL-) | 675
COL | CANopen fault mgt | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [CANopen fault mgt] (COL) | [COM. FAULT MANAGEMENT] (CLL-) | 676
SLL | Modbus fault mgt | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Modbus fault mgt] (SLL) | [COM. FAULT MANAGEMENT] (CLL-) | 677
SSB | Trq/I limit. stop | 16#2418 = 9240 | 16#203E/29 | 16#8F/01/29 = 143/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] (nO) | - | [Trq/I limit. stop] (SSb) | [Torque OR I LIM. DETECT] (tId-) | 678
STO | Trq/I limit. time out | 16#2419 = 9241 | 16#203E/2A | 16#8F/01/2A = 143/01/42 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 1000 ms | 0 ms ... 9999 ms | [Trq/I limit. time out] (StO) | [Torque OR I LIM. DETECT] (tId-) | 679
TNL | Autotune fault mgt | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Autotune fault mgt] (tnL) | [AUTO TUNING FAULT] (tnF-) | 680
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 9999 | [Pairing password] (PPI) | [CARDS PAIRING] (PPI-) | 681
LFF | Fallback speed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Fallback speed] (LFF) | [FALLBACK SPEED] (LFF-) | 682
AIC2 | AI net. Channel | 16#14A4 = 5284 | 16#2016/55 | 16#7B/01/55 = 123/01/85 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [AI2 net. Channel] (AIC2) | [PID REGULATOR] (PId-) [VIRTUAL AI2] (AU2-) | 683
FQF | Frequency meter | 16#3909 = 14601 | 16#2074/2 | 16#AA/01/02 = 170/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Frequency meter] (FqF) | [FREQUENCY METER] (FqF-) | 684
FQC | Pulse scal. divisor | 16#390A = 14602 | 16#2074/3 | 16#AA/01/03 = 170/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 1.0 | 1.0 ... 100.0 | [Pulse scal. divisor] (FqC) | [FREQUENCY METER] (FqF-) | 685
FQA | Overspd. pulse thd. | 16#390C = 14604 | 16#2074/5 | 16#AA/01/05 = 170/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | [No] (nO) | [No] (nO) ... 20000 Hz | [Overspd. pulse thd.] (FqA) | [FREQUENCY METER] (FqF-) | 686
TDS | Pulse overspd delay | 16#390D = 14605 | 16#2074/6 | 16#AA/01/06 = 170/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse overspd delay] (tdS) | [FREQUENCY METER] (FqF-) | 687
FDT | Level fr. pulse ctrl | 16#390E = 14606 | 16#2074/7 | 16#AA/01/07 = 170/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | [No] (nO) | [No] (nO) ... 599.0 Hz | [Level fr. pulse ctrl] (Fdt) | [FREQUENCY METER] (FqF-) | 688
FQT | Pulse thd. wo Run | 16#390F = 14607 | 16#2074/8 | 16#AA/01/08 = 170/01/08 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | [No] (nO) | [No] (nO) ... 1000 Hz | [Pulse thd. wo Run] (Fqt) | [FREQUENCY METER] (FqF-) | 689
TQB | Pulse wo Run delay | 16#3910 = 14608 | 16#2074/9 | 16#AA/01/09 = 170/01/09 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse wo Run delay] (tqb) | [FREQUENCY METER] (FqF-) | 690
TLD | Dynamic load time | 16#3018 = 12312 | 16#205D/D | 16#9E/01/71 = 158/01/113 | - | Configuration and settings | R/WS | INT (Signed16) | 0.01 s | [No] (nO) | [No] (nO) ... 10.00 s | [Dynamic load time] (tLd) | [DYNAMIC LOAD DETECT.] (dLd-) | 691
DLD | Dyn. load threshold | 16#3017 = 12311 | 16#205D/C | 16#9E/01/70 = 158/01/112 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Dyn. load threshold] (dLd) | [DYNAMIC LOAD DETECT.] (dLd-) | 692
DLB | Dyn. load Mgt. | 16#3019 = 12313 | 16#205D/E | 16#9E/01/72 = 158/01/114 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Dyn. load Mgt.] (dLb) | [DYNAMIC LOAD DETECT.] (dLd-) | 693
NCA1 | Communication scanner, address of write word 1 | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 |  |  | 694
NCA2 | Communication scanner, address of write word 2 | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 |  |  | 695
NCA3 | Communication scanner, address of write word 3 | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 696
NCA4 | Communication scanner, address of write word 4 | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 697
NCA5 | Communication scanner, address of write word 5 | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 698
NCA6 | Communication scanner, address of write word 6 | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 699
NCA7 | Communication scanner, address of write word 7 | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 700
NCA8 | Communication scanner, address of write word 8 | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 701
NMA1 | Communication scanner, address of read word 1 | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 |  |  | 702
NMA2 | Communication scanner, address of read word 2 | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 |  |  | 703
NMA3 | Communication scanner, address of read word 3 | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 704
NMA4 | Communication scanner, address of read word 4 | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 705
NMA5 | Communication scanner, address of read word 5 | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 706
NMA6 | Communication scanner, address of read word 6 | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 707
NMA7 | Communication scanner, address of read word 7 | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 708
NMA8 | Communication scanner, address of read word 8 | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 709
OMA1 | Option scanner read adress parameter 1 | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 |  |  | 710
OMA2 | Option scanner read adress parameter 2 | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 |  |  | 711
OMA3 | Option scanner read adress parameter 3 | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 712
OMA4 | Option scanner read adress parameter 4 | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 713
OMA5 | Option scanner read adress parameter 5 | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 714
OMA6 | Option scanner read adress parameter 6 | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 715
OCA1 | Option scanner write adress parameter 1 | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 |  |  | 716
OCA2 | Option scanner write adress parameter 2 | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 |  |  | 717
OCA3 | Option scanner write adress parameter 3 | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 718
OCA4 | Option scanner write adress parameter 4 | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 719
OCA5 | Option scanner write adress parameter 5 | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 720
OCA6 | Option scanner write adress parameter 6 | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 721
ADD | Modbus Address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 247 | [Modbus Address] (Add) | [MODBUS NETWORK] (Md1-) | 722
AMOC | Modbus add Com.C. | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 247 | [Modbus add Com.C.] (AMOC) | [MODBUS NETWORK] (Md1-) | 723
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19.2 Kbps] (19 2) | - | [Modbus baud rate] (tbr) | [MODBUS NETWORK] (Md1-) | 724
TFO | Modbus format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8-E-1] (8E1) | - | [Modbus format] (tFO) | [MODBUS NETWORK] (Md1-) | 725
TTO | Modbus time out | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Modbus time out] (ttO) | [MODBUS NETWORK] (Md1-) | 726
ADCO | CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | [OFF] (OFF) | [OFF] (OFF) ... 127 | [CANopen address] (AdCO) | [CANopen] (CnO-) | 727
BDCO | CANopen bit rate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [250 kbps] (250 ) | - | [CANopen bit rate] (bdCO) | [CANopen] (CnO-) | 728
ERCO | Error code | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 | - | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [Error code] (ErCO) | [CANopen] (CnO-) [CANopen MAP] (CnM-) | 729
FLO | Forced local assign. | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Forced local assign.] (FLO) | [FORCED LOCAL] (LCF-) | 730
FLOC | Forced local Ref. | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Forced local Ref.] (FLOC) | [FORCED LOCAL] (LCF-) | 731
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOt) | [FORCED LOCAL] (LCF-) | 732
ADRC | Address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (AdrC) | [COMMUNICATION CARD] (Cbd-) | 733
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R | WORD (Enumeration) | - | Refer to programming manual | - | [PPO profile used] (PrFL) | [COMMUNICATION CARD] (Cbd-) | 734
DPMA | Active Master: 1 or 2 | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R | WORD (Enumeration) | - | [MCL1] (1) | - | [DP Master Active] (dPMA) | [COMMUNICATION CARD] (Cbd-) | 735
ECSA | EtherCAT second address | 16#1A23 = 6691 | 16#2024/5C | 16#82/01/5C = 130/01/92 | - | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat 2nd addr] (ECSA) | [COMMUNICATION CARD] (Cbd-) | 736
CIOA | Configured DeviceNet Assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] (21) | - | [Conf. Assembly] (CIOA) | [COMMUNICATION CARD] (Cbd-) | 737
CIO2 | Configured Ethenet/IP Assembly | 16#1A0C = 6668 | 16#2024/45 | 16#82/01/45 = 130/01/69 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] (21) | - | [Conf. Assembly] (CIO2) | [COMMUNICATION CARD] (Cbd-) | 738
BTUA | Bluetooth activation | 16#1A0E = 6670 | 16#2024/47 | 16#82/01/47 = 130/01/71 | ONOFF | Configuration and settings | R/WS | WORD (Enumeration) | - | [OFF] (OFF) | - | [Bluetooth Activation] (btUA) | [BLUETOOTH] (btH-) | 739
BTUC | Bluetooth Visibility Condition | 16#1A0F = 6671 | 16#2024/48 | 16#82/01/48 = 130/01/72 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Bluetooth Visibility] (btUC) | [BLUETOOTH] (btH-) | 740
BTPI | Bluetooth PIN code | 16#1A11 = 6673 | 16#2024/4A | 16#82/01/4A = 130/01/74 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [PIN code] (btPI) | [BLUETOOTH] (btH-) | 741
BDR | Bit rate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Bit rate] (bdr) | [COMMUNICATION CARD] (Cbd-) | 742
PRC | Peer Cop node | 16#19CE = 6606 | 16#2024/7 | 16#82/01/07 = 130/01/07 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - |  |  | 743
GLB | Global Tx | 16#19CF = 6607 | 16#2024/8 | 16#82/01/08 = 130/01/08 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 32 |  |  | 744
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R | WORD (Enumeration) | - | [Automatic] (AUtO) | - | [Data rate used] (bdrU) | [COMMUNICATION CARD] (Cbd-) | 745
IPM | IP mode | 16#FAFA = 64250 |  | = | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual | - |  |  | 746
ETHM | Communication option : Protocol used by the Ethernet card | 16#FAF1 = 64241 |  | = | ETHM | Configuration and settings | R/W | WORD (Enumeration) | - | [ModbusTCP] (MbtP) | - | [Ethernet protocol] (EtHM) | [COMMUNICATION CARD] (Cbd-) | 747
RDS | Rate setting | 16#FAFB = 64251 |  | = | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto] (AUtO) | - | [Rate setting] (rdS) | [COMMUNICATION CARD] (Cbd-) | 748
EWE | Services | 16#FB08 = 64264 |  | = | EWE | Configuration and settings | R/W | WORD (BitString16) | - | 0 | - |  |  | 749
ARD | Actual rate | 16#FB0A = 64266 |  | = | RDS | Configuration and settings | R | WORD (Enumeration) | - |  | - |  |  | 750
ICFG | Profinet : IPAR Local Config | 16#FB14 = 64276 |  | = | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [iPar Local Conf] (ICFG) | [COMMUNICATION CARD] (Cbd-) | 751
IPAD | Profinet : Last Error Code | 16#FB18 = 64280 |  | = | - | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Cod] (IPAd) | [COMMUNICATION CARD] (Cbd-) | 752
IPAE | Profinet : IPAR Service Status | 16#FB17 = 64279 |  | = | IPAE | Configuration and settings | R/W | WORD (Enumeration) | - | [Idle state] (IdLE) | - | [iPar State] (IPAE) | [COMMUNICATION CARD] (Cbd-) | 753
IPAF | Profinet : IPAR Error management | 16#FB15 = 64277 |  | = | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] (YES) | - | [iPar Error Mgt] (IPAF) | [COMMUNICATION CARD] (Cbd-) | 754
IPAS | Profinet : IPAR Autosave Enable | 16#FB13 = 64275 |  | = | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [iPar Autosave] (IPAS) | [COMMUNICATION CARD] (Cbd-) | 755
IPAT | Profinet : IPAR Config Autosave timer | 16#FB16 = 64278 |  | = | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 9999 | [iPar timer] (IPAt) | [COMMUNICATION CARD] (Cbd-) | 756
IPAV | Profinet : IPAR Validation | 16#FB12 = 64274 |  | = | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] (nO) | - | [iPar Validation] (IPAU) | [COMMUNICATION CARD] (Cbd-) | 757
L1D | LI1 On Delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI1 On Delay] (L1d) | [LI1 CONFIGURATION] (L1-) | 758
R1 | R1 Assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [No drive flt] (FLt) | - | [R1 Assignment] (r1) | [R1 CONFIGURATION] (r1-) | 759
R2 | R2 Assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [R2 Assignment] (r2) | [R2 CONFIGURATION] (r2-) | 760
L2D | LI2 On Delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI2 On Delay] (L2d) | [LI2 CONFIGURATION] (L2-) | 761
R1D | R1 Delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (r1d) | [R1 CONFIGURATION] (r1-) | 762
R2D | R2 Delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (r2d) | [R2 CONFIGURATION] (r2-) | 763
L3D | LI3 On Delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI3 On Delay] (L3d) | [LI3 CONFIGURATION] (L3-) | 764
R1S | R1 Active at | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R1 Active at] (r1S) | [R1 CONFIGURATION] (r1-) | 765
R2S | R2 Active at | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] (POS) | - | [R2 Active at] (r2S) | [R2 CONFIGURATION] (r2-) | 766
L4D | LI4 On Delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI4 On Delay] (L4d) | [LI4 CONFIGURATION] (L4-) | 767
R1H | R1 Holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R1 Holding time] (r1H) | [R1 CONFIGURATION] (r1-) | 768
R2H | R2 Holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R2 Holding time] (r2H) | [R2 CONFIGURATION] (r2-) | 769
L5D | LI5 On Delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI5 On Delay] (L5d) | [LI5 CONFIGURATION] (L5-) | 770
L6D | LI6 On Delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LI6 On Delay] (L6d) | [LI6 CONFIGURATION] (L6-) | 771
LA1D | AI1 as LI delay | 16#0FB5 = 4021 | 16#200A/16 | 16#75/01/16 = 117/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LA1 On Delay] (LA1d) | [LA1 CONFIGURATION] (LA1-) | 772
LA2D | AI2 as LI delay | 16#0FB6 = 4022 | 16#200A/17 | 16#75/01/17 = 117/01/23 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 200 ms | [LA2 On Delay] (LA2d) | [LA2 CONFIGURATION] (LA2-) | 773
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 | - | Configuration and settings | R | INT (Signed16) | 1 |  | - |  |  | 774
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 | - | Configuration and settings | R | UINT (Unsigned16) | 0.1 A |  | 0.0 A ... 6553.5 A |  |  | 775
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 | - | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz |  |  | 776
MMF | Measured motor frequency (signed value) | 16#0C93 = 3219 | 16#2002/14 | 16#71/01/14 = 113/01/20 | - | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Measured output fr.] (MMF) | [MONITORING] (MOn-) | 777
SOTR | OTR without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 | - | Configuration and settings | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % |  |  | 778
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 | - | Configuration and settings | R | UINT (Unsigned16) | 0.1 V |  | [No meas.] (----) ... 6553.5 V |  |  | 779
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 | - | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % |  |  | 780
STFR | Estimated stator frequency (signed value) | 16#0CD1 = 3281 | 16#2002/52 | 16#71/01/52 = 113/01/82 | - | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Stator frequency] (StFr) | [MONITORING] (SUP-) [MONITORING] (MOn-) | 781
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 | - | Configuration and settings | R | INT (Signed16) | 0.001 V |  | - |  |  | 782
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 | - | Configuration and settings | R | INT (Signed16) | 0.001 V |  | - |  |  | 783
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 | - | Configuration and settings | R | INT (Signed16) | 0.001 mA |  | - |  |  | 784
SAO1 | AO1 physical image without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 | - | Configuration and settings | R | INT (Signed16) | Refer to programming manual |  | - |  |  | 785
EBHT | Encoder Board Hardware Type | 16#0DE9 = 3561 | 16#2005/3E | 16#72/01/A2 = 114/01/162 | EBHT | Configuration and settings | R | WORD (Enumeration) | - | [No] (nO) | - |  |  | 786
PGI | Encoder pulse number | 16#15E4 = 5604 | 16#201A/5 | 16#7D/01/05 = 125/01/05 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1024 | 100 ... 3600 | [Number of pulses] (PGI) | [ENCODER CONFIGURATION] (IEn-) | 787
ENS | Encoder signals | 16#15E8 = 5608 | 16#201A/9 | 16#7D/01/09 = 125/01/09 | ENS | Configuration and settings | R/WS | WORD (Enumeration) | - | [AABB] (AAbb) | - | [Encoder type] (EnS) | [ENCODER CONFIGURATION] (IEn-) | 788
ENU | Encoder use | 16#15E6 = 5606 | 16#201A/7 | 16#7D/01/07 = 125/01/07 | ENU | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Encoder usage] (EnU) | [ENCODER CONFIGURATION] (IEn-) | 789
DANF | Select delta speed for encoder | 16#160B = 5643 | 16#201A/2C | 16#7D/01/2C = 125/01/44 | DANF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Over] (OUEr) | - | [ANF Direction check] (dAnF) | [ENCODER FAULT] (Sdd-) [ENCODER CONFIGURATION] (IEn-) | 790
FANF | Follow detectionANF fault | 16#160A = 5642 | 16#201A/2B | 16#7D/01/2B = 125/01/43 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 5.0 Hz | 0.1 Hz ... 50.0 Hz | [ANF Frequency Thd.] (FAnF) | [ENCODER FAULT] (Sdd-) [ENCODER CONFIGURATION] (IEn-) | 791
LANF | Level detection ANF fault | 16#1608 = 5640 | 16#201A/29 | 16#7D/01/29 = 125/01/41 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 10.0 Hz | [ANF Detection level] (LAnF) | [ENCODER FAULT] (Sdd-) [ENCODER CONFIGURATION] (IEn-) | 792
TANF | Time detectionANF fault | 16#1609 = 5641 | 16#201A/2A | 16#7D/01/2A = 125/01/42 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 10.00 s | [ANF Time Thd.] (tAnF) | [ENCODER FAULT] (Sdd-) [ENCODER CONFIGURATION] (IEn-) | 793
ULT | Underload reaction time | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld T. Del. Detect] (ULt) | [PROCESS UNDERLOAD] (ULd-) | 794
SRB | Hysteresis for steady state | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 599.0 Hz | [Hysteresis Freq.Att.] (Srb) | [PROCESS UNDERLOAD] (ULd-) [PROCESS OVERLOAD] (OLd-) [SETTINGS] (SEt-) | 795
UDL | Underload behaviour | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Underload Mangmt.] (UdL) | [PROCESS UNDERLOAD] (ULd-) | 796
RMUD | Underload minimum speed detection | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 | - | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Unld. Freq.Thr. Det.] (rMUd) | [PROCESS UNDERLOAD] (ULd-) [SETTINGS] (SEt-) | 797
LUL | Underload level | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [PROCESS UNDERLOAD] (ULd-) [SETTINGS] (SEt-) | 798
LUN | Underload level at motor nominal speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 | - | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUn) | [PROCESS UNDERLOAD] (ULd-) [SETTINGS] (SEt-) | 799
TOL | Overload reaction time | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Time Detect.] (tOL) | [PROCESS OVERLOAD] (OLd-) | 800
ODL | Overload behaviour | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Ovld.Proces.Mngmt] (OdL) | [PROCESS OVERLOAD] (OLd-) | 801
SCL3 | SCF3 detection | 16#1B6A = 7018 | 16#2028/13 | 16#84/01/13 = 132/01/19 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | [Ground short circuit] (SCL3) | [DC Bus] (dCC-) | 802
DCCM | DC Bus chaining mode configuration | 16#361A = 13850 | 16#206C/33 | 16#A6/01/33 = 166/01/51 | DCCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [DC-Bus chaining] (dCCM) | [DC Bus] (dCC-) | 803
DCCC | DC Bus chaining compatibility | 16#361B = 13851 | 16#206C/34 | 16#A6/01/34 = 166/01/52 | DCCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Altivar] (AtU) | - | [DC-Bus compat.] (dCCC) | [DC Bus] (dCC-) | 804
I2TA | I²t model activation for current limitation | 16#259F = 9631 | 16#2042/20 | 16#91/01/20 = 145/01/32 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [I²t model activation] (I2tA) | [Dyn Current limit] (I2t-) | 805
I2TI | maximum current of I²t model | 16#25A0 = 9632 | 16#2042/21 | 16#91/01/21 = 145/01/33 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 A | ((INV * 3 / 2) + 1) | - | [max current of I²t] (I2tI) | [Dyn Current limit] (I2t-) | 806
I2TM | Monitoring of I²t overload level | 16#25A2 = 9634 | 16#2042/23 | 16#91/01/23 = 145/01/35 | - | Configuration and settings | R | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [I²t overload level] (I2tM) | [MONIT. MOTOR] (MMO-) | 807
I2TT | maximum time of I²t model | 16#25A1 = 9633 | 16#2042/22 | 16#91/01/22 = 145/01/34 | - | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | - | [max time of I²t] (I2tt) | [Dyn Current limit] (I2t-) | 808
MSTP | With or whithout memo stop switch | 16#30EB = 12523 | 16#205F/18 | 16#9F/01/7C = 159/01/124 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] (YES) | - | [Memo Stop] (MStP) | [POSITIONING BY SENSORS] (LPO-) | 809
PRST | Priority restart even if switch stop is activated | 16#30EC = 12524 | 16#205F/19 | 16#9F/01/7D = 159/01/125 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [Priority restart] (PrSt) | [POSITIONING BY SENSORS] (LPO-) | 810
FBST | FB : Status | 16#3A70 = 14960 | 16#2077/3D | 16#AB/01/A1 = 171/01/161 | FBST | Function blocks | R | WORD (Enumeration) | - |  | - | [FB status] (FbSt) | [MONIT. FUN. BLOCKS] (MFb-) | 811
FBFT | FB : Fault | 16#3A71 = 14961 | 16#2077/3E | 16#AB/01/A2 = 171/01/162 | FBFT | Function blocks | R | WORD (Enumeration) | - |  | - | [FB fault] (FbFt) | [MONIT. FUN. BLOCKS] (MFb-) | 812
FBCD | FB : Command | 16#3A72 = 14962 | 16#2077/3F | 16#AB/01/A3 = 171/01/163 | SPST | Function blocks | R/W | WORD (Enumeration) | - |  | - | [FB command] (FbCd) | [FUNCTION BLOCKS] (FbM-) | 813
FBRM | FB : Run Mode | 16#3A73 = 14963 | 16#2077/40 | 16#AB/01/A4 = 171/01/164 | PSLIN | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | [FB start mode] (FbrM) | [FUNCTION BLOCKS] (FbM-) | 814
FBSM | FB : Stop Mode | 16#3A74 = 14964 | 16#2077/41 | 16#AB/01/A5 = 171/01/165 | ECFG | Function blocks | R/WS | WORD (Enumeration) | - | [Freewheel] (YES) | - | [Stop FB stop motor] (FbSM) | [FUNCTION BLOCKS] (FbM-) | 815
FBDF | FB : behaviour on drive fault | 16#3A75 = 14965 | 16#2077/42 | 16#AB/01/A6 = 171/01/166 | SPIG | Function blocks | R/WS | WORD (Enumeration) | - | [Stop] (StOP) | - | [FB on drive fault] (FbdF) | [FUNCTION BLOCKS] (FbM-) | 816
IA01 | FB : Analog Input 01 assignement | 16#3A34 = 14900 | 16#2077/1 | 16#AB/01/65 = 171/01/101 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA01) | [INPUTS ASSIGNMENTS] (FbA-) | 817
IA02 | FB : Analog Input 02 assignement | 16#3A35 = 14901 | 16#2077/2 | 16#AB/01/66 = 171/01/102 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA02) | [INPUTS ASSIGNMENTS] (FbA-) | 818
IA03 | FB : Analog Input 03 assignement | 16#3A36 = 14902 | 16#2077/3 | 16#AB/01/67 = 171/01/103 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA03) | [INPUTS ASSIGNMENTS] (FbA-) | 819
IA04 | FB : Analog Input 04 assignement | 16#3A37 = 14903 | 16#2077/4 | 16#AB/01/68 = 171/01/104 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA04) | [INPUTS ASSIGNMENTS] (FbA-) | 820
IA05 | FB : Analog Input 05 assignement | 16#3A38 = 14904 | 16#2077/5 | 16#AB/01/69 = 171/01/105 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA05) | [INPUTS ASSIGNMENTS] (FbA-) | 821
IA06 | FB : Analog Input 06 assignement | 16#3A39 = 14905 | 16#2077/6 | 16#AB/01/6A = 171/01/106 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA06) | [INPUTS ASSIGNMENTS] (FbA-) | 822
IA07 | FB : Analog Input 07 assignement | 16#3A3A = 14906 | 16#2077/7 | 16#AB/01/6B = 171/01/107 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA07) | [INPUTS ASSIGNMENTS] (FbA-) | 823
IA08 | FB : Analog Input 08 assignement | 16#3A3B = 14907 | 16#2077/8 | 16#AB/01/6C = 171/01/108 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA08) | [INPUTS ASSIGNMENTS] (FbA-) | 824
IA09 | FB : Analog Input 09 assignement | 16#3A3C = 14908 | 16#2077/9 | 16#AB/01/6D = 171/01/109 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA09) | [INPUTS ASSIGNMENTS] (FbA-) | 825
IA10 | FB : Analog Input 10 assignement | 16#3A3D = 14909 | 16#2077/A | 16#AB/01/6E = 171/01/110 | PSA | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IA10) | [INPUTS ASSIGNMENTS] (FbA-) | 826
IL01 | FB : Logical Input 01 assignement | 16#3A48 = 14920 | 16#2077/15 | 16#AB/01/79 = 171/01/121 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL01) | [INPUTS ASSIGNMENTS] (FbA-) | 827
IL02 | FB : Logical Input 02 assignement | 16#3A49 = 14921 | 16#2077/16 | 16#AB/01/7A = 171/01/122 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL02) | [INPUTS ASSIGNMENTS] (FbA-) | 828
IL03 | FB : Logical Input 03 assignement | 16#3A4A = 14922 | 16#2077/17 | 16#AB/01/7B = 171/01/123 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL03) | [INPUTS ASSIGNMENTS] (FbA-) | 829
IL04 | FB : Logical Input 04 assignement | 16#3A4B = 14923 | 16#2077/18 | 16#AB/01/7C = 171/01/124 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL04) | [INPUTS ASSIGNMENTS] (FbA-) | 830
IL05 | FB : Logical Input 05 assignement | 16#3A4C = 14924 | 16#2077/19 | 16#AB/01/7D = 171/01/125 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL05) | [INPUTS ASSIGNMENTS] (FbA-) | 831
IL06 | FB : Logical Input 06 assignement | 16#3A4D = 14925 | 16#2077/1A | 16#AB/01/7E = 171/01/126 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL06) | [INPUTS ASSIGNMENTS] (FbA-) | 832
IL07 | FB : Logical Input 07 assignement | 16#3A4E = 14926 | 16#2077/1B | 16#AB/01/7F = 171/01/127 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL07) | [INPUTS ASSIGNMENTS] (FbA-) | 833
IL08 | FB : Logical Input 08 assignement | 16#3A4F = 14927 | 16#2077/1C | 16#AB/01/80 = 171/01/128 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL08) | [INPUTS ASSIGNMENTS] (FbA-) | 834
IL09 | FB : Logical Input 09 assignement | 16#3A50 = 14928 | 16#2077/1D | 16#AB/01/81 = 171/01/129 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL09) | [INPUTS ASSIGNMENTS] (FbA-) | 835
IL10 | FB : Logical Input 10 assignement | 16#3A51 = 14929 | 16#2077/1E | 16#AB/01/82 = 171/01/130 | PSL | Function blocks | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (IL10) | [INPUTS ASSIGNMENTS] (FbA-) | 836
LA01 | FB : ADL Container 01 | 16#3A5C = 14940 | 16#2077/29 | 16#AB/01/8D = 171/01/141 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 837
LA02 | FB : ADL Container 02 | 16#3A5D = 14941 | 16#2077/2A | 16#AB/01/8E = 171/01/142 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 838
LA03 | FB : ADL Container 03 | 16#3A5E = 14942 | 16#2077/2B | 16#AB/01/8F = 171/01/143 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 839
LA04 | FB : ADL Container 04 | 16#3A5F = 14943 | 16#2077/2C | 16#AB/01/90 = 171/01/144 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 840
LA05 | FB : ADL Container 05 | 16#3A60 = 14944 | 16#2077/2D | 16#AB/01/91 = 171/01/145 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 841
LA06 | FB : ADL Container 06 | 16#3A61 = 14945 | 16#2077/2E | 16#AB/01/92 = 171/01/146 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 842
LA07 | FB : ADL Container 07 | 16#3A62 = 14946 | 16#2077/2F | 16#AB/01/93 = 171/01/147 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 843
LA08 | FB : ADL Container 08 | 16#3A63 = 14947 | 16#2077/30 | 16#AB/01/94 = 171/01/148 | - | Function blocks | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 844
M001 | FB : M001 parameter | 16#3A7A = 14970 | 16#2077/47 | 16#AB/01/AB = 171/01/171 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M001) | [FB PARAMETERS] (FbP-) | 845
M002 | FB : M002 parameter | 16#3A7B = 14971 | 16#2077/48 | 16#AB/01/AC = 171/01/172 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M002) | [FB PARAMETERS] (FbP-) | 846
M003 | FB : M003 parameter | 16#3A7C = 14972 | 16#2077/49 | 16#AB/01/AD = 171/01/173 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M003) | [FB PARAMETERS] (FbP-) | 847
M004 | FB : M004 parameter | 16#3A7D = 14973 | 16#2077/4A | 16#AB/01/AE = 171/01/174 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M004) | [FB PARAMETERS] (FbP-) | 848
M005 | FB : M005 parameter | 16#3A7E = 14974 | 16#2077/4B | 16#AB/01/AF = 171/01/175 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M005) | [FB PARAMETERS] (FbP-) | 849
M006 | FB : M006 parameter | 16#3A7F = 14975 | 16#2077/4C | 16#AB/01/B0 = 171/01/176 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M006) | [FB PARAMETERS] (FbP-) | 850
M007 | FB : M007 parameter | 16#3A80 = 14976 | 16#2077/4D | 16#AB/01/B1 = 171/01/177 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M007) | [FB PARAMETERS] (FbP-) | 851
M008 | FB : M008 parameter | 16#3A81 = 14977 | 16#2077/4E | 16#AB/01/B2 = 171/01/178 | - | Function blocks | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (M008) | [FB PARAMETERS] (FbP-) | 852
S001 | FB : Status register 1 | 16#3A84 = 14980 | 16#2077/51 | 16#AB/01/B5 = 171/01/181 | S001 | Function blocks | R | WORD (BitString16) | - |  | - |  |  | 853
S002 | FB : Status register 2 | 16#3A85 = 14981 | 16#2077/52 | 16#AB/01/B6 = 171/01/182 | S002 | Function blocks | R | WORD (BitString16) | - |  | - |  |  | 854
S006 | FB : Status register 6 | 16#3A89 = 14985 | 16#2077/56 | 16#AB/01/BA = 171/01/186 | S006 | Function blocks | R | WORD (BitString16) | - |  | - |  |  | 855
BNV | FB : Binary format version of the drive | 16#3A8E = 14990 | 16#2077/5B | 16#AB/01/BF = 171/01/191 | - | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Prg. format version] (bnU) | [FB IDENTIFICATION] (FbI-) | 856
CTV | FB : Catalog version of the drive | 16#3A8F = 14991 | 16#2077/5C | 16#AB/01/C0 = 171/01/192 | - | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Catalogue version] (CtU) | [FB IDENTIFICATION] (FbI-) | 857
BNS | FB : program file size | 16#3A90 = 14992 | 16#2077/5D | 16#AB/01/C1 = 171/01/193 | - | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Program size] (bnS) | [FB IDENTIFICATION] (FbI-) | 858
BVER | FB : program user version | 16#3A91 = 14993 | 16#2077/5E | 16#AB/01/C2 = 171/01/194 | - | Function blocks | R | UINT (Unsigned16) | 1 |  | 0 ... 255 | [Program version] (bUEr) | [FB IDENTIFICATION] (FbI-) | 859
SLSA | Safely Limited Speed assignment | 16#3BC4 = 15300 | 16#207B/1 | 16#AD/01/65 = 173/01/101 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | (nO) | - |  |  | 860
SLT | Safely Limited Speed type | 16#3BC5 = 15301 | 16#207B/2 | 16#AD/01/66 = 173/01/102 | SLT | Safety function | R/WS | WORD (Enumeration) | - | (tYP1) | - |  |  | 861
SLSP | SLS set point | 16#3BC6 = 15302 | 16#207B/3 | 16#AD/01/67 = 173/01/103 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz |  |  | 862
SLTT | SLS tolerance threshold | 16#3BC7 = 15303 | 16#207B/4 | 16#AD/01/68 = 173/01/104 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz |  |  | 863
SLWT | SLS Wait Time | 16#3BC9 = 15305 | 16#207B/6 | 16#AD/01/6A = 173/01/106 | - | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 5000 ms |  |  | 864
SLSS | SLS Status | 16#3BC8 = 15304 | 16#207B/5 | 16#AD/01/69 = 173/01/105 | SLSS | Safety function | R | WORD (Enumeration) | - |  | - | [SLS status] (SLSS) | [MONIT. SAFETY] (SAF-) | 865
SS1A | Safe Speed 1 assignment | 16#3BCE = 15310 | 16#207B/B | 16#AD/01/6F = 173/01/111 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | (nO) | - |  |  | 866
SSRT | SS1 ramp value | 16#3BCF = 15311 | 16#207B/C | 16#AD/01/70 = 173/01/112 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 | 0.1 | 0.1 ... 599.0 |  |  | 867
SSRU | SS1 ramp uni | 16#3BD0 = 15312 | 16#207B/D | 16#AD/01/71 = 173/01/113 | SSRU | Safety function | R/WS | WORD (Enumeration) | - | (1H) | - |  |  | 868
SSSL | SLS/SS1 standstill level | 16#3BD1 = 15313 | 16#207B/E | 16#AD/01/72 = 173/01/114 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz |  |  | 869
SSTT | SS1 trip threshold | 16#3BD2 = 15314 | 16#207B/F | 16#AD/01/73 = 173/01/115 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz |  |  | 870
SS1S | SS1 Status | 16#3BD3 = 15315 | 16#207B/10 | 16#AD/01/74 = 173/01/116 | SS1S | Safety function | R | WORD (Enumeration) | - |  | - | [SS1 status] (SS1S) | [MONIT. SAFETY] (SAF-) | 871
STOA | Safely Torque Off assignment | 16#3BD8 = 15320 | 16#207B/15 | 16#AD/01/79 = 173/01/121 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | (nO) | - |  |  | 872
PWRM | Safely Torque Off assignment | 16#3BD9 = 15321 | 16#207B/16 | 16#AD/01/7A = 173/01/122 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | (PWrM) | - |  |  | 873
STOS | Safe Torque Off Status | 16#3BDA = 15322 | 16#207B/17 | 16#AD/01/7B = 173/01/123 | STOS | Safety function | R | WORD (Enumeration) | - |  | - | [STO status] (StOS) | [MONIT. SAFETY] (SAF-) | 874
LIDT | Debounce Time | 16#3BE2 = 15330 | 16#207B/1F | 16#AD/01/83 = 173/01/131 | - | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 50 ms | 0 ms ... 2000 ms |  |  | 875
LIRT | Response Time | 16#3BE3 = 15331 | 16#207B/20 | 16#AD/01/84 = 173/01/132 | - | Safety function | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 50 ms |  |  | 876
SFTY | Safe Drive Status | 16#3BF0 = 15344 | 16#207B/2D | 16#AD/01/91 = 173/01/145 | SFTY | Safety function | R | WORD (Enumeration) | - |  | - |  |  | 877
SAF1 | Safety fault register 1 | 16#3BF6 = 15350 | 16#207B/33 | 16#AD/01/97 = 173/01/151 | - | Safety function | R | WORD (BitString16) | - |  | - | [Safety fault Reg1] (SAF1) | [MORE FAULT INFO] (AFI-) | 878
SAF2 | Safety fault register 2 | 16#3BFF = 15359 | 16#207B/3C | 16#AD/01/A0 = 173/01/160 | - | Safety function | R | WORD (BitString16) | - |  | - | [Safety fault Reg2] (SAF2) | [MORE FAULT INFO] (AFI-) | 879
SF00 | Safety fault subregister 0 | 16#3BF7 = 15351 | 16#207B/34 | 16#AD/01/98 = 173/01/152 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 0] (SF00) | [MORE FAULT INFO] (AFI-) | 880
SF01 | Safety fault subregister 1 | 16#3BF8 = 15352 | 16#207B/35 | 16#AD/01/99 = 173/01/153 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 1] (SF01) | [MORE FAULT INFO] (AFI-) | 881
SF02 | Safety fault subregister 2 | 16#3BF9 = 15353 | 16#207B/36 | 16#AD/01/9A = 173/01/154 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 2] (SF02) | [MORE FAULT INFO] (AFI-) | 882
SF03 | Safety fault subregister 3 | 16#3BFA = 15354 | 16#207B/37 | 16#AD/01/9B = 173/01/155 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 3] (SF03) | [MORE FAULT INFO] (AFI-) | 883
SF04 | Safety fault subregister 4 | 16#3BFB = 15355 | 16#207B/38 | 16#AD/01/9C = 173/01/156 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 4] (SF04) | [MORE FAULT INFO] (AFI-) | 884
SF05 | Safety fault subregister 5 | 16#3BFC = 15356 | 16#207B/39 | 16#AD/01/9D = 173/01/157 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 5] (SF05) | [MORE FAULT INFO] (AFI-) | 885
SF06 | Safety fault subregister 6 | 16#3BFD = 15357 | 16#207B/3A | 16#AD/01/9E = 173/01/158 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 6] (SF06) | [MORE FAULT INFO] (AFI-) | 886
SF07 | Safety fault subregister 7 | 16#3BFE = 15358 | 16#207B/3B | 16#AD/01/9F = 173/01/159 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 7] (SF07) | [MORE FAULT INFO] (AFI-) | 887
SF08 | Safety fault subregister 8 | 16#3C00 = 15360 | 16#207B/3D | 16#AD/01/A1 = 173/01/161 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 8] (SF08) | [MORE FAULT INFO] (AFI-) | 888
SF09 | Safety fault subregister 9 | 16#3C01 = 15361 | 16#207B/3E | 16#AD/01/A2 = 173/01/162 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 9] (SF09) | [MORE FAULT INFO] (AFI-) | 889
SF10 | Safety fault subregister 10 | 16#3C02 = 15362 | 16#207B/3F | 16#AD/01/A3 = 173/01/163 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 10] (SF10) | [MORE FAULT INFO] (AFI-) | 890
SF11 | Safety fault subregister 11 | 16#3C03 = 15363 | 16#207B/40 | 16#AD/01/A4 = 173/01/164 | - | Safety function | R | WORD (BitString16) | - |  | - | [SAFF Subcode 11] (SF11) | [MORE FAULT INFO] (AFI-) | 891
SR11 | SAF1 REGISTER x (1 is last) | 16#1CE9 = 7401 | 16#202C/2 | 16#86/01/02 = 134/01/02 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 892
SR12 | SAF1 REGISTER x (1 is last) | 16#1CEA = 7402 | 16#202C/3 | 16#86/01/03 = 134/01/03 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 893
SR13 | SAF1 REGISTER x (1 is last) | 16#1CEB = 7403 | 16#202C/4 | 16#86/01/04 = 134/01/04 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 894
SR14 | SAF1 REGISTER x (1 is last) | 16#1CEC = 7404 | 16#202C/5 | 16#86/01/05 = 134/01/05 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 895
SR15 | SAF1 REGISTER x (1 is last) | 16#1CED = 7405 | 16#202C/6 | 16#86/01/06 = 134/01/06 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 896
SR16 | SAF1 REGISTER x (1 is last) | 16#1CEE = 7406 | 16#202C/7 | 16#86/01/07 = 134/01/07 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 897
SR17 | SAF1 REGISTER x (1 is last) | 16#1CEF = 7407 | 16#202C/8 | 16#86/01/08 = 134/01/08 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 898
SR18 | SAF1 REGISTER x (1 is last) | 16#1CF0 = 7408 | 16#202C/9 | 16#86/01/09 = 134/01/09 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 899
SR21 | SAF2 REGISTER x (1 is last) | 16#1CF3 = 7411 | 16#202C/C | 16#86/01/0C = 134/01/12 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 900
SR22 | SAF2 REGISTER x (1 is last) | 16#1CF4 = 7412 | 16#202C/D | 16#86/01/0D = 134/01/13 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 901
SR23 | SAF2 REGISTER x (1 is last) | 16#1CF5 = 7413 | 16#202C/E | 16#86/01/0E = 134/01/14 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 902
SR24 | SAF2 REGISTER x (1 is last) | 16#1CF6 = 7414 | 16#202C/F | 16#86/01/0F = 134/01/15 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 903
SR25 | SAF2 REGISTER x (1 is last) | 16#1CF7 = 7415 | 16#202C/10 | 16#86/01/10 = 134/01/16 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 904
SR26 | SAF2 REGISTER x (1 is last) | 16#1CF8 = 7416 | 16#202C/11 | 16#86/01/11 = 134/01/17 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 905
SR27 | SAF2 REGISTER x (1 is last) | 16#1CF9 = 7417 | 16#202C/12 | 16#86/01/12 = 134/01/18 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 906
SR28 | SAF2 REGISTER x (1 is last) | 16#1CFA = 7418 | 16#202C/13 | 16#86/01/13 = 134/01/19 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 907
SRA1 | SF00 REGISTER x (1 is last) | 16#1CFD = 7421 | 16#202C/16 | 16#86/01/16 = 134/01/22 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 908
SRA2 | SF00 REGISTER x (1 is last) | 16#1CFE = 7422 | 16#202C/17 | 16#86/01/17 = 134/01/23 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 909
SRA3 | SF00 REGISTER x (1 is last) | 16#1CFF = 7423 | 16#202C/18 | 16#86/01/18 = 134/01/24 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 910
SRA4 | SF00 REGISTER x (1 is last) | 16#1D00 = 7424 | 16#202C/19 | 16#86/01/19 = 134/01/25 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 911
SRA5 | SF00 REGISTER x (1 is last) | 16#1D01 = 7425 | 16#202C/1A | 16#86/01/1A = 134/01/26 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 912
SRA6 | SF00 REGISTER x (1 is last) | 16#1D02 = 7426 | 16#202C/1B | 16#86/01/1B = 134/01/27 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 913
SRA7 | SF00 REGISTER x (1 is last) | 16#1D03 = 7427 | 16#202C/1C | 16#86/01/1C = 134/01/28 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 914
SRA8 | SF00 REGISTER x (1 is last) | 16#1D04 = 7428 | 16#202C/1D | 16#86/01/1D = 134/01/29 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 915
SRB1 | SF01 REGISTER x (1 is last) | 16#1D07 = 7431 | 16#202C/20 | 16#86/01/20 = 134/01/32 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 916
SRB2 | SF01 REGISTER x (1 is last) | 16#1D08 = 7432 | 16#202C/21 | 16#86/01/21 = 134/01/33 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 917
SRB3 | SF01 REGISTER x (1 is last) | 16#1D09 = 7433 | 16#202C/22 | 16#86/01/22 = 134/01/34 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 918
SRB4 | SF01 REGISTER x (1 is last) | 16#1D0A = 7434 | 16#202C/23 | 16#86/01/23 = 134/01/35 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 919
SRB5 | SF01 REGISTER x (1 is last) | 16#1D0B = 7435 | 16#202C/24 | 16#86/01/24 = 134/01/36 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 920
SRB6 | SF01 REGISTER x (1 is last) | 16#1D0C = 7436 | 16#202C/25 | 16#86/01/25 = 134/01/37 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 921
SRB7 | SF01 REGISTER x (1 is last) | 16#1D0D = 7437 | 16#202C/26 | 16#86/01/26 = 134/01/38 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 922
SRB8 | SF01 REGISTER x (1 is last) | 16#1D0E = 7438 | 16#202C/27 | 16#86/01/27 = 134/01/39 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 923
SRC1 | SF02 REGISTER x (1 is last) | 16#1D11 = 7441 | 16#202C/2A | 16#86/01/2A = 134/01/42 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 924
SRC2 | SF02 REGISTER x (1 is last) | 16#1D12 = 7442 | 16#202C/2B | 16#86/01/2B = 134/01/43 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 925
SRC3 | SF02 REGISTER x (1 is last) | 16#1D13 = 7443 | 16#202C/2C | 16#86/01/2C = 134/01/44 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 926
SRC4 | SF02 REGISTER x (1 is last) | 16#1D14 = 7444 | 16#202C/2D | 16#86/01/2D = 134/01/45 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 927
SRC5 | SF02 REGISTER x (1 is last) | 16#1D15 = 7445 | 16#202C/2E | 16#86/01/2E = 134/01/46 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 928
SRC6 | SF02 REGISTER x (1 is last) | 16#1D16 = 7446 | 16#202C/2F | 16#86/01/2F = 134/01/47 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 929
SRC7 | SF02 REGISTER x (1 is last) | 16#1D17 = 7447 | 16#202C/30 | 16#86/01/30 = 134/01/48 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 930
SRC8 | SF02 REGISTER x (1 is last) | 16#1D18 = 7448 | 16#202C/31 | 16#86/01/31 = 134/01/49 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 931
SRD1 | SF03 REGISTER x (1 is last) | 16#1D1B = 7451 | 16#202C/34 | 16#86/01/34 = 134/01/52 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 932
SRD2 | SF03 REGISTER x (1 is last) | 16#1D1C = 7452 | 16#202C/35 | 16#86/01/35 = 134/01/53 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 933
SRD3 | SF03 REGISTER x (1 is last) | 16#1D1D = 7453 | 16#202C/36 | 16#86/01/36 = 134/01/54 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 934
SRD4 | SF03 REGISTER x (1 is last) | 16#1D1E = 7454 | 16#202C/37 | 16#86/01/37 = 134/01/55 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 935
SRD5 | SF03 REGISTER x (1 is last) | 16#1D1F = 7455 | 16#202C/38 | 16#86/01/38 = 134/01/56 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 936
SRD6 | SF03 REGISTER x (1 is last) | 16#1D20 = 7456 | 16#202C/39 | 16#86/01/39 = 134/01/57 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 937
SRD7 | SF03 REGISTER x (1 is last) | 16#1D21 = 7457 | 16#202C/3A | 16#86/01/3A = 134/01/58 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 938
SRD8 | SF03 REGISTER x (1 is last) | 16#1D22 = 7458 | 16#202C/3B | 16#86/01/3B = 134/01/59 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 939
SRE1 | SF04 REGISTER x (1 is last) | 16#1D25 = 7461 | 16#202C/3E | 16#86/01/3E = 134/01/62 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 940
SRE2 | SF04 REGISTER x (1 is last) | 16#1D26 = 7462 | 16#202C/3F | 16#86/01/3F = 134/01/63 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 941
SRE3 | SF04 REGISTER x (1 is last) | 16#1D27 = 7463 | 16#202C/40 | 16#86/01/40 = 134/01/64 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 942
SRE4 | SF04 REGISTER x (1 is last) | 16#1D28 = 7464 | 16#202C/41 | 16#86/01/41 = 134/01/65 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 943
SRE5 | SF04 REGISTER x (1 is last) | 16#1D29 = 7465 | 16#202C/42 | 16#86/01/42 = 134/01/66 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 944
SRE6 | SF04 REGISTER x (1 is last) | 16#1D2A = 7466 | 16#202C/43 | 16#86/01/43 = 134/01/67 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 945
SRE7 | SF04 REGISTER x (1 is last) | 16#1D2B = 7467 | 16#202C/44 | 16#86/01/44 = 134/01/68 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 946
SRE8 | SF04 REGISTER x (1 is last) | 16#1D2C = 7468 | 16#202C/45 | 16#86/01/45 = 134/01/69 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 947
SRF1 | SF05 REGISTER x (1 is last) | 16#1D2F = 7471 | 16#202C/48 | 16#86/01/48 = 134/01/72 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 948
SRF2 | SF05 REGISTER x (1 is last) | 16#1D30 = 7472 | 16#202C/49 | 16#86/01/49 = 134/01/73 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 949
SRF3 | SF05 REGISTER x (1 is last) | 16#1D31 = 7473 | 16#202C/4A | 16#86/01/4A = 134/01/74 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 950
SRF4 | SF05 REGISTER x (1 is last) | 16#1D32 = 7474 | 16#202C/4B | 16#86/01/4B = 134/01/75 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 951
SRF5 | SF05 REGISTER x (1 is last) | 16#1D33 = 7475 | 16#202C/4C | 16#86/01/4C = 134/01/76 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 952
SRF6 | SF05 REGISTER x (1 is last) | 16#1D34 = 7476 | 16#202C/4D | 16#86/01/4D = 134/01/77 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 953
SRF7 | SF05 REGISTER x (1 is last) | 16#1D35 = 7477 | 16#202C/4E | 16#86/01/4E = 134/01/78 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 954
SRF8 | SF05 REGISTER x (1 is last) | 16#1D36 = 7478 | 16#202C/4F | 16#86/01/4F = 134/01/79 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 955
SRG1 | SF06 REGISTER x (1 is last) | 16#1D39 = 7481 | 16#202C/52 | 16#86/01/52 = 134/01/82 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 956
SRG2 | SF06 REGISTER x (1 is last) | 16#1D3A = 7482 | 16#202C/53 | 16#86/01/53 = 134/01/83 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 957
SRG3 | SF06 REGISTER x (1 is last) | 16#1D3B = 7483 | 16#202C/54 | 16#86/01/54 = 134/01/84 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 958
SRG4 | SF06 REGISTER x (1 is last) | 16#1D3C = 7484 | 16#202C/55 | 16#86/01/55 = 134/01/85 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 959
SRG5 | SF06 REGISTER x (1 is last) | 16#1D3D = 7485 | 16#202C/56 | 16#86/01/56 = 134/01/86 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 960
SRG6 | SF06 REGISTER x (1 is last) | 16#1D3E = 7486 | 16#202C/57 | 16#86/01/57 = 134/01/87 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 961
SRG7 | SF06 REGISTER x (1 is last) | 16#1D3F = 7487 | 16#202C/58 | 16#86/01/58 = 134/01/88 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 962
SRG8 | SF06 REGISTER x (1 is last) | 16#1D40 = 7488 | 16#202C/59 | 16#86/01/59 = 134/01/89 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 963
SRH1 | SF07 REGISTER x (1 is last) | 16#1D43 = 7491 | 16#202C/5C | 16#86/01/5C = 134/01/92 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 964
SRH2 | SF07 REGISTER x (1 is last) | 16#1D44 = 7492 | 16#202C/5D | 16#86/01/5D = 134/01/93 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 965
SRH3 | SF07 REGISTER x (1 is last) | 16#1D45 = 7493 | 16#202C/5E | 16#86/01/5E = 134/01/94 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 966
SRH4 | SF07 REGISTER x (1 is last) | 16#1D46 = 7494 | 16#202C/5F | 16#86/01/5F = 134/01/95 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 967
SRH5 | SF07 REGISTER x (1 is last) | 16#1D47 = 7495 | 16#202C/60 | 16#86/01/60 = 134/01/96 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 968
SRH6 | SF07 REGISTER x (1 is last) | 16#1D48 = 7496 | 16#202C/61 | 16#86/01/61 = 134/01/97 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 969
SRH7 | SF07 REGISTER x (1 is last) | 16#1D49 = 7497 | 16#202C/62 | 16#86/01/62 = 134/01/98 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 970
SRH8 | SF07 REGISTER x (1 is last) | 16#1D4A = 7498 | 16#202C/63 | 16#86/01/63 = 134/01/99 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 971
SRI1 | SF08 REGISTER x (1 is last) | 16#1D4D = 7501 | 16#202D/2 | 16#86/01/66 = 134/01/102 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 972
SRI2 | SF08 REGISTER x (1 is last) | 16#1D4E = 7502 | 16#202D/3 | 16#86/01/67 = 134/01/103 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 973
SRI3 | SF08 REGISTER x (1 is last) | 16#1D4F = 7503 | 16#202D/4 | 16#86/01/68 = 134/01/104 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 974
SRI4 | SF08 REGISTER x (1 is last) | 16#1D50 = 7504 | 16#202D/5 | 16#86/01/69 = 134/01/105 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 975
SRI5 | SF08 REGISTER x (1 is last) | 16#1D51 = 7505 | 16#202D/6 | 16#86/01/6A = 134/01/106 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 976
SRI6 | SF08 REGISTER x (1 is last) | 16#1D52 = 7506 | 16#202D/7 | 16#86/01/6B = 134/01/107 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 977
SRI7 | SF08 REGISTER x (1 is last) | 16#1D53 = 7507 | 16#202D/8 | 16#86/01/6C = 134/01/108 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 978
SRI8 | SF08 REGISTER x (1 is last) | 16#1D54 = 7508 | 16#202D/9 | 16#86/01/6D = 134/01/109 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 979
SRJ1 | SF09 REGISTER x (1 is last) | 16#1D57 = 7511 | 16#202D/C | 16#86/01/70 = 134/01/112 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 980
SRJ2 | SF09 REGISTER x (1 is last) | 16#1D58 = 7512 | 16#202D/D | 16#86/01/71 = 134/01/113 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 981
SRJ3 | SF09 REGISTER x (1 is last) | 16#1D59 = 7513 | 16#202D/E | 16#86/01/72 = 134/01/114 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 982
SRJ4 | SF09 REGISTER x (1 is last) | 16#1D5A = 7514 | 16#202D/F | 16#86/01/73 = 134/01/115 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 983
SRJ5 | SF09 REGISTER x (1 is last) | 16#1D5B = 7515 | 16#202D/10 | 16#86/01/74 = 134/01/116 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 984
SRJ6 | SF09 REGISTER x (1 is last) | 16#1D5C = 7516 | 16#202D/11 | 16#86/01/75 = 134/01/117 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 985
SRJ7 | SF09 REGISTER x (1 is last) | 16#1D5D = 7517 | 16#202D/12 | 16#86/01/76 = 134/01/118 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 986
SRJ8 | SF09 REGISTER x (1 is last) | 16#1D5E = 7518 | 16#202D/13 | 16#86/01/77 = 134/01/119 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 987
SRK1 | SF10 REGISTER x (1 is last) | 16#1D61 = 7521 | 16#202D/16 | 16#86/01/7A = 134/01/122 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 988
SRK2 | SF10 REGISTER x (1 is last) | 16#1D62 = 7522 | 16#202D/17 | 16#86/01/7B = 134/01/123 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 989
SRK3 | SF10 REGISTER x (1 is last) | 16#1D63 = 7523 | 16#202D/18 | 16#86/01/7C = 134/01/124 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 990
SRK4 | SF10 REGISTER x (1 is last) | 16#1D64 = 7524 | 16#202D/19 | 16#86/01/7D = 134/01/125 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 991
SRK5 | SF10 REGISTER x (1 is last) | 16#1D65 = 7525 | 16#202D/1A | 16#86/01/7E = 134/01/126 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 992
SRK6 | SF10 REGISTER x (1 is last) | 16#1D66 = 7526 | 16#202D/1B | 16#86/01/7F = 134/01/127 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 993
SRK7 | SF10 REGISTER x (1 is last) | 16#1D67 = 7527 | 16#202D/1C | 16#86/01/80 = 134/01/128 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 994
SRK8 | SF10 REGISTER x (1 is last) | 16#1D68 = 7528 | 16#202D/1D | 16#86/01/81 = 134/01/129 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 995
SRL1 | SF11 REGISTER x (1 is last) | 16#1D6B = 7531 | 16#202D/20 | 16#86/01/84 = 134/01/132 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 996
SRL2 | SF11 REGISTER x (1 is last) | 16#1D6C = 7532 | 16#202D/21 | 16#86/01/85 = 134/01/133 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 997
SRL3 | SF11 REGISTER x (1 is last) | 16#1D6D = 7533 | 16#202D/22 | 16#86/01/86 = 134/01/134 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 998
SRL4 | SF11 REGISTER x (1 is last) | 16#1D6E = 7534 | 16#202D/23 | 16#86/01/87 = 134/01/135 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 999
SRL5 | SF11 REGISTER x (1 is last) | 16#1D6F = 7535 | 16#202D/24 | 16#86/01/88 = 134/01/136 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 1000
SRL6 | SF11 REGISTER x (1 is last) | 16#1D70 = 7536 | 16#202D/25 | 16#86/01/89 = 134/01/137 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 1001
SRL7 | SF11 REGISTER x (1 is last) | 16#1D71 = 7537 | 16#202D/26 | 16#86/01/8A = 134/01/138 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 1002
SRL8 | SF11 REGISTER x (1 is last) | 16#1D72 = 7538 | 16#202D/27 | 16#86/01/8B = 134/01/139 | - | Safety function | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 |  |  | 1003
R1F | R1 FallBack Enable | 16#10C2 = 4290 | 16#200C/5B | 16#76/01/5B = 118/01/91 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (r1F) | [R1 CONFIGURATION] (r1-) | 1004
R2F | R2 FallBack Enable | 16#10C3 = 4291 | 16#200C/5C | 16#76/01/5C = 118/01/92 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (r2F) | [R2 CONFIGURATION] (r2-) | 1005
HRFC | Extended Fault Reset | 16#1BEE = 7150 | 16#2029/33 | 16#84/01/97 = 132/01/151 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] (nO) | - | (HrFC) | [FAULT RESET] (rSt-) | 1006
SMSA | SMS Activation | 16#3C14 = 15380 | 16#207B/51 | 16#AD/01/B5 = 173/01/181 | SMSA | Safety function | R/WS | WORD (Enumeration) | - | (nO) | - |  |  | 1007
SMLL | SMS Low Limit | 16#3C15 = 15381 | 16#207B/52 | 16#AD/01/B6 = 173/01/182 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | - |  |  | 1008
SMLH | SMS High Limit | 16#3C16 = 15382 | 16#207B/53 | 16#AD/01/B7 = 173/01/183 | - | Safety function | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | - |  |  | 1009
SMLS | SMS Assignment | 16#3C17 = 15383 | 16#207B/54 | 16#AD/01/B8 = 173/01/184 | SPSL | Safety function | R/WS | WORD (Enumeration) | - | (nO) | - |  |  | 1010
SMSS | SMS Status | 16#3C18 = 15384 | 16#207B/55 | 16#AD/01/B9 = 173/01/185 | SMSS | Safety function | R | WORD (Enumeration) | - |  | - | (SMSS) | [MONIT. SAFETY] (SAF-) | 1011
GDLA | GDL Assignment | 16#3C1E = 15390 | 16#207B/5B | 16#AD/01/BF = 173/01/191 | SMSA | Safety function | R/WS | WORD (Enumeration) | - | (nO) | - |  |  | 1012
GLLD | GDL Long Delay | 16#3C1F = 15391 | 16#207B/5C | 16#AD/01/C0 = 173/01/192 | - | Safety function | R/WS | UINT (Unsigned16) | 1 s | 1 s | 1 s ... 3600 s |  |  | 1013
GLSD | GDL Short Delay | 16#3C20 = 15392 | 16#207B/5D | 16#AD/01/C1 = 173/01/193 | - | Safety function | R/WS | UINT (Unsigned16) | 1 s | 1 s | 1 s ... 3600 s |  |  | 1014
GDLS | GDL Status | 16#3C21 = 15393 | 16#207B/5E | 16#AD/01/C2 = 173/01/194 | GDLS | Safety function | R | WORD (Enumeration) | - |  | - | (GdLS) | [MONIT. SAFETY] (SAF-) | 1015

## Enumerations
Code | Values | Display | Description
ACT | 0 | [Not done] (tAb)
| 1 | [Pending] (PEnd)
| 2 | [In Progress] (PrOG)
| 3 | [Failed] (FAIL)
| 4 | [Done] (dOnE)
ACTION | 0 | [No action] (nO)
| 1 | [Do tune] (YES)
| 2 | [Erase tune] (CLr)
ADC | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [Continuous] (Ct)
AIOL | 0 | [0 - 100%] (POS)
| 1 | [+/- 100%] (nEG)
AIOT | 1 | [Voltage] (10U)
| 2 | [Current] (0A)
| 5 | [Voltage +/-] (n10U)
AST | 3 | [IPM align.] (IPMA)
| 4 | [SPM align] (SPMA)
| 5 | [PSI align.] (PSI)
| 6 | [PSIO align.] (PSIO)
| 254 | [No align.] (nO)
AUT | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [One] (OnE)
BDCO | 38 | [50 kbps] (50 )
| 52 | [125 kbps] (125 )
| 60 | [250 kbps] (250 )
| 68 | [500 kbps] (500 )
| 76 | [1 Mbps] (1M)
BFR | 0 | [50Hz IEC] (50)
| 1 | [60Hz NEMA] (60)
BIP | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [2 IBR] (2Ibr)
BLC | 0 | [No] (nO)
| 2 | [R2] (r2)
| 17 | [LO1] (LO1)
| 64 | [DO1] (dO1)
BMP | 0 | [Stop] (StOP)
| 1 | [Bumpless] (bUMP)
BOA | 0 | [Inactive] (nO)
| 1 | [Dynamic] (dYnA)
| 2 | [Static] (StAt)
BRA | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [High torq. A] (dYnA)
BSP | 0 | [Standard] (bSd)
| 1 | [Pedestal] (bLS)
| 2 | [Deadband] (bnS)
| 4 | [Deadband 0] (bnS0)
BST | 0 | [Traveling] (HOr)
| 1 | [Hoisting] (UEr)
CDX | 1 | [Terminals] (tEr)
| 2 | [Local] (LOC)
| 3 | [HMI] (LCC)
| 10 | [Modbus] (Mdb)
| 20 | [CANopen] (CAn)
| 30 | [Com. card] (nEt)
CFG | 0 | [Start/Stop] (StS)
| 1 | [M. handling] (HdG)
| 2 | [Hoisting] (HSt)
| 3 | [Gen. Use] (GEn)
| 4 | [PID regul.] (PId)
| 5 | [Network C.] (nEt)
CFPS | 0 | [None] (nO)
| 1 | [Set n°1] (CFP1)
| 2 | [Set n°2] (CFP2)
| 3 | [Set n°3] (CFP3)
CHCF | 1 | [Not separ.] (SIM)
| 2 | [Separate] (SEP)
| 3 | [I/O profile] (IO)
CIOA | 0 | [20/70] (20)
| 1 | [21/71] (21)
| 2 | [100/101] (100)
| 3 | [Unconfig.] (UnCG)
CNFS | 0 | [In progress] (nO)
| 1 | [Config. n°0] (CnF0)
| 2 | [Config. n°1] (CnF1)
| 3 | [Config. n°2] (CnF2)
CNL | 0 | [Terminals] (tErM)
| 1 | [Local] (LOC)
| 2 | [HMI] (HMI)
| 3 | [Modbus] (Mdb)
| 6 | [CANopen] (CAn)
| 7 | [+/- speed] (tUd)
| 8 | [LUD->NotDef] (LUd)
| 9 | [Com. card] (nEt)
| 14 | [Mfg] (Ind)
| 15 | [PC tool] (PWS)
COP | 0 | [No] (nO)
| 1 | [Reference] (SP)
| 2 | [Command] (Cd)
| 3 | [Cmd + ref.] (ALL)
CSLFN | 0 | [No] (nO)
| 180 | [Jog] (FJOG)
| 181 | [Preset spd2] (FPS1)
| 182 | [Preset spd3] (FPS2)
| 183 | [PID ref. 2] (FPr1)
| 184 | [PID ref. 3] (FPr2)
| 185 | [+Speed] (FUSP)
| 186 | [-Speed] (FdSP)
| 187 | [T/K] (Ft )
CSLOUT | 0 | [No] (nO)
| 129 | [LO1] (LO1)
| 146 | [R2] (r2)
| 161 | [DO1] (dO1)
CTT | 0 | [SVC V] (UUC)
| 3 | [Standard] (Std)
| 4 | [V/F 5pts] (UF5)
| 5 | [Sync. mot.] (SYn)
| 6 | [V/F Quad.] (UFq)
| 7 | [Energy Sav.] (nLd)
DANF | 0 | [Over] (OUEr)
| 1 | [Both] (bOtH)
DCCC | 0 | [Altivar] (AtU)
| 1 | [Lexium] (LHM)
DCCM | 0 | [No] (nO)
| 1 | [Bus & Main] (MAIn)
| 2 | [Only Bus] (bUS)
DOTD | 0 | [Freewheel] (nSt)
| 1 | [Ramp stop] (rMP)
DPMA | 1 | [MCL1] (1)
| 2 | [MCL2] (2)
DSF | 0 | [Standard] (Std)
| 1 | [Optimized] (OPt)
DUR | 0 | [5 minutes] (5)
| 1 | [10 minutes] (10)
| 2 | [30 minutes] (30)
| 3 | [1 hour] (1H)
| 4 | [2 hours] (2H)
| 5 | [3 hours] (3H)
| 6 | [Unlimited] (Ct)
EBHT | 0 | [No] (nO)
| 1 | [RS422 5V] (rS05)
| 2 | [Push Pull 24V] (PP24)
| 3 | [Open collector 15V] (OC15)
| 4 | [Open collector 12V] (OC12)
| 5 | [RS422 15V] (rS15)
| 6 | [Push Pull 15V] (PP15)
| 7 | [Push Pull 12V] (PP12)
ECFG | 0 | [Ignore] (nO)
| 1 | [Freewheel] (YES)
| 2 | [Per STT] (Stt)
| 4 | [fallback spd] (LFF)
| 5 | [Spd maint.] (rLS)
| 6 | [Ramp stop] (rMP)
| 7 | [Fast stop] (FSt)
| 8 | [DC injection] (dCI)
ENS | 1 | [AABB] (AAbb)
| 2 | [AB] (Ab)
ENU | 0 | [No] (nO)
| 1 | [Fdbk monit.] (SEC)
ERRD | 16#0000 | [No fault] (nOF)
| 16#1000 | [Precharge] (CrF)
| 16#1000 | [Motor overload] (OLF)
| 16#1000 | [Overspeed] (SOF)
| 16#1000 | [IGBT desaturation] (HdF)
| 16#1000 | [internal- CPU] (InFE)
| 16#1000 | [Ch.sw. fault] (CSF)
| 16#1000 | [Angle error] (ASF)
| 16#2230 | [IGBT short circuit] (SCF4)
| 16#2310 | [Overcurrent] (OCF)
| 16#2311 | [Proc.Overload Flt] (OLC)
| 16#2320 | [Motor short circuit] (SCF1)
| 16#2320 | [Motor short circuit] (SCF5)
| 16#2330 | [Ground short circuit] (SCF3)
| 16#3110 | [Mains overvoltage] (OSF)
| 16#3120 | [Undervoltage] (USF)
| 16#3130 | [Input phase loss] (PHF)
| 16#3310 | [Overbraking] (ObF)
| 16#3310 | [1 output phase loss] (OPF1)
| 16#3310 | [3out ph loss] (OPF2)
| 16#4210 | [Drive overheat] (OHF)
| 16#4210 | [IGBT overheat] (tJF)
| 16#4310 | [PTC fault] (OtFL)
| 16#5000 | [Out. contact. stuck] (FCF1)
| 16#5000 | [Out. contact. open.] (FCF2)
| 16#5000 | [input contactor] (LCF)
| 16#5210 | [Internal- I measure] (InF9)
| 16#5210 | [Internal-mains circuit] (InFA)
| 16#5210 | [Internal- th. sensor] (InFb)
| 16#5530 | [Control Eeprom] (EEF1)
| 16#5530 | [Power Eeprom] (EEF2)
| 16#6100 | [Rating error] (InF1)
| 16#6100 | [PWR Calib.] (InF2)
| 16#6100 | [Int.serial link] (InF3)
| 16#6100 | [Int.Mfg area] (InF4)
| 16#6100 | [Cards pairing] (HCF)
| 16#6300 | [Incorrect config.] (CFF)
| 16#6300 | [Invalid config.] (CFI)
| 16#6300 | [Bad conf] (CFI2)
| 16#7000 | [Internal-option] (InF6)
| 16#7110 | [Brake feedback] (brF)
| 16#7300 | [Load slipping] (AnF)
| 16#7300 | [LI6=PTC probe] (PtFL)
| 16#7300 | [AI3 4-20mA loss] (LFF3)
| 16#7310 | [Speed fdback loss] (SPF)
| 16#7400 | [FB fault] (FbE)
| 16#7400 | [FB stop flt.] (FbES)
| 16#7510 | [Modbus com.] (SLF1)
| 16#7510 | [HMI com.] (SLF3)
| 16#7520 | [int. com.link] (ILF)
| 16#7520 | [Com. network] (CnF)
| 16#7530 | [PC com.] (SLF2)
| 16#8100 | [CAN com.] (COF)
| 16#9000 | [External flt-LI/Bit] (EPF1)
| 16#9000 | [External fault com.] (EPF2)
| 16#FF00 | [Auto-tuning] (tnF)
| 16#FF01 | [Brake control] (bLF)
| 16#FF02 | [Torque/current lim] (SSF)
| 16#FF03 | [Pr.Underload.Flt] (ULF)
| 16#FF03 | [Safety fault] (SAFF)
| 16#FF80 | [Load fault] (dLF)
ETHM | 0 | [ModbusTCP] (MbtP)
| 1 | [EthernetIP] (EtIP)
ETST | 1 | [Init] (InIt)
| 2 | [PreOp] (PrOP)
| 3 | [Boot] (bOOt)
| 4 | [SafeOp] (SFOP)
| 8 | [Op] (OP)
FBFT | 0 | [No] (nO)
| 1 | [Internal] (Int)
| 2 | [Binary file] (bIn)
| 3 | [Intern para.] (InP)
| 4 | [Para. RW] (PAr)
| 5 | [Calculation] (CAL)
| 6 | [TO AUX] (tOAU)
| 7 | [TO synch] (tOPP)
| 8 | [Bad ADLC] (AdL)
| 9 | [Input assig.] (In)
FBST | 0 | [Idle] (IdLE)
| 1 | [Check prog.] (CHEC)
| 2 | [Stop] (StOP)
| 3 | [Init] (InIt)
| 4 | [Run] (rUn)
| 5 | [Error] (Err)
FCS | 0 | [NO] (nO)
| 2 | [Internal 1] (rEC1)
| 3 | (rEC2)
| 64 | [Factory set.] (InI)
| 71 | (InI1)
FFM | 0 | [Standard] (Std)
| 1 | [Always] (rUn)
| 2 | [Never] (StP)
FLU | 0 | [Not cont.] (FnC)
| 1 | [Continuous] (FCt)
| 2 | [No] (FnO)
FOR | 0 | [No] (nO)
| 1 | [AUTO] (AUtO)
| 2 | [8-O-1] (8o1)
| 3 | [8-E-1] (8E1)
| 4 | [8-N-1] (8n1)
| 5 | [8-N-2] (8n2)
| 6 | [7-O-1] (7o1)
| 7 | [7-E-1] (7E1)
| 8 | [7-O-2] (7o2)
| 9 | [7-E-2] (7E2)
GDLS | 0 | (nO)
| 1 | (OFF)
| 2 | (Std)
| 3 | (LGd)
| 4 | (On)
| 5 | (FLt)
HMIS | 0 | [Auto-tuning] (tUn)
| 1 | [In DC inject.] (dCb)
| 2 | [Ready] (rdY)
| 3 | [Freewheel] (nSt)
| 4 | [Drv running] (rUn)
| 5 | [In accel.] (ACC)
| 6 | [In decel.] (dEC)
| 7 | [Current lim.] (CLI)
| 8 | [Fast stop] (FSt)
| 9 | [Mot. fluxing] (FLU)
| 11 | [no mains V.] (nLP)
| 12 | [Active PWR] (PrA)
| 13 | [control.stop] (CtL)
| 14 | [Dec. adapt.] (Obr)
| 15 | [Output cut] (SOC)
| 17 | [UnderV. al.] (USA)
| 18 | [In mfg. test] (tC)
| 19 | [in autotest] (St)
| 20 | [autotest err] (FA)
| 21 | [Autotest OK] (YES)
| 22 | [eeprom test] (EP)
| 23 | [In fault] (FLt)
| 25 | [DCP] (dCP)
| 28 | [SS1 active] (SS1)
| 29 | [SLS active] (SLS)
| 30 | [STO active] (StO)
| 31 | (SMS)
| 32 | (GdL)
HSO | 0 | [No] (nO)
| 1 | [Speed ref] (SSO)
| 2 | [I Limit] (CSO)
INCPER | 0 | [0,01%] (0.01)
| 1 | [0,1%] (0.1)
| 2 | [1%] (1)
INR | 0 | [0.01] (0.01)
| 1 | [0.1] (0.1)
| 2 | [1] (1)
IPAE | 0 | [Idle state] (IdLE)
| 1 | [Initialization] (InIt)
| 2 | [Config] (COnF)
| 3 | [Ready] (rdY)
| 4 | [Operation.] (OPE)
| 5 | [Unconfig.] (UCFG)
| 6 | [Unrec. fault] (UrEC)
IPM | 0 | [Fixed] (MAnU)
| 1 | [BOOTP] (bOOtP)
| 2 | [DHCP] (dHCP)
| 3 | [DCP] (dCP)
L_H | 0 | [Active low] (LO)
| 1 | [Active high] (HIG)
LFT | 0 | [No fault] (nOF)
| 2 | [Control Eeprom] (EEF1)
| 3 | [Incorrect config.] (CFF)
| 4 | [Invalid config.] (CFI)
| 5 | [Modbus com.] (SLF1)
| 6 | [int. com.link] (ILF)
| 7 | [Com. network] (CnF)
| 8 | [External flt-LI/Bit] (EPF1)
| 9 | [Overcurrent] (OCF)
| 10 | [Precharge] (CrF)
| 11 | [Speed fdback loss] (SPF)
| 12 | [Load slipping] (AnF)
| 16 | [Drive overheat] (OHF)
| 17 | [Motor overload] (OLF)
| 18 | [Overbraking] (ObF)
| 19 | [Mains overvoltage] (OSF)
| 20 | [1 output phase loss] (OPF1)
| 21 | [Input phase loss] (PHF)
| 22 | [Undervoltage] (USF)
| 23 | [Motor short circuit] (SCF1)
| 24 | [Overspeed] (SOF)
| 25 | [Auto-tuning] (tnF)
| 26 | [Rating error] (InF1)
| 27 | [PWR Calib.] (InF2)
| 28 | [Int.serial link] (InF3)
| 29 | [Int.Mfg area] (InF4)
| 30 | [Power Eeprom] (EEF2)
| 32 | [Ground short circuit] (SCF3)
| 33 | [3out ph loss] (OPF2)
| 34 | [CAN com.] (COF)
| 35 | [Brake control] (bLF)
| 38 | [External fault com.] (EPF2)
| 41 | [Brake feedback] (brF)
| 42 | [PC com.] (SLF2)
| 44 | [Torque/current lim] (SSF)
| 45 | [HMI com.] (SLF3)
| 49 | [LI6=PTC probe] (PtFL)
| 50 | [PTC fault] (OtFL)
| 51 | [Internal- I measure] (InF9)
| 52 | [Internal-mains circuit] (InFA)
| 53 | [Internal- th. sensor] (InFb)
| 54 | [IGBT overheat] (tJF)
| 55 | [IGBT short circuit] (SCF4)
| 56 | [Motor short circuit] (SCF5)
| 58 | [Out. contact. stuck] (FCF1)
| 59 | [Out. contact. open.] (FCF2)
| 64 | [input contactor] (LCF)
| 67 | [IGBT desaturation] (HdF)
| 68 | [Internal-option] (InF6)
| 69 | [internal- CPU] (InFE)
| 71 | [AI3 4-20mA loss] (LFF3)
| 73 | [Cards pairing] (HCF)
| 76 | [Load fault] (dLF)
| 77 | [Bad conf] (CFI2)
| 99 | [Ch.sw. fault] (CSF)
| 100 | [Pr.Underload.Flt] (ULF)
| 101 | [Proc.Overload Flt] (OLC)
| 105 | [Angle error] (ASF)
| 107 | [Safety fault] (SAFF)
| 108 | [FB fault] (FbE)
| 109 | [FB stop flt.] (FbES)
N_Y | 0 | [No] (nO)
| 1 | [Yes] (YES)
NCV | 0 | [Unknown rating] (nO)
| 1 | [0,12kW] (U01)
| 2 | [0,18kW / 0.25HP] (U02)
| 3 | [0,25kW] (U03)
| 4 | [0,37kW / 0.5HP] (U04)
| 5 | [0,55kW / 0.75HP] (U06)
| 6 | [0,75kW / 1HP] (U07)
| 7 | [5,5kW / 7.5HP] (U09)
| 8 | [1,1kW / 1.5HP] (U11)
| 9 | [1,5kW / 2HP] (U15)
| 10 | [1,85kW] (U18)
| 11 | [2,2kW / 3HP] (U22)
| 12 | [3kW] (U30)
| 13 | [4kW / 5HP] (U37)
| 14 | [4kW / 5HP] (U40)
| 15 | [5,5kW / 7.5HP] (U55)
| 16 | [7,5kW / 10HP] (U75)
| 17 | [9kW] (U90)
| 18 | [11kW / 15HP] (d11)
| 19 | [15kW / 20HP] (d15)
| 20 | [18,5kW / 25HP] (d18)
| 21 | [22kW / 30HP] (d22)
| 22 | [30kW / 40HP] (d30)
NPL | 0 | [1] (POS)
| 1 | [0] (nEG)
ONOFF | 0 | [OFF] (OFF)
| 1 | [ON] (On)
OPL | 0 | [No] (nO)
| 1 | [Yes] (YES)
| 2 | [Output cut] (OAC)
PRFL | 0 | [Unconfig.] (UnCG)
| 1 | [1] (1)
| 2 | [2] (2)
| 7 | [7] (7)
| 9 | [9] (9)
| 100 | [100] (100)
| 101 | [101] (101)
| 102 | [102] (102)
PSA | 0 | [No] (nO)
| 1 | [AI1] (AI1)
| 2 | [AI2] (AI2)
| 3 | [AI3] (AI3)
| 129 | [I motor] (OCr)
| 130 | [Motor freq.] (OFr)
| 131 | [Ramp out.] (OrP)
| 132 | [Motor torq.] (trq)
| 133 | [Sign. torque] (Stq)
| 134 | [sign ramp] (OrS)
| 135 | [PID ref.] (OPS)
| 136 | [PID feedbk] (OPF)
| 137 | [PID error] (OPE)
| 138 | [PID output] (OPI)
| 139 | [Mot. power] (OPr)
| 140 | [Mot thermal] (tHr)
| 141 | [Drv thermal] (tHd)
| 142 | [Torque 4Q] (tqMS)
| 160 | [+/-Speed] (UPdt)
| 161 | [+/-spd HMI] (UPdH)
| 163 | [HMI] (LCC)
| 164 | [Modbus] (Mdb)
| 167 | [CANopen] (CAn)
| 169 | [Com. card] (nEt)
| 173 | [Sig. o/p frq.] (OFS)
| 174 | [Mot therm2] (tHr2)
| 175 | [Mot therm3] (tHr3)
| 179 | [Torque lim.] (tqL)
| 180 | [Motor volt.] (UOP)
| 181 | [RP] (PI)
| 183 | [AI Virtual 1] (AIU1)
| 184 | [DO1] (dO1)
| 185 | [AI Virtual 2] (AIU2)
| 240 | [OA01] (OA01)
| 241 | [OA02] (OA02)
| 242 | [OA03] (OA03)
| 243 | [OA04] (OA04)
| 244 | [OA05] (OA05)
| 245 | [OA06] (OA06)
| 246 | [OA07] (OA07)
| 247 | [OA08] (OA08)
| 248 | [OA09] (OA09)
| 249 | [OA10] (OA10)
PSL | 0 | [No] (nO)
| 1 | [No drive flt] (FLt)
| 2 | [Drv running] (rUn)
| 3 | [Output cont] (OCC)
| 4 | [Freq.Th.att.] (FtA)
| 5 | [HSP attain.] (FLA)
| 6 | [I attained] (CtA)
| 7 | [Freq.ref.att] (SrA)
| 8 | [Th.mot. att.] (tSA)
| 9 | [Brk control] (bLC)
| 10 | [PID error al.] (PEE)
| 11 | [PID fdbk al.] (PFA)
| 13 | [FreqTh.att.2] (F2A)
| 14 | [Th. drv. att.] (tAd)
| 21 | [Pro.Undload] (ULA)
| 22 | [Ovld.P.Alrm] (OLA)
| 27 | [Rope slack] (rSdA)
| 28 | [High tq. att.] (ttHA)
| 29 | [Low tq. att.] (ttLA)
| 30 | [Forward] (MFrd)
| 31 | [Reverse] (MrrS)
| 37 | [Th.mot2 att] (tS2)
| 38 | [Th.mot3 att] (tS3)
| 47 | [Neg Torque] (AtS)
| 48 | [Cnfg.0 act.] (CnF0)
| 49 | [Cnfg.1 act.] (CnF1)
| 50 | [Cnfg.2 act.] (CnF2)
| 52 | [set 1 active] (CFP1)
| 53 | [set 2 active] (CFP2)
| 54 | [set 3 active] (CFP3)
| 64 | [DC charged] (dbL)
| 65 | [In braking] (brS)
| 66 | [P. removed] (PrM)
| 72 | [Fr.met. alar.] (FqLA)
| 73 | [Input cont.] (LLC)
| 77 | [I present] (MCP)
| 78 | [Limit sw.att] (LSA)
| 79 | [Load alarm] (dLdA)
| 80 | [Alarm Grp 1] (AG1)
| 81 | [Alarm Grp 2] (AG2)
| 82 | [Alarm Grp 3] (AG3)
| 85 | [LI6=PTC al.] (PLA)
| 87 | [Ext. fault al] (EFA)
| 88 | [Under V. al.] (USA)
| 89 | [Uvolt warn] (UPA)
| 91 | [Al. °C drv.] (tHA)
| 95 | [Lim T/I att.] (SSA)
| 96 | [ch1 active] (Fr1)
| 97 | [ch2 active] (Fr2)
| 98 | [ch1 active] (Cd1)
| 99 | [ch2 active] (Cd2)
| 100 | [ch1B active] (Fr1b)
| 101 | [Spool end] (EbO)
| 102 | [Sync wobbl] (tSY)
| 104 | [IGBT al.] (tJA)
| 107 | [AI3 Al. 4-20] (AP3)
| 116 | [SHORT#FN1] (Fn1)
| 117 | [SHORT#FN2] (Fn2)
| 118 | [SHORT#FN3] (Fn3)
| 119 | [SHORT#FN4] (Fn4)
| 127 | [Ready] (rdY)
| 128 | [Yes] (YES)
| 129 | [LI1] (LI1)
| 130 | [LI2] (LI2)
| 131 | [LI3] (LI3)
| 132 | [LI4] (LI4)
| 133 | [LI5] (LI5)
| 134 | [LI6] (LI6)
| 143 | [LAI1] (LAI1)
| 144 | [LAI2] (LAI2)
| 160 | [CD00] (Cd00)
| 161 | [CD01] (Cd01)
| 162 | [CD02] (Cd02)
| 163 | [CD03] (Cd03)
| 164 | [CD04] (Cd04)
| 165 | [CD05] (Cd05)
| 166 | [CD06] (Cd06)
| 167 | [CD07] (Cd07)
| 168 | [CD08] (Cd08)
| 169 | [CD09] (Cd09)
| 170 | [CD10] (Cd10)
| 171 | [CD11] (Cd11)
| 172 | [CD12] (Cd12)
| 173 | [CD13] (Cd13)
| 174 | [CD14] (Cd14)
| 175 | [CD15] (Cd15)
| 176 | [C100] (C100)
| 177 | [C101] (C101)
| 178 | [C102] (C102)
| 179 | [C103] (C103)
| 180 | [C104] (C104)
| 181 | [C105] (C105)
| 182 | [C106] (C106)
| 183 | [C107] (C107)
| 184 | [C108] (C108)
| 185 | [C109] (C109)
| 186 | [C110] (C110)
| 187 | [C111] (C111)
| 188 | [C112] (C112)
| 189 | [C113] (C113)
| 190 | [C114] (C114)
| 191 | [C115] (C115)
| 192 | [C200] (C200)
| 193 | [C201] (C201)
| 194 | [C202] (C202)
| 195 | [C203] (C203)
| 196 | [C204] (C204)
| 197 | [C205] (C205)
| 198 | [C206] (C206)
| 199 | [C207] (C207)
| 200 | [C208] (C208)
| 201 | [C209] (C209)
| 202 | [C210] (C210)
| 203 | [C211] (C211)
| 204 | [C212] (C212)
| 205 | [C213] (C213)
| 206 | [C214] (C214)
| 207 | [C215] (C215)
| 208 | [C300] (C300)
| 209 | [C301] (C301)
| 210 | [C302] (C302)
| 211 | [C303] (C303)
| 212 | [C304] (C304)
| 213 | [C305] (C305)
| 214 | [C306] (C306)
| 215 | [C307] (C307)
| 216 | [C308] (C308)
| 217 | [C309] (C309)
| 218 | [C310] (C310)
| 219 | [C311] (C311)
| 220 | [C312] (C312)
| 221 | [C313] (C313)
| 222 | [C314] (C314)
| 223 | [C315] (C315)
| 240 | [OL01] (OL01)
| 241 | [OL02] (OL02)
| 242 | [OL03] (OL03)
| 243 | [OL04] (OL04)
| 244 | [OL05] (OL05)
| 245 | [OL06] (OL06)
| 246 | [OL07] (OL07)
| 247 | [OL08] (OL08)
| 248 | [OL09] (OL09)
| 249 | [OL10] (OL10)
| 250 | (GdL)
PSLIN | 0 | [No] (nO)
| 1 | [No drive flt] (FLt)
| 4 | [Freq.Th.att.] (FtA)
| 13 | [FreqTh.att.2] (F2A)
| 96 | [ch1 active] (Fr1)
| 97 | [ch2 active] (Fr2)
| 98 | [ch1 active] (Cd1)
| 99 | [ch2 active] (Cd2)
| 100 | [ch1B active] (Fr1b)
| 128 | [Yes] (YES)
| 129 | [LI1] (LI1)
| 130 | [LI2] (LI2)
| 131 | [LI3] (LI3)
| 132 | [LI4] (LI4)
| 133 | [LI5] (LI5)
| 134 | [LI6] (LI6)
| 143 | [LAI1] (LAI1)
| 144 | [LAI2] (LAI2)
| 160 | [CD00] (Cd00)
| 161 | [CD01] (Cd01)
| 162 | [CD02] (Cd02)
| 163 | [CD03] (Cd03)
| 164 | [CD04] (Cd04)
| 165 | [CD05] (Cd05)
| 166 | [CD06] (Cd06)
| 167 | [CD07] (Cd07)
| 168 | [CD08] (Cd08)
| 169 | [CD09] (Cd09)
| 170 | [CD10] (Cd10)
| 171 | [CD11] (Cd11)
| 172 | [CD12] (Cd12)
| 173 | [CD13] (Cd13)
| 174 | [CD14] (Cd14)
| 175 | [CD15] (Cd15)
| 177 | [C101] (C101)
| 178 | [C102] (C102)
| 179 | [C103] (C103)
| 180 | [C104] (C104)
| 181 | [C105] (C105)
| 182 | [C106] (C106)
| 183 | [C107] (C107)
| 184 | [C108] (C108)
| 185 | [C109] (C109)
| 186 | [C110] (C110)
| 187 | [C111] (C111)
| 188 | [C112] (C112)
| 189 | [C113] (C113)
| 190 | [C114] (C114)
| 191 | [C115] (C115)
| 193 | [C201] (C201)
| 194 | [C202] (C202)
| 195 | [C203] (C203)
| 196 | [C204] (C204)
| 197 | [C205] (C205)
| 198 | [C206] (C206)
| 199 | [C207] (C207)
| 200 | [C208] (C208)
| 201 | [C209] (C209)
| 202 | [C210] (C210)
| 203 | [C211] (C211)
| 204 | [C212] (C212)
| 205 | [C213] (C213)
| 206 | [C214] (C214)
| 207 | [C215] (C215)
| 209 | [C301] (C301)
| 210 | [C302] (C302)
| 211 | [C303] (C303)
| 212 | [C304] (C304)
| 213 | [C305] (C305)
| 214 | [C306] (C306)
| 215 | [C307] (C307)
| 216 | [C308] (C308)
| 217 | [C309] (C309)
| 218 | [C310] (C310)
| 219 | [C311] (C311)
| 220 | [C312] (C312)
| 221 | [C313] (C313)
| 222 | [C314] (C314)
| 223 | [C315] (C315)
| 240 | [OL01] (OL01)
| 241 | [OL02] (OL02)
| 242 | [OL03] (OL03)
| 243 | [OL04] (OL04)
| 244 | [OL05] (OL05)
| 245 | [OL06] (OL06)
| 246 | [OL07] (OL07)
| 247 | [OL08] (OL08)
| 248 | [OL09] (OL09)
| 249 | [OL10] (OL10)
PTCX | 0 | [No] (nO)
| 1 | [Always] (AS)
| 2 | [Power ON] (rdS)
| 3 | [Motor ON] (rS)
QSTD | 2 | (FSt2)
| 6 | (FSt6)
RDS | 0 | [Auto] (AUtO)
| 1 | [10M. full] (10F)
| 2 | [10M. half] (10H)
| 3 | [100M. full] (100F)
| 4 | [100M. half] (100H)
RPR | 0 | [No] (nO)
| 1 | [reset kWh] (APH)
| 2 | [rst. runtime] (rtH)
| 3 | [rst runtim I] (rtHI)
| 4 | [rst. P On t.] (PtH)
| 64 | [Reset all] (ALL)
RPT | 0 | [Linear] (LIn)
| 1 | [S ramp] (S)
| 2 | [U ramp] (U)
| 3 | [Customized] (CUS)
RSD | 0 | [No] (nO)
| 1 | [Drive estim.] (drI)
| 2 | [Ext. sensor] (PES)
SCS | 0 | [No] (nO)
| 1 | [Config 0] (Str0)
| 2 | [Config 1] (Str1)
| 3 | [Config 2] (Str2)
SFT | 1 | [SFR type 1] (HF1)
| 2 | [SFR type 2] (HF2)
SFTY | 0 | [Standard] (Std)
| 1 | [Safe] (SAFE)
SLSS | 0 | [Not config.] (nO)
| 1 | [Idle] (IdLE)
| 2 | [Safe ramp] (SS1)
| 3 | [Spd limited] (SLS)
| 4 | [Safe stop] (StO)
| 5 | [Fault] (FLt)
| 6 | [SLS wait] (WAIt)
| 7 | [SLS Start] (Strt)
SLT | 0 | (tYP1)
| 1 | (tYP2)
| 2 | (tYP3)
| 3 | (tYP4)
| 4 | (tYP5)
| 5 | (tYP6)
SMOT | 0 | [No info.] (nO)
| 1 | [Low salient] (LLS)
| 2 | [Med salient] (MLS)
| 3 | [High salient] (HLS)
SMSA | 0 | (nO)
| 1 | (YES)
SMSS | 0 | (nO)
| 1 | (SMS)
| 2 | (FtI)
| 3 | (FtO)
SOP | 6 | [6 µs] (6)
| 8 | [8 µs] (8)
| 10 | [10 µs] (10)
SPIG | 0 | [Stop] (StOP)
| 1 | [Ignore] (IGn)
SPSL | 0 | (nO)
| 1 | (L34)
| 2 | (L56)
| 3 | (L3PW)
| 4 | (PWrM)
SPST | 0 | [Stop] (StOP)
| 1 | [Start] (Strt)
SS1S | 0 | [Not config.] (nO)
| 1 | [Idle] (IdLE)
| 2 | [Safe ramp] (SS1)
| 3 | [Safe stop] (StO)
| 4 | [Fault] (FLt)
SSRU | 0 | (1H)
| 1 | (10H)
| 2 | (100H)
STOS | 0 | [Idle] (IdLE)
| 1 | [Safe stop] (StO)
| 2 | [Fault] (FLt)
STP | 0 | [No] (nO)
| 1 | [DC Maintain] (MMS)
| 2 | [Ramp stop] (rMP)
| 4 | [Lock-out] (LnF)
STR | 0 | [No] (nO)
| 1 | [RAM] (rAM)
| 2 | [EEprom] (EEP)
STT | 0 | [Ramp stop] (rMP)
| 1 | [Fast stop] (FSt)
| 2 | [Freewheel] (nSt)
| 3 | [DC injection] (dCI)
STUN | 0 | [Default] (tAb)
| 1 | [Measure] (MEAS)
| 2 | [Custom] (CUS)
TBR | 0 | [Not config.] (nO)
| 4 | [Automatic] (AUtO)
| 8 | [300 bps] (300)
| 12 | [600 bps] (600)
| 16 | [1.2 Kbps] (1 2)
| 20 | [2.4 Kbps] (2 4)
| 24 | [4.8 Kbps] (4 8)
| 28 | [9.6 Kbps] (9 6)
| 30 | [10 Kbps] (10 )
| 32 | [19.2 Kbps] (19 2)
| 34 | [20 Kbps] (20 )
| 35 | [28.8 Kbps] (28 8)
| 36 | [38.4 Kbps] (38 4)
| 37 | [45.45 Kbps] (45 4)
| 38 | [50 Kbps] (50 )
| 40 | [57.6 Kbps] (57 6)
| 42 | [93.75 Kbps] (93 7)
| 44 | [100 Kbps] (100 )
| 48 | [115.2 Kbps] (115 )
| 52 | [125 Kbps] (125 )
| 53 | [156 Kbps] (156 )
| 54 | [187.5 Kbps] (187 )
| 56 | [230.4 Kbps] (230 )
| 60 | [250 Kbps] (250 )
| 64 | [460.8 Kbps] (460 )
| 68 | [500 Kbps] (500 )
| 69 | [625 Kbps] (625 )
| 70 | [800 Kbps] (800 )
| 72 | [921.6 Kbps] (921 )
| 76 | [1 Mbps] (1M)
| 80 | [1.5 Mbps] (1M5)
| 81 | [2.5 Mbps] (2M5)
| 82 | [3 Mbps] (3M)
| 83 | [6 Mbps] (6M)
| 84 | [10 Mbps] (10M)
| 86 | [5 Mbps] (5M)
| 88 | [12 Mbps] (12M)
| 92 | [100 Mbps] (100M)
TCC | 0 | [2 wire] (2C)
| 1 | [3 wire] (3C)
TCT | 0 | [Level] (LEL)
| 1 | [Transition] (trn)
| 2 | [Fwd priority] (PFO)
THT | 0 | [No] (nO)
| 1 | [Self cooled] (ACL)
| 2 | [Force-cool] (FCL)
TUNU | 0 | [No] (nO)
| 1 | [Therm mot] (tM)
| 2 | [Cold tun] (Ct)
URES | 20 | [200V ac] (200)
| 22 | [220V ac] (220)
| 23 | [230V ac] (230)
| 24 | [240V ac] (240)
| 38 | [380V ac] (380)
| 40 | [400V ac] (400)
| 44 | [440V ac] (440)
| 46 | [460V ac] (460)
| 50 | [500V ac] (500)
| 53 | (525)
| 60 | [600V ac] (600)
| 254 | [Lexium] (LHM)
USB | 0 | [Std fault] (0)
| 1 | [Flt wo relay] (1)
| 2 | [Alarm] (2)
VCAL | 0 | [No] (nO)
| 1 | [100-120(1)] (110M)
| 2 | [100-120(3)] (110t)
| 3 | [200-240(1)] (M2)
| 4 | [200-240(3)] (M3)
| 5 | [380-500(1)] (480M)
| 6 | [380-500(3)] (n4)
| 7 | [525-600(1)] (690M)
| 8 | [525-600(3)] (S6)
| 9 | [500 / 600V] (600M)
| 10 | [500 / 600V] (S6X)

## Registers
CCC CRC |  | Bit 0: | = 1: The terminal board is the active channel.
|  | Bit 1: | = 1: The local keypad is the active channel.
|  | Bit 2: | = 1: The remote keypad is the active channel.
|  | Bit 3: | = 1: Modbus is the active channel.
|  | Bit 4: | Reserved (= 0).
|  | Bit 5: | Reserved (= 0).
|  | Bit 6: | = 1: CANopen is the active channel.
|  | Bit 7: | = 1: The terminals are the active channel in the +/- speed reference.
|  | Bit 8: | = 1: The remote keypad is the active channel (up-down speed)
|  | Bit 9: | = 1: The network card is the active channel.
|  | Bit 10: | Reserved (= 0).
|  | Bit 11: | Reserved (= 0).
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | Reserved (= 0).
|  | Bit 14: | Reserved (= 0).
|  | Bit 15: | = 1: SoMove software is the active channel.
CIC |  | Bit 0: | = 1: Change of rating.
|  | Bit 1: | Reserved (= 0).
|  | Bit 2: | = 1: The network card has been removed.
|  | Bit 3: | = 1: Saving to the EEPROM non-volatile memory is inconsistent with power on.
|  | Bit 4: | = 1: The network card has been changed.
|  | Bit 5: | Reserved (= 0).
|  | Bit 6: | Reserved (= 0).
|  | Bit 7: | Reserved (= 0).
|  | Bit 8: | Reserved (= 0).
|  | Bit 9: | Reserved (= 0).
|  | Bit 10: | Reserved (= 0).
|  | Bit 11: | Reserved (= 0).
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | Reserved (= 0).
|  | Bit 14: | Reserved (= 0).
|  | Bit 15: | Reserved (= 0).
If one of these events occurs, the drive will indicate a fault [Invalid config.] (CFI) and then automatically applies a factory setting.
CMD CMP0 CMP1 CMP2 CMP3 CMP4 CMP5 CMP6 CMP7 CMP8 | Possible values in CiA402 profile, separate or not separate mode:
|  | Bit 0: | Switch on/Contactor command.
|  | Bit 1: | Disable voltage/Authorization to supply AC power.
|  | Bit 2: | Quick stop/Emergency stop.
|  | Bit 3: | Enable operation/Run command.
|  | Bit 4: | Reserved (set to 0).
|  | Bit 5: | Reserved (set to 0).
|  | Bit 6: | Reserved (set to 0).
|  | Bit 7: | Fault reset/Fault acknowledgment active on 0 to 1 rising edge.
|  | Bit 8: | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
|  | Bit 9: | Reserved (set to 0).
|  | Bit 10: | Reserved (set to 0).
|  | Bit 11: | Can be assigned to commands.
|  | Bit 12: | Can be assigned to commands.
|  | Bit 13: | Can be assigned to commands.
|  | Bit 14: | Can be assigned to commands.
|  | Bit 15: | Can be assigned to commands.
Possible values in the IO profile:
On state command [2 wire] (2C).
|  | Bit 0: | Forward (on state) command
= 0: No forward command
= 1: Forward command
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
Bit 1 to Bit 15: Can be assigned to commands.
On edge command [3 wire] (3C).
|  | Bit 0: | Stop (run authorization).
= 0: Stop
= 1: Run is authorized on a forward or reverse command
|  | Bit 1: | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
Bit 2 to Bit 15 can be assigned to commands.
CMI |  | Bit 0: | Factory setting command (active at 1).
|  | Bit 1: | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2: | Reserved (= 0).
|  | Bit 3: | Reserved (= 0).
|  | Bit 4: | Reserved (= 0).
|  | Bit 5: | Reserved (= 0).
|  | Bit 6: | Reserved (= 0).
|  | Bit 7: | Reserved (= 0).
|  | Bit 8: | Reserved (= 0).
|  | Bit 9: | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0: 0.1 Hz
= 1: Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10: | Reserved (= 0).
|  | Bit 11: | Reserved (= 0).
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | Reserved (= 0).
|  | Bit 14: | Reserved (= 0).
|  | Bit 15: | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CRP0 CRP1 CRP2 CRP3 CRP4 CRP5 CRP6 CRP7 CRP8 | Bit 0 to Bit 7: Active command channels
|  | 0 = | The terminal board is the active channel.
|  | 1 = | The local keypad is the active channel.
|  | 2 = | The remote keypad is the active channel.
|  | 3 = | Modbus is the active channel.
|  | 4 = | Reserved
|  | 5 = | Reserved
|  | 6 = | CANopen is the active channel.
|  | 7 = | The terminals are the active channel in the +/- speed reference.
|  | 8 = | The remote keypad is the active channel (up-down speed)
|  | 9 = | The network card is the active channel.
|  | 10 = | Reserved
|  | 11 = | Reserved
|  | 12 = | Reserved
|  | 13 = | Reserved
|  | 14 = | Reserved
|  | 15 = | SoMove software is the active channel.
Bit 8 to Bit 15: Active reference channels
|  | 0 = | The terminals are the active channel via an analog input.
|  | 1 = | The local keypad is the active channel.
|  | 2 = | The remote keypad is the active channel.
|  | 3 = | Modbus is the active channel.
|  | 4 = | Reserved
|  | 5 = | Reserved
|  | 6 = | CANopen is the active channel.
|  | 7 = | The terminals are the active channel in the +/- speed reference.
|  | 8 = | The remote keypad is the active channel (up-down speed)
|  | 9 = | The network card is the active channel.
|  | 10 = | Reserved
|  | 11 = | Reserved
|  | 12 = | Reserved
|  | 13 = | Reserved
|  | 14 = | Reserved
|  | 15 = | SoMove software is the active channel.
ETA EP0 EP1 EP2 EP3 EP4 EP5 EP6 EP7 EP8 | Possible values in CiA402 profile, separate or not separate mode:
|  | Bit 0: | = 1: "Ready to switch on", awaiting power section line supply
|  | Bit 1: | = 1: "Switched on", ready
|  | Bit 2: | = 1: "Operation enabled", running
|  | Bit 3: | = 1: Fault detection
|  | Bit 4: | "Voltage enabled", power section line supply present
= 0: Power section line supply absent
= 1: Power section line supply present
When the drive is powered by the power section only, this bit is always at 1.
|  | Bit 5: | = 0: Quick stop/Emergency stop
|  | Bit 6: | = 1: "Switched on disabled", power section line supply locked
|  | Bit 7: | Warning, alarm
= 0: No alarm
= 1: Alarm
|  | Bit 8: | Reserved (= 0)
|  | Bit 9: | Remote: command or reference via the network
= 0: Command or reference via the graphic display terminal or the remote display terminal
= 1: Command or reference via the network
|  | Bit 10: | Target reference reached
= 0: The reference is not reached
= 1: The reference has been reached
When the drive is in speed mode, this is the speed reference.
|  | Bit 11: | "Internal limit active", reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | "Stop key", STOP via stop key
= 0: STOP key not pressed
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15: | "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (see the Communication manuals).
Possible values in the I/O profile:
Note: The value is identical in the CiA402 profile and the I/O profile. In the I/O profile, the description of the values is simplified and does not refer to the CiA402 (Drivecom) state chart.
|  | Bit 0: | Reserved (= 0 or 1)
|  | Bit 1: | Ready
= 0: Not ready
= 1: Ready
|  | Bit 2: | Running
= 0: The drive will not start if a reference other than zero is applied.
= 1: Running, if a reference other than zero is applied, the drive can start.
|  | Bit 3: | Fault
= 0: No fault
= 1: Fault
|  | Bit 4: | Power section line supply present
= 0: Power section line supply absent
= 1: Power section line supply present
|  | Bit 5: | Reserved (= 1)
|  | Bit 6: | Reserved (= 0 or 1)
|  | Bit 7: | Alarm
= 0: No alarm
= 1: Alarm
|  | Bit 8: | Reserved (= 0)
|  | Bit 9: | Command via a network
= 0: Command via the terminals or the graphic display terminal
= 1: Command via a network
|  | Bit 10: | Reference reached
= 0: The reference is not reached
= 1: The reference has been reached
|  | Bit 11: | Reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by LSP and HSP parameters.
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | Stop via STOP key
= 0: STOP key not pressed
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15: | Direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
ETI IP0 IP1 IP2 IP3 IP4 IP5 IP6 IP7 IP8 |  | Bit 0: | = 1: Access to the EEPROM non-volatile memory in progress
|  | Bit 1: | = 0: No parameter consistency check
= 1: Parameter consistency check
|  | Bit 2: | = 0: The drive is not in fault state or a fault is detected
= 1: The drive is in fault state but the fault is no longer present (not reset)
|  | Bit 3: | Reserved (= 0).
|  | Bit 4: | = 1: The drive is in speed mode
|  | Bit 5: | = 1: DC injection braking (identical to LSR4, bit 11)
|  | Bit 6: | = 0: Drive in steady state
= 1: Drive in transient state
|  | Bit 7: | = 1: Motor thermal state threshold reached for the active motor
|  | Bit 8: | = 1: Overbraking (identical to LSR5, bit 1)
|  | Bit 9: | = 1: Acceleration in progress (identical to LSR4, bit 13)
|  | Bit 10: | = 1: Deceleration in progress (identical to LSR4, bit 14)
|  | Bit 11: | = 1: Current limit in progress
|  | Bit 12: | = 1: Fast stop in progress (identical to LSR4, bit 15)
|  | Bit 13: | bit 13 = 0 and bit 14 = 0: Drive controled by terminal or local keypad
|  | Bit 14: | bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
|  | Bit 15: | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
EWE |  | Bit 0: | = 1: Enable Web
|  | Bit 1: | = 1: Enable Email
|  | Bit 2: | Reserved (= 0).
|  | Bit 3: | Reserved (= 0).
|  | Bit 4: | Reserved (= 0).
|  | Bit 5: | Reserved (= 0).
|  | Bit 6: | Reserved (= 0).
|  | Bit 7: | Reserved (= 0).
|  | Bit 8: | Reserved (= 0).
|  | Bit 9: | Reserved (= 0).
|  | Bit 10: | Reserved (= 0).
|  | Bit 11: | Reserved (= 0).
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | Reserved (= 0).
|  | Bit 14: | Reserved (= 0).
|  | Bit 15: | Reserved (= 0).
FrY | Selection of menus to be loaded.
|  | Bit 0: | = 1: [All] (ALL): all parameters.
|  | Bit 1: | = 1:[Drive menu] (drM): The [1 DRIVE MENU] (drI-) menu without [COMMUNICATION] (COM-). In the [2.4 DISPLAY CONFIG.] menu, [Return std name] returns to [No].
|  | Bit 2: | Reserved (=0 ou 1).
|  | Bit 3: | = 1:[Motor param] (MOt): Motor parameters,
The following selection is accessible only if [Config. Source] (FCSI) = [Macro-Conf] (InI) :
|  | Bit 4: | = 1:[Comm. menu] (COM): The [COMMUNICATION] (COM-) menu without either [Scan. In1 address] (nMA1) to [Scan. In8 address] (nMA8) or [Scan.Out1 address] (nCA1) to [Scan.Out8 address] (nCA8).
|  | Bit 5: | Reserved (=0 ou 1).
|  | Bit 6: | Reserved (=0 ou 1).
|  | Bit 7: | = 1: [Display config.] (dIS): The [2.3 MONITORING CONFIG.] (MCF-) menu
|  | Bit 8: | Reserved (=0 ou 1).
|  | Bit 9: | Reserved (=0 ou 1).
|  | Bit 10: | Reserved (=0 ou 1).
|  | Bit 11: | Reserved (=0 ou 1).
|  | Bit 12: | Reserved (=0 ou 1).
|  | Bit 13: | Reserved (=0 ou 1).
|  | Bit 14: | Reserved (=0 ou 1).
|  | Bit 15: | Reserved (=0 ou 1).
See the multiple selection procedure for the integrated display terminal and for the graphic display terminal.
Note: In factory configuration and after a return to "factory settings", [PARAMETER GROUP LIST] will be empty.
IL1I IL1R |  | Bit 0: | Value of LI1.
|  | Bit 1: | Value of LI2.
|  | Bit 2: | Value of LI3.
|  | Bit 3: | Value of LI4.
|  | Bit 4: | Value of LI5
|  | Bit 5: | Value of LI6
|  | Bit 6: | Reserved (= 0).
|  | Bit 7: | Reserved (= 0).
|  | Bit 8: | Reserved (= 0).
|  | Bit 9: | Reserved (= 0).
|  | Bit 10: | Reserved (= 0).
|  | Bit 11: | Reserved (= 0).
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | Reserved (= 0).
|  | Bit 14: | Reserved (= 0).
|  | Bit 15: | Reserved (= 0).
LRS1 |  | Bit 0: | Reserved (= 0)
|  | Bit 1: | = 1: The drive is in fault state.
|  | Bit 2: | = 0: The drive is locked, the motor is not powered
= 1: The drive is unlocked, power can be supplied to the motor (RUN state)
|  | Bit 3: | = 1: The output contactor is controlled
|  | Bit 4: | = 1: Frequency threshold (ftd) reached: [Freq. Th. attained] (FtA)
|  | Bit 5: | = 1: High speed (HSP) reached: [HSP attained] (FLA)
|  | Bit 6: | = 1: Current threshold (Ctd) reached: [Current Th. attained] (CtA)
|  | Bit 7: | = 1: Frequency reference reached: [Frequency ref. att.] (SrA)
|  | Bit 8: | = 1: Motor 1 thermal state threshold [Motor therm. level] (ttd) reached: [Motor th. state att.] (tSA)
|  | Bit 9: | = 1: Brake contactor command [Brake assignment] (bLC) active
|  | Bit 10: | = 1: PID regulator error alarm: [PID error al] (PEE)
|  | Bit 11: | = 1: PID regulator feedback alarm: [PID fdbk al.] (PFA)
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | = 1: Second frequency threshold (ftd) reached: [Freq. Th. 2 attained] (FA2)
|  | Bit 14: | = 1: Drive thermal state threshold [Drv therm. state al] (tHA) reached: [Th. drv. att.] (tAd)
|  | Bit 15: | = 1: The "traverse control" function is active
LRS2 |  | Bit 0: | Reserved (=0).
|  | Bit 1: | Reserved (=0).
|  | Bit 2: | Reserved (=0).
|  | Bit 3: | Reserved (=0).
|  | Bit 4: | Reserved (=0).
|  | Bit 5: | = 1: Undeload alarm (ULA)
|  | Bit 6: | = 1: Overload alarm (OLA)
|  | Bit 7: | Reserved (=0).
|  | Bit 8: | Reserved (=0).
|  | Bit 9: | Reserved (=0).
|  | Bit 10: | Reserved (=0).
|  | Bit 11: | = 1: Rope slack (see parameter [Rope slack config.] (rSd)).
|  | Bit 12: | = 1: [High torque alarm] (ttHA): High torque threshold reached [High torque thd.] (ttH).
|  | Bit 13: | = 1: [Low torque alarm] (ttLA): Low torque threshold reached [Low torque thd.] (ttL).
|  | Bit 14: | = 1: [Forwardt] (MFrd): Motor direction Forward.
|  | Bit 15: | = 1: [Reverse] (MrrS): Motor direction Reverse.
LRS3 |  | Bit 0: | = 0: Reference channel 1 or 1B (Fr1) or (Fr1b) is active
= 1: Reference channel 2 (Fr2) is active
|  | Bit 1: | = 0: Command channel 1 (Cd1) is active
= 1: Command channel 2 (Cd2) is active
|  | Bit 2: | = 0: Ramp set 1 (ACC) and (dEC)
= 1: Ramp set 2 (AC2) and (dE2)
|  | Bit 3: | = 0: Current limit 1 (CLI) is active
= 1: Current limit 2 (CL2) is active
|  | Bit 4: | Reserved (= 0)
|  | Bit 5: | = 1: Motor 2 thermal state threshold [Motor2 therm. level] (ttd2) reached: [Th.mot2 att] (tS2)
|  | Bit 6: | = 1: Motor 3 thermal state threshold [Motor3 therm. level] (ttd3) reached: [Th.mot3 att] (tS3)
|  | Bit 7: | Reserved (= 0)
|  | Bit 8: | 24 VDC external power supply present
|  | Bit 9: | = 1: Stop on low speed time limit function [Low speed time out] (tLS)
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | Reserved (= 0)
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | Reserved (= 0)
|  | Bit 15: | = 0: The output torque is positive (forward)
= 1: The output torque is negative (reverse)
LRS4 |  | Bit 0: | = 1: Configuration 0 is active
|  | Bit 1: | = 1: Configuration 1 is active [Cnfg.1 act.] (CnF1)
|  | Bit 2: | = 1: Configuration 2 is active [Cnfg.2 act.] (CnF2)
|  | Bit 3: | Reserved (= 0)
|  | Bit 4: | = 1: Parameter set 1 is active: [Set 1 active] (CFP1)
|  | Bit 5: | = 1: Parameter set 2 is active: [Set 2 active] (CFP2)
|  | Bit 6: | = 1: Parameter set 3 is active: [Set 3 active] (CFP3)
|  | Bit 7: | Reserved (= 0)
|  | Bit 8: | = 0: Power section line supply present
= 1: Power section line supply absent
|  | Bit 9: | = 1: Motor "fluxing" in progress: [In motor fluxing] (FLX)
|  | Bit 10: | = 1: The motor is "fluxed"
|  | Bit 11: | = 1: DC injection braking (identical to ETI, bit 5)
|  | Bit 12: | = 1: Current limiting in progress
|  | Bit 13: | = 1: Acceleration in progress (identical to ETI, bit 9)
|  | Bit 14: | = 1: Deceleration in progress (identical to ETI, bit 10)
|  | Bit 15: | = 1: Fast stop in progress: [Fast stop in prog.] (FSt) (identical to ETI, bit 12)
LRS5 |  | Bit 0: | = 1: Drive DC bus loading: [DC bus loading] (dbL)
|  | Bit 1: | = 1: Drive braking [In braking] (brS)
|  | Bit 2: | = 1: The "Power removal" function is active
|  | Bit 3: | = 1: Automatic restart attempts in progress: [Auto restart] (AUtO)
|  | Bit 4: | = 1: "Auto-tuning" in progress: [Auto-tuning] (tUn)
|  | Bit 5: | = 1: Controlled stop in progress following loss of power section line supply (CTL)
|  | Bit 6: | = 1: The drive cannot follow the configured deceleration ramp, deceleration automatically adapted (OBR)
|  | Bit 7: | = 1: Controlled output cut in progress (SOC)
|  | Bit 8: | = 1: [Freq. meter Alarm] (FqLA): Measured speed threshold reached: [Pulse warning thd.] (FqL).
|  | Bit 9: | = 1: The line contactor is active
|  | Bit 10: | = 1: Autotune complete (TUD)
|  | Bit 11: | Reserved (= 0 or 1)
|  | Bit 12: | Reserved (= 0 or 1)
|  | Bit 13: | = 1: Current present in the motor (MCP)
|  | Bit 14: | = 1: If the "limit switch management" [LIMIT SWITCHES] function is activated. The [Stop FW limit sw.] or [Stop RV limit sw.] stops are reached.
|  | Bit 15: | = 1: [Dynamic load alarm] (dLdA): Detection dynamic load alarm (see [DYNAMIC LOAD DETECT.] (dLd-)).
LRS6 |  | Bit 0: | = 1: Alarm group 1 is active
|  | Bit 1: | = 1: Alarm group 2 is active
|  | Bit 2: | = 1: Alarm group 3 is active
|  | Bit 3: | Reserved (= 0)
|  | Bit 4: | Reserved (= 0)
|  | Bit 5: | = 1: LI6 PTC probe alarm: [LI6 =PTC alarm] (PtC3)
|  | Bit 6: | Reserved (= 0)
|  | Bit 7: | = 1: External fault [External fault alarm] (EtF)
|  | Bit 8: | = 1: Undervoltage alarm [Undervoltage] (USA)
|  | Bit 9: | = 1: Undervoltage prevention Alarm
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | = 1: Drive overheat alarm (tHA)
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | Reserved (= 0)
|  | Bit 15: | = 1: Current or torque limit alarm after time-out [Trq/I limit. time out] (StO)
LRS7 |  | Bit 0: | = 1: Reference channel 1 or 1B (Fr1) or (Fr1b) is active
|  | Bit 1: | = 1: Reference channel 2 (Fr2) is active
|  | Bit 2: | = 1: Command channel 1 (Cd1) is active
|  | Bit 3: | = 1: Command channel 2 (Cd2) is active
|  | Bit 4: | = 1: Reference channel 1B (Fr1b) is active
|  | Bit 5: | = 1: Spool end ("traverse control" function)
|  | Bit 6: | = 1: Master-slave synchronization ("traverse control" function)
|  | Bit 7: | Reserved (= 0)
|  | Bit 8: | = 1: IGBT thermal state alarm
|  | Bit 9: | Reserved (= 0)
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | = 1: 4-20 mA alarm on analog input AI3: [AI3 4-20 mA loss] (LFF3)
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | Reserved (= 0)
|  | Bit 15: | Reserved (= 0)
LRS8 |  | Bit 0: | Reserved (= 0)
|  | Bit 1: | Reserved (= 0)
|  | Bit 2: | Reserved (= 0)
|  | Bit 3: | Reserved (= 0)
|  | Bit 4: | Reserved (= 0)
|  | Bit 5: | Reserved (= 0)
|  | Bit 6: | Reserved (= 0)
|  | Bit 7: | Reserved (= 0)
|  | Bit 8: | Reserved (= 0)
|  | Bit 9: | = 1: force local mode activated (FLO)
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | Reserved (= 0)
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | Reserved (= 0)
|  | Bit 15: | = 1: Drive ready(rdY)
OL1R |  | Bit 0: | Value of R1.
|  | Bit 1: | Value of R2.
|  | Bit 2: | Reserved (= 0).
|  | Bit 3: | Reserved (= 0).
|  | Bit 4: | Reserved (= 0).
|  | Bit 5: | Reserved (= 0).
|  | Bit 6: | Reserved (= 0).
|  | Bit 7: | Reserved (= 0).
|  | Bit 8: | Value of LO1.
|  | Bit 9: | Reserved (= 0).
|  | Bit 10: | Reserved (= 0).
|  | Bit 11: | Reserved (= 0).
|  | Bit 12: | Reserved (= 0).
|  | Bit 13: | Reserved (= 0).
|  | Bit 14: | Reserved (= 0).
|  | Bit 15: | Reserved (= 0).
The outputs (relays or logic ouputs) can be controlled by the network. The outputs to control should not be assigned to a function of the drive, otherwise the writing is without effect.
S001 |  | Bit 0: | Reserved (= 0)
|  | Bit 1: | Reserved (= 0)
|  | Bit 2: | Reserved (= 0)
|  | Bit 3: | Reserved (= 0)
|  | Bit 4: | Reserved (= 0)
|  | Bit 5: | = 1: period 100ms, duty cycle 50%
|  | Bit 6: | = 1: period 1s, duty cycle 50%
|  | Bit 7: | = 1: period 1min, duty cycle 50%
|  | Bit 8: | Reserved (= 0)
|  | Bit 9: | Reserved (= 0)
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | Reserved (= 0)
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | = 1: FB is executing its 1rst cycle since last RUN.
|  | Bit 14: | Reserved (= 0)
|  | Bit 15: | Reserved (= 0)
S002 |  | Bit 0: | Reserved (= 0)
|  | Bit 1: | Reserved (= 0)
|  | Bit 2: | Reserved (= 0)
|  | Bit 3: | Reserved (= 0)
|  | Bit 4: | Reserved (= 0)
|  | Bit 5: | Reserved (= 0)
|  | Bit 6: | Reserved (= 0)
|  | Bit 7: | Reserved (= 0)
|  | Bit 8: | Reserved (= 0)
|  | Bit 9: | Reserved (= 0)
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | = 1: Option Ok
|  | Bit 12: | = 1: CANopen Ok
|  | Bit 13: | = 1: Modbus Ok
|  | Bit 14: | Reserved (= 0)
|  | Bit 15: | Reserved (= 0)
S006 |  | Bit 0: | Reserved (= 0)
|  | Bit 1: | Reserved (= 0)
|  | Bit 2: | Reserved (= 0)
|  | Bit 3: | Reserved (= 0)
|  | Bit 4: | Reserved (= 0)
|  | Bit 5: | Reserved (= 0)
|  | Bit 6: | Reserved (= 0)
|  | Bit 7: | Reserved (= 0)
|  | Bit 8: | Reserved (= 0)
|  | Bit 9: | Reserved (= 0)
|  | Bit 10: | Reserved (= 0)
|  | Bit 11: | Reserved (= 0)
|  | Bit 12: | Reserved (= 0)
|  | Bit 13: | Reserved (= 0)
|  | Bit 14: | = 1: Users variable save request (Save configuration)
|  | Bit 15: | Reserved (= 0)