# General Specification for Universal Enclosures

Stainless Steel AISI304L enclosures for multiple purposes from Low Voltage switchgear panels to automation and control installations.

Dimensions (Height x Width x Depth): From 300x200x150 to 1200x1000x300

Table of contents:

1	General Terms	2

2	Compliance with the standards	2

3	Specific requirements	2

3.1 Body :	3

3.2 Doors:	3

3.3 Mounting plate:	3

3.4 Accessories:	3

4	Operation & Maintenance	3

4.1 Quality Assurance	3

4.2 Product delivery, storage and handling	3

5	Sustainable development	3

# General Terms

Enclosures particularly intended for industrial sectors where cleanliness, hygiene and resistance to corrosion are of paramount importance, such as in the chemical, Oil & Gas, food and beverage, agriculture, pharmaceutics, industries, etc.

Stainless Steel AISI 304L with brushed polishing (a.k.a. Scotch-brite ® finish) used for its capacity against corrosion and its easy cleaning. It offers a good prevention against corrosion (intercrystalline, galvanic and granular) especially in presence of organic acids (acetic and vinyl).

Thanks to a composition containing:

> A minimum % of carbon in order to avoid corrosion.

> A high level of nickel and chromium blend.

Type of stainless steel Chemical composition (%)

| AISI grade | N. Europe | Carbon | Chromium | Nickel | Molybdenum |
| --- | --- | --- | --- | --- | --- |
| 304L | 1.4307 | < 0.03 | 17-19 | 8-10 | 0 |
| 316L | 1.4404 | < 0.03 | 17-19 | 10-13 | 2-2.25 |

Certification according IEC62208 should be issued by an Official body (as Bureau Veritas or other).

Product is UL certified, look for the marking on the inside of the enclosure.

# Compliance with the standards

| Standard | Title | Use |
| --- | --- | --- |
| IEC62208 | Empty enclosures for low-voltage switchgear and controlgear assemblies | - Test 9.2 : Marking compliance - Test 9.3 : Static Loads resistance maximum admissible load in plate: 250Kgs/m2, maximum admissible load on door: 50 Kgs/m2) - Test 9.10: Continuity of the circuit protection < 0,1 Ohms - Test 9.12: Verification of resistance to corrosion: Outer cycle. |
| IEC60529 | Degrees of protection provided by enclosures (IP code) | Degree of protection against liquids and dust to enter the enclosure. - IP 66 for single door enclosures - IP55 for double door |
| IEC62262 | Degrees of protection provided by enclosures for electrical equipment against external mechanical impacts (IK code) | Degree of protection from solid bodies to enter the enclosure. - IK10 For plain door - IK08 for glass door |
| UL508A | Standard for Industrial control panels | NEMA Types: - 1, 2, 3, 3R, 4, 4X, 5, 12 and 13 for single door - 1, 2, 12K for double door enclosures |

# Specific requirements

Robust construction made from stainless steel sheet quality 304L, manufactured as a cross folded and welded structure from a continuous length of sheet with back welded frame. Enclosure made of Stainless Steel 304L with Scotch-brite ® polish and lesser roughness (Ra) than 0’8 µm. Enclosure with welded studs on both body and door for earthing connection.

## Body :

Double folding as a front rain gutter railing. Rear panel with shouldered studs with built-in spacers for fixing mounting plates. Rear panel drillings covered with plastic plugs for wall fixing.

## Doors:

Stainless steel door with punched corners, flush-mounted, with foamed-in polyurethane gasket. ( that assures the highest degree of protection for a longer time than stuck gasket.) Mounting strips fitted on both sides, screw-fastened hinges. Left or right opening to a minimum of 120º. Door reinforcement frame for enclosures from 1000 mm hight, with holes every 25 mm to assemble accesories. Standard door closure by 3 mm double bar key (chrome-plated ZAMAC).

The enclosure can be supplied with a glazed door with security glass 4mm thick when required.

## Mounting plate:

Able to be equipped with all the type of plates: plain metal, perforated, rectangular “telequick“ perforated, or insulating material (glass-reinforced polyester or bakelite) and eventually with depth adjustable support.

## Accessories:

Lock inserts, wall fixing brackets can be installed from the outside for easy installation, earthing straps, wiring plan/documents pocket, viewing window, distribution chassis, panels, thermal control devices, swing frame, internal door, DIN rails.

# Operation & Maintenance

## Quality Assurance

All materials and products shall be new, sound and uniform in quality, size, shape, color and texture.

The assembler shall be responsible for ensuring that the required standards of quality control as mentioned in relative sections are maintained for the proposed enclosures.

If requested by the client, the supplier shall provide proof of application of a quality procedure complying with standards. This means:

- Use of a quality manual approved and signed by a management representative.

- regular updating of this manual so that it reflects the most recent applicable quality control procedures,

- ISO 9001 or ISO 14001 certification

## Product delivery, storage and handling

- Deliver, store, protect and handle products to site as per manufacturer’s instructions.

- Store enclosures in clean and dry space. Inspect for exterior damage. Maintain factory wrapping or provide an additional heavy canvas or heavy plastic cover to protect units from dirt, water, construction debris and traffic.

- Lift only with lugs provided for the purpose. Handle carefully to avoid damage to enclosure and finish.

# Sustainable development

- Production site organisation shall be non polluting and certified to comply with ISO 9001 and ISO 14001 standards.

- Enclosures shall be designed according to Eco-design and the materials shall be of halogen free type.

- Enclosure painting process shall be complying with environmental directives RoHS.

- Packaging ecological and re-usable as a must.