## Register List
Category | Sub Cat 1 | Sub Cat 2 | Description | PM5110_11 | PM5310 | PM5330_31 | PM5320 | PM5340_41 | Register | Units | Size (INT16) | Data Type | Access | Range | Default | User Notes
System Setup & Status |  |  |  | Y | Y | Y | Y | Y | 1 | --- |  | --- | --- | --- | ---
| Product & Features |  |  | Y | Y | Y | Y | Y | 30 | --- |  | --- | --- | --- | ---
|  |  | Meter Name | Y | Y | Y | Y | Y | 30 | --- | 20 | UTF8 | RWC | --- | PM5xxx = "Power Meter"
|  |  | Meter Model | Y | Y | Y | Y | Y | 50 | --- | 20 | UTF8 | RWC | --- | PM5110 = "PM5110" PM5111 = "PM5111" PM5310 = "PM5310" PM5330 = "PM5330" PM5331 = "PM5331" PM5320 = "PM5320" PM5340 = "PM5340" PM5341 = "PM5341" PM5100 = "PM5100"
|  |  | Manufacturer | Y | Y | Y | Y | Y | 70 | --- | 20 | UTF8 | RWC | --- | "Schneider Electric"
|  |  | Product ID Number | Y | Y | Y | Y | Y | 90 | --- | 1 | INT16U | RWC |  | PM5110 = 15270 PM5111 = 15271 PM5310 = 15272 PM5330 = 15273 PM5331 = 15274 PM5320 = 15275 PM5340 = 15276 PM5341 = 15277 PM5100 = 15278
|  |  | Hardware Detected | Y | Y | Y | Y | Y | 91 | --- | 4 | BITMAP | R | 0x0000 – 0xFFFF | PM5110 = 0x001B PM5111 = 0x001B PM5310 = 0x001B PM5330 = 0x001B PM5331 = 0x001B PM5320 = 0x001D PM5340 = 0x001D PM5341 = 0x001D | Bitmap indicating base hardware options detected Bit 01 = HMI Bit 02 = Modbus Serial Communications Port Bit 03 = Modbus Ethernet Communications Port Bit 04 = Digital Inputs Bit 05 = Digital Outputs Bit 06-16 Not Used
|  |  | Supported Features | Y | Y | Y | Y | Y | 95 | --- | 4 | BITMAP | R | 0x0000 – 0xFFFF PM5110 = 0x161D PM5111 = 0x161D PM5310 = 0x169D PM5330 = 0x169D PM5331 = 0x169D PM5320 = 0x169D PM5340 = 0x169D PM5341 = 0x169D | 0 | Bitmap indicating features supported Bit 01 = 1 Cycle Metering Bit 02 = 5/6 Cycle Metering Bit 03 = 50/60 Cycle Metering Bit 04 = Min/Max Bit 05 = Accumulated Energy Bit 06 = Conditional Energy Bit 07 = Time-of-Use Energy Bit 08 = Multi-tarrif Energy Bit 09 = Input Metering Bit 10 = Demand Bit 11 = Alarms Bit 12 = Waveform Capture Bit 13 = Datalogging Bit 14 = Not Used Bit 15 = Not Used Bit 16 = Not Used
| Manufacturing Data |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Meter |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Manufacturing Unit Id (To be prefixed in Serial Number While Displaying) | Y | Y | Y | Y | Y | 129 |  | 1 | INT16U | R | --- | 0
|  |  | Serial Number | Y | Y | Y | Y | Y | 130 | --- | 2 | INT32U | R |  | 0
|  |  | Date of Manufacture | Y | Y | Y | Y | Y | 132 | --- | 4 | DATETIME | R | --- | 0
|  |  | Hardware Revision | Y | Y | Y | Y | Y | 136 | --- | 5 | UTF8 | R | --- | 0
|  |  | Production History 01 | Y | Y | Y | Y | Y | 141 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 02 | Y | Y | Y | Y | Y | 142 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 03 | Y | Y | Y | Y | Y | 143 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 04 | Y | Y | Y | Y | Y | 144 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 05 | Y | Y | Y | Y | Y | 145 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 06 | Y | Y | Y | Y | Y | 146 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 07 | Y | Y | Y | Y | Y | 147 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 08 | Y | Y | Y | Y | Y | 148 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 09 | Y | Y | Y | Y | Y | 149 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 10 | Y | Y | Y | Y | Y | 150 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 11 | Y | Y | Y | Y | Y | 151 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 12 | Y | Y | Y | Y | Y | 152 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 13 | Y | Y | Y | Y | Y | 153 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 14 | Y | Y | Y | Y | Y | 154 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 15 | Y | Y | Y | Y | Y | 155 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 16 | Y | Y | Y | Y | Y | 156 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 17 | Y | Y | Y | Y | Y | 157 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 18 | Y | Y | Y | Y | Y | 158 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 19 | Y | Y | Y | Y | Y | 159 | --- | 1 | INT16U | R | --- | 0
|  |  | Production History 20 | Y | Y | Y | Y | Y | 160 | --- | 1 | INT16U | R | --- | 0
|  |  | Checksum | Y | Y | Y | Y | Y | 161 | --- | 1 | INT16U | R | --- | 0
| Firmware Versions |  |  | Y | Y | Y | Y | Y | 1637 | --- |  | --- | --- | --- | ---
|  | Operating System |  | Y | Y | Y | Y | Y | 1637 | --- |  | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | 1637 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | Y | Y | Y | Y | 1638 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | 1639 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | 1640 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | 1641 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Previous Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | 1642 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | Y | Y | Y | Y | 1643 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | 1644 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | 1645 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | 1646 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Date/Time of Last Firmware Download | Y | Y | Y | Y | Y | 1647 | --- | 4 | DATETIME | R | --- | N/A
|  | Language |  | Y | Y | Y | Y | Y | 1701 | --- |  | --- | --- | --- | ---
|  |  | Present Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | 1701 | --- | 1 | INT16U | R | 0 – 32,767 | 0 | The firmware version takes the following form: XXYYT
|  |  | X – Major | Y | Y | Y | Y | Y | 1702 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | 1703 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | 1704 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | 1705 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Previous Firmware Version (DLF Format) X.Y.T | Y | Y | Y | Y | Y | 1706 | --- | 1 | INT16U | R | 0 – 32,767 | 0
|  |  | X – Major | Y | Y | Y | Y | Y | 1707 | --- | 1 | INT16U | R | 00 – 99 | 0
|  |  | Y – Minor | Y | Y | Y | Y | Y | 1708 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Z – Quality | Y | Y | Y | Y | Y | 1709 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | T – Internal evolutions | Y | Y | Y | Y | Y | 1710 | --- | 1 | INT16U | R | 0000 – 9999 | 0
|  |  | Date/Time of Last Firmware Download | Y | Y | Y | Y | Y | 1711 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Checksum | Y | Y | Y | Y | Y | 1715 | --- | 1 | INT16U | R | --- | 0
|  |  | Bridge Code Version | Y | Y | Y | Y | Y | 1716 | --- | 1 | INT16U | R | --- | 0
| Firmware Download Log |  |  | Y | Y | Y | Y | Y | 1751 | --- |  | --- | --- | --- | ---
|  |  | Date/Time of Firmware Download 01 | Y | Y | Y | Y | Y | 1751 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 01 | Y | Y | Y | Y | Y | 1755 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 01 | Y | Y | Y | Y | Y | 1756 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 01 | Y | Y | Y | Y | Y | 1757 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 02 | Y | Y | Y | Y | Y | 1758 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 02 | Y | Y | Y | Y | Y | 1762 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 02 | Y | Y | Y | Y | Y | 1763 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 02 | Y | Y | Y | Y | Y | 1764 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 03 | Y | Y | Y | Y | Y | 1765 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 03 | Y | Y | Y | Y | Y | 1769 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 03 | Y | Y | Y | Y | Y | 1770 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 03 | Y | Y | Y | Y | Y | 1771 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 04 | Y | Y | Y | Y | Y | 1772 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 04 | Y | Y | Y | Y | Y | 1776 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 04 | Y | Y | Y | Y | Y | 1777 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 04 | Y | Y | Y | Y | Y | 1778 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 05 | Y | Y | Y | Y | Y | 1779 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 05 | Y | Y | Y | Y | Y | 1783 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 05 | Y | Y | Y | Y | Y | 1784 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 05 | Y | Y | Y | Y | Y | 1785 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 06 | Y | Y | Y | Y | Y | 1786 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 06 | Y | Y | Y | Y | Y | 1790 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 06 | Y | Y | Y | Y | Y | 1791 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 06 | Y | Y | Y | Y | Y | 1792 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 07 | Y | Y | Y | Y | Y | 1793 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 07 | Y | Y | Y | Y | Y | 1797 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 07 | Y | Y | Y | Y | Y | 1798 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 07 | Y | Y | Y | Y | Y | 1799 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 08 | Y | Y | Y | Y | Y | 1800 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 08 | Y | Y | Y | Y | Y | 1804 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 08 | Y | Y | Y | Y | Y | 1805 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 08 | Y | Y | Y | Y | Y | 1806 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 09 | Y | Y | Y | Y | Y | 1807 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 09 | Y | Y | Y | Y | Y | 1811 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 09 | Y | Y | Y | Y | Y | 1812 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 09 | Y | Y | Y | Y | Y | 1813 | --- | 1 | INT16U | R |  | 0
|  |  | Date/Time of Firmware Download 10 | Y | Y | Y | Y | Y | 1814 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Firmware Version 10 | Y | Y | Y | Y | Y | 1818 | --- | 1 | INT16U | R |  | 0
|  |  | Communications Channel 10 | Y | Y | Y | Y | Y | 1819 | --- | 1 | INT16U | R |  | 0
|  |  | Status of Download 10 | Y | Y | Y | Y | Y | 1820 | --- | 1 | INT16U | R |  | 0
|  |  | Dwonload Log Counter | Y | Y | Y | Y | Y | 1821 | --- | 1 | INT16U | R
| Meter Resets |  |  | Y | Y | Y | Y | Y | 1822 | --- |  | --- | --- | --- | ---
|  |  | Last Unit Restart DateTime | Y | Y | Y | Y | Y | 1824 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Number of Metering System Restarts | Y | Y | Y | Y | Y | 1828 | --- | 1 | INT16U | R | --- | 0
|  |  | Number of Control Power Failures | Y | Y | Y | Y | Y | 1829 | --- | 1 | INT16U | R | --- | 0
|  |  | Date/Time of Last Control Power Failure | Y | Y | Y | Y | Y | 1830 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Duration of Last Control Power Failure | Y | Y | Y | Y | Y | 1834 | seconds | 2 | INT32U | R | --- | 0
|  |  | Cause of Last Meter Reset | Y | Y | Y | Y | Y | 1836 | --- | 1 | INT16U | R | 0 – 2 | 0 | 0 = Unknown 1 = Reset command 2 = Power failure
| Timekeeping |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Present Date & Time (7 register format) |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Year | Y | Y | Y | Y | Y | 1837 | year | 1 | INT16U | R | 2000 – 2127 | 2000
|  |  | Month | Y | Y | Y | Y | Y | 1838 | month | 1 | INT16U | R | 1 – 12 | 1
|  |  | Day | Y | Y | Y | Y | Y | 1839 | days | 1 | INT16U | R | 1 – 31 | 1
|  |  | Hour | Y | Y | Y | Y | Y | 1840 | hours | 1 | INT16U | R | 0 – 23 | 0
|  |  | Minute | Y | Y | Y | Y | Y | 1841 | minutes | 1 | INT16U | R | 0 – 59 | 0
|  |  | Second | Y | Y | Y | Y | Y | 1842 | seconds | 1 | INT16U | R | 0 – 59 | 0
|  |  | Millisecond | Y | Y | Y | Y | Y | 1843 | msec | 1 | INT16U | R | 0 – 999 | 0
|  |  | Day of Week | [5 empty] | 1844 | --- | 1 | INT16U | R | 1 – 7 | N/A | 1 = Sunday, 2 = Monday, etc.
|  | Present Date & Time (4 register format) |  | Y | Y | Y | Y | Y | 1845 | --- |  | --- | --- | --- | ---
|  |  | Year | Y | Y | Y | Y | Y | 1845 | --- | 1 | INT16U | R | 0 – 127 | 0
|  |  | Month & Day | Y | Y | Y | Y | Y | 1846 | --- | 1 | INT16U | R | 1 – 12, 1 – 31 | 0
|  |  | Hour & Minute | Y | Y | Y | Y | Y | 1847 | --- | 1 | INT16U | R | 0 – 23, 0 – 59 | 0
|  |  | Milliseconds | Y | Y | Y | Y | Y | 1848 | --- | 1 | INT16U | R | 0 – 59,999 | 0
| Security |  |  | Y | Y | Y | Y | Y | 1880 | --- |  | --- | --- | --- | ---
|  | Passwords |  | Y | Y | Y | Y | Y | 1880 | --- |  | --- | --- | --- | ---
|  |  | Setup Password | Y | Y | Y | Y | Y | 1880 | --- | 4 | UTF8 | WC | --- | "0000"
|  |  | Energy Reset Password | Y | Y | Y | Y | Y | 1884 | --- | 4 | UTF8 | WC | --- | "0000"
|  |  | Demand Reset Password | Y | Y | Y | Y | Y | 1888 | --- | 4 | UTF8 | WC | --- | "0000"
|  |  | Min/Max Reset Password | Y | Y | Y | Y | Y | 1892 | --- | 4 | UTF8 | WC | --- | "0000"
|  | Revenue Security | [7 empty] | --- |  | --- | --- | --- | ---
|  |  | Revenue Security Status | Y | Y | Y | Y | Y | 1921 | --- | 1 | INT16U | R | 0 – 1 | 0 | 0 = inactive, 1 = active
Meter Setup & Status |  |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
| Miscellaneous Control & Status |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Active Load Timer | Y | Y | Y | Y | Y | 2002 | seconds | 2 | INT32U | R | --- | 0 | Increments when average current exceeds the Active Load Timer Setpoint.
|  |  | Meter Operation Timer | Y | Y | Y | Y | Y | 2004 | seconds | 2 | INT32U | R | --- | 0
|  |  | Cycle Count | Y | Y | Y | Y | Y | 2006 | --- | 2 | INT32U | R | --- | 0
| Metering Setup |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Power System |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Number of Phases | Y | Y | Y | Y | Y | 2014 | --- | 1 | INT16U | RWC | 1 or 3 | 3 | Must match Power System Configuration Enumeration
|  |  | Number of Wires | Y | Y | Y | Y | Y | 2015 | --- | 1 | INT16U | RWC | 2 – 4 | 4 | Must match Power System Configuration Enumeration
|  |  | Power System Configuration | Y | Y | Y | Y | Y | 2016 | --- | 1 | INT16U | RWC | 0 – 13 PM5350: 0 - 12 | 11 | 0 = 1ph, 2w, LN 1 = 1ph, 2w, LL 2 = 1ph, 3w, LL with N ( 2phase) 3 = 3ph, 3w, Delta, Ungrounded 4 = 3ph, 3w, Delta, Corner Grounded 5 = 3ph, 3w, Wye, Ungrounded 6 = 3ph, 3w, Wye Grounded 7 = 3ph, 3w, Wye, Resistance Grounded 8 = 3ph, 4w, Open Delta, Center-Tapped 9 = 3ph, 4w, Delta, Center-Tapped 10 = 3ph, 4w, Wye, Ungrounded 11 = 3ph, 4w, Wye Grounded 12 = 3ph, 4w, Wye, Resistance Grounded 13 = Multi-Circuit 3 circuit LN 14 = Multi-Circuit 2 Circuit LN ( Not used ) 15 = Multi-Circuit 1 Cicuit LN ( Not used ) 16 = Multi-Circuit 3 Circuit LL ( Not used ) 17 = Multi-Circuit 2 Circuit LL ( Not used ) 18 = Multi-Circuit 1 Circuit LL ( Not used ) 19 = Multi-Circuit 1 Circuit LL 1 Circuit LN ( Not used ) 20 = Multi-Circuit Wye
|  |  | Nominal Frequency | Y | Y | Y | Y | Y | 2017 | Hz | 1 | INT16U | RWC | 50, 60, 400 PM5350: 50, 60 Ashoka and Akbar: 50, 60 | 50 | PM5350 does not support 400Hz Ashoka: EM32xx does not support 400Hz Akbar: PM5xxx does not support 400Hz
|  |  | Nominal Voltage | Y | Y | Y | Y | Y | 2018 | V | 2 | FLOAT32 | RWC | 230 | 230
|  |  | Nominal Current | Y | Y | Y | Y | Y | 2020 | A | 2 | FLOAT32 | RWC | 5 | 5
|  |  | Nominal Power Factor | Y | Y | Y | Y | Y | 2022 | --- | 2 |  | RWC | 0.8 | 0.8
|  |  | Normal Phase Rotation | Y | Y | Y | Y | Y | 2024 | --- | 1 | INT16U | RWC | 0 – 1 | 0
|  | Instrument Transformers |  | Y | Y | Y | Y | Y | 2025 | --- |  | --- | --- | --- | ---
|  |  | Number VTs | Y | Y | Y | Y | Y | 2025 | --- | 1 | INT16U | RWC | Depends on Power System | 0
|  |  | VT Primary | Y | Y | Y | Y | Y | 2026 | V | 2 | FLOAT32 | RWC | 100 - 999000 | 120
|  |  | VT Secondary | Y | Y | Y | Y | Y | 2028 | V | 1 | INT16U | RWC | 100, 110, 115, 120 | 120
|  |  | Number CTs | Y | Y | Y | Y | Y | 2029 | --- | 1 | INT16U | RWC | Depends on Power System | 0
|  |  | CT Primary | Y | Y | Y | Y | Y | 2030 | A | 1 | INT16U | RWC | 1 – 32,767 | 5
|  |  | CT Secondary | Y | Y | Y | Y | Y | 2031 | A | 1 | INT16U | RWC | 1 , 5 | 5
|  |  | CT Location for 1 or 2 CT Metering | Y | Y | Y | Y | Y | 2034 | --- | 1 | INT16U | RWC | 1 – 3 | 1 | If 1 CT, value is meter terminal connected If 2 CT, value is meter terminal not connected 1 = Phase A, 2 = Phase B, 3 = Phase C
|  |  | VT Location for 1 or 2 VT Metering | Y | Y | Y | Y | Y | 2035 | --- | 1 | INT16U | RWC | 1 – 3 | 1 | Must match CT Location
|  |  | VT Connection Type | Y | Y | Y | Y | Y | 2036 | --- | 1 | INT16U | RWC | 0 –4 | 0 | 0 = Direct Connect 1 = Delta (2 VT) 2 = Wye (3 VT) 3 = L-N (1 VT) 4 = L-L (1 VT) 5 = L-L W/N (2 VT)
|  | Operating Modes |  | Y | Y | Y | Y | Y | 2046 | --- |  | --- | --- | --- | ---
|  |  | Peak Current Demand Over Last Year | Y | Y | Y | Y | Y | 2048 | A | 2 | FLOAT32 | RWC |  | 0 | Entered by the user for use in calculation of Total Demand Distortion. 0 = Calculation performed using peak demand of 3-phase average current.
|  |  | Active Load Timer Setpoint | Y | Y | Y | Y | Y | 2050 | A | 2 | FLOAT32 | RWC | 0 – (10 * CT Ratio) | 5
|  |  | Reserved | [5 empty] | 2052 | --- | 54 | INT16U | R |  | N/A
| Energy Pulse Output Setup |  |  | Y | Y | Y | Y | Y | 2126 | --- |  | --- | --- | --- | ---
|  | Alarm / Energy LED Mode | Alarm / Energy LED Mode | Y | Y | Y | Y | Y | 2126 | --- | 1 | INT16U | RWC | 0 – 2 | 1 | 0 = Disable, 1 = Active Alarm (default), 2 = Energy
|  | Energy Pulse Output Channel 01 |  | Y | Y | Y | Y | Y | 2130 | --- |  | --- | --- | --- | ---
|  |  | Energy Channel | Y | Y | Y | Y | Y | 2130 | --- | 1 | INT16U | RWC | 0 – 18 PM5350: 0 - 9 | 0 | 0 = Not Used 1 = Active Energy Delivered (Into Load) 2 = Active Energy Received (Out of Load) 3 = Active Energy Delivered + Received 4 = Reactive Energy Delivered 5 = Reactive Energy Received 6 = Reactive Energy Delivered + Received 7 = Apparent Energy Delivered 8 = Apparent Energy Received 9 = Apparent Energy Delivered + Received 10 = Active Energy Delivered Phase A 11 = Active Energy Delivered Phase B 12 = Active Energy Delivered Phase C 13 = Reactive Energy Delivered Phase A 14 = Reactive Energy Delivered Phase B 15 = Reactive Energy Delivered Phase C 16 = Apparent Energy Delivered Phase A 17 = Apparent Energy Delivered Phase B 18 = Apparent Energy Delivered Phase C
|  |  | Digital Output Association | Y | Y | Y | Y | Y | 2131 | --- | 1 | INT16U | RWC | 0 – 99 | 0 | 0 = No association 1 - 2 = Digital Output 99 = LED A digital output shall be permitted to be associated with only 1 energy value. If the Energy Channel is not 0, a valid digital output association must be made. In PM5110/11 references, 1 = Digital output and 99 = LED available
|  |  | Pulse Weight | Y | Y | Y | Y | Y | 2132 | kWh, kVAh, kVAh | 2 | UINT32 | RWC | 1E-10 – 1E10 | 0 | If the Energy Channel is not 0, a non-zero pulse weight must be entered.
|  | Energy Pulse Output Channel 02 |  | Y | Y | Y | Y | Y | 2134 | --- |  | --- | --- | --- | --- | See Energy Pulse Output Channel 01
|  |  | Energy Channel | Y | Y | Y | Y | Y | 2134 | --- | 1 | INT16U | RWC | 0 – 18 | 0
|  |  | Digital Output Association | Y | Y | Y | Y | Y | 2135 | --- | 1 | INT16U | RWC | 0 – 99 | 0
|  |  | Pulse Weight | Y | Y | Y | Y | Y | 2136 | kWh, kVAh, kVAh | 2 | UINT32 | RWC | 1E-10 – 1E10 | 0
|  | Energy Pulse Output Channel 03 |  |  | Y | Y | Y | Y | 2138 | --- |  | --- | --- | --- | --- | See Energy Pulse Output Channel 01
|  |  | Energy Channel |  | Y | Y | Y | Y | 2138 | --- | 1 | INT16U | RWC | 0 – 18 | 0
|  |  | Digital Output Association |  | Y | Y | Y | Y | 2139 | --- | 1 | INT16U | RWC | 0 – 99 | 0
|  |  | Pulse Weight |  | Y | Y | Y | Y | 2140 | kWh, kVAh, kVAh | 2 | UINT32 | RWC | 1E-10 – 1E10 | 0
Bitmapped Status Holding Registers |  |  |  | Y | Y | Y | Y | Y
| Digital Input Status Holding Registers |  |  | Y | Y | Y | Y | Y
|  | On/Off Status |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Digital Input Status Validity - Base Unit | Y | Y | Y | Y | Y | 2400 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000
|  |  | Digital Input Status - Base Unit | Y | Y | Y | Y | Y | 2401 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000
| Digital Output Status Holding Registers |  |  | Y | Y | Y | Y | Y
|  | On/Off Status |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Digital Output Status Validity - Base Unit | Y | Y | Y | Y | Y | 2402 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000
|  |  | Digital Output Status - Base Unit | Y | Y | Y | Y | Y | 2403 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000
| Detected Alarm Status Bitmap Holding Registers |  |  | Y | Y | Y | Y | Y
|  | Standard Alarms |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Standard - 1 second Group 1 Validity | Y | Y | Y | Y | Y | 2420 | --- | 1 | BITMAP | R |  | 0 | See PTI document for definition
|  |  | Standard - 1 second Group 1 | Y | Y | Y | Y | Y | 2421 | --- | 1 | BITMAP | R |  | 0 | 0 = Not Detected; 1 = Detected
|  |  | Standard - 1 second Group 2 Validity | Y | Y | Y | Y | Y | 2422 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard - 1 second Group 2 | Y | Y | Y | Y | Y | 2423 | --- | 1 | BITMAP | R |  | 0
|  | Unary Alarms |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Unary Validity | Y | Y | Y | Y | Y | 2440 | --- | 1 | BITMAP | R |  | 0
|  |  | Unary | Y | Y | Y | Y | Y | 2441 | --- | 1 | BITMAP | R |  | 0
|  | Digital Alarms |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Digital Group 1 Validity | Y | Y | Y | Y | Y | 2442 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital Group 1 | Y | Y | Y | Y | Y | 2443 | --- | 1 | BITMAP | R |  | 0
Meter Data (Basic) |  |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
| Energy - 32 bit floating point values |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Accumulated Energy - 32 bit floating point values |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Active Energy Delivered (Into Load) | Y | Y | Y | Y | Y | 2700 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Received (Out of Load) | Y | Y | Y | Y | Y | 2702 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Delivered + Received | Y | Y | Y | Y | Y | 2704 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Delivered- Received | Y | Y | Y | Y | Y | 2706 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Delivered | Y | Y | Y | Y | Y | 2708 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Received | Y | Y | Y | Y | Y | 2710 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Delivered + Received | Y | Y | Y | Y | Y | 2712 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Delivered - Received | Y | Y | Y | Y | Y | 2714 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Delivered | Y | Y | Y | Y | Y | 2716 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Received | Y | Y | Y | Y | Y | 2718 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Delivered + Received | Y | Y | Y | Y | Y | 2720 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Delivered - Received | Y | Y | Y | Y | Y | 2722 | kVAh | 2 | FLOAT32 | R | --- | 0
| 1s Metering (50/60 Cycles) |  |  | Y | Y | Y | Y | Y | 3000 | --- |  | --- | --- | --- | ---
|  | Current |  | Y | Y | Y | Y | Y | 3000 | --- |  | --- | --- | --- | ---
|  |  | Current A | Y | Y | Y | Y | Y | 3000 | A | 2 | FLOAT32 | R
|  |  | Current B | Y | Y | Y | Y | Y | 3002 | A | 2 | FLOAT32 | R
|  |  | Current C | Y | Y | Y | Y | Y | 3004 | A | 2 | FLOAT32 | R
|  |  | Current N | Y | Y | Y | Y | Y | 3006 | A | 2 | FLOAT32 | R |  |  | Reportable only in systems where there is a N current and when all wired phase currents are metered
|  |  | Current G | Y | Y | Y | Y | Y | 3008 | A | 2 | FLOAT32 | R |  |  | Reportable only in systems where there is not a N current and when all wired phase currents are metered
|  |  | Current Avg | Y | Y | Y | Y | Y | 3010 | A | 2 | FLOAT32 | R
|  | Current Unbalance |  | Y | Y | Y | Y | Y | 3012 | --- |  | --- | --- | --- | ---
|  |  | Current Unbalance A | Y | Y | Y | Y | Y | 3012 | % | 2 | FLOAT32 | R
|  |  | Current Unbalance B | Y | Y | Y | Y | Y | 3014 | % | 2 | FLOAT32 | R
|  |  | Current Unbalance C | Y | Y | Y | Y | Y | 3016 | % | 2 | FLOAT32 | R
|  |  | Current Unbalance Worst | Y | Y | Y | Y | Y | 3018 | % | 2 | FLOAT32 | R
|  | Voltage |  | Y | Y | Y | Y | Y | 3020 | --- |  | --- | --- | --- | ---
|  |  | Voltage A-B | Y | Y | Y | Y | Y | 3020 | V | 2 | FLOAT32 | R
|  |  | Voltage B-C | Y | Y | Y | Y | Y | 3022 | V | 2 | FLOAT32 | R
|  |  | Voltage C-A | Y | Y | Y | Y | Y | 3024 | V | 2 | FLOAT32 | R
|  |  | Voltage L-L Avg | Y | Y | Y | Y | Y | 3026 | V | 2 | FLOAT32 | R
|  |  | Voltage A-N | Y | Y | Y | Y | Y | 3028 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where Van is connected
|  |  | Voltage B-N | Y | Y | Y | Y | Y | 3030 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where Vbn is connected
|  |  | Voltage C-N | Y | Y | Y | Y | Y | 3032 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where Vcn is connected
|  |  | Voltage N-G | [5 empty] | 3034 | V | 2 | FLOAT32 | R |  |  | Need to indicate under what conditions this value will be reported.
|  |  | Voltage L-N Avg | Y | Y | Y | Y | Y | 3036 | V | 2 | FLOAT32 | R |  |  | Reportable only in systems where a L-N voltage is applied
|  | Voltage Unbalance |  | Y | Y | Y | Y | Y | 3038 | --- |  | --- | --- | --- | ---
|  |  | Voltage Unbalance A-B | Y | Y | Y | Y | Y | 3038 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance B-C | Y | Y | Y | Y | Y | 3040 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance C-A | Y | Y | Y | Y | Y | 3042 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance L-L Worst | Y | Y | Y | Y | Y | 3044 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance A-N | Y | Y | Y | Y | Y | 3046 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance B-N | Y | Y | Y | Y | Y | 3048 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance C-N | Y | Y | Y | Y | Y | 3050 | % | 2 | FLOAT32 | R
|  |  | Voltage Unbalance L-N Worst | Y | Y | Y | Y | Y | 3052 | % | 2 | FLOAT32 | R
|  | Power |  | Y | Y | Y | Y | Y | 3054 | --- |  | --- | --- | --- | ---
|  |  | Active Power A | Y | Y | Y | Y | Y | 3054 | kW | 2 | FLOAT32 | R
|  |  | Active Power B | Y | Y | Y | Y | Y | 3056 | kW | 2 | FLOAT32 | R
|  |  | Active Power C | Y | Y | Y | Y | Y | 3058 | kW | 2 | FLOAT32 | R
|  |  | Active Power Total | Y | Y | Y | Y | Y | 3060 | kW | 2 | FLOAT32 | R
|  |  | Reactive Power A | Y | Y | Y | Y | Y | 3062 | kVAR | 2 | FLOAT32 | R
|  |  | Reactive Power B | Y | Y | Y | Y | Y | 3064 | kVAR | 2 | FLOAT32 | R
|  |  | Reactive Power C | Y | Y | Y | Y | Y | 3066 | kVAR | 2 | FLOAT32 | R
|  |  | Reactive Power Total | Y | Y | Y | Y | Y | 3068 | kVAR | 2 | FLOAT32 | R
|  |  | Apparent Power A | Y | Y | Y | Y | Y | 3070 | kVA | 2 | FLOAT32 | R
|  |  | Apparent Power B | Y | Y | Y | Y | Y | 3072 | kVA | 2 | FLOAT32 | R
|  |  | Apparent Power C | Y | Y | Y | Y | Y | 3074 | kVA | 2 | FLOAT32 | R
|  |  | Apparent Power Total | Y | Y | Y | Y | Y | 3076 | kVA | 2 | FLOAT32 | R
|  | Power Factor |  | Y | Y | Y | Y | Y | 3078 | --- |  | --- | --- | --- | ---
|  |  | Power Factor A | Y | Y | Y | Y | Y | 3078 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Power Factor B | Y | Y | Y | Y | Y | 3080 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Power Factor C | Y | Y | Y | Y | Y | 3082 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Power Factor Total | Y | Y | Y | Y | Y | 3084 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Displacement Power Factor A | Y | Y | Y | Y | Y | 3086 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Displacement Power Factor B | Y | Y | Y | Y | Y | 3088 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Displacement Power Factor C | Y | Y | Y | Y | Y | 3090 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Displacement Power Factor Total | Y | Y | Y | Y | Y | 3092 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  | Frequency | Frequency | Y | Y | Y | Y | Y | 3110 | Hz | 2 | FLOAT32 | R | 42 – 70
|  | Power Factor, Alternate Format |  | Y | Y | Y | Y | Y | 3192 | ---
|  |  | Power Factor Total IEC | Y | Y | Y | Y | Y | 3192 | --- | 2 | FLOAT32 | R | -1 to 1
|  |  | Power Factor Total Lead Lag | Y | Y | Y | Y | Y | 3194 | --- | 2 | FLOAT32 | R | -1 to 1
|  |  | Power Factor Total IEC | Y | Y | Y | Y | Y | 3196 | --- | 1 | INT16 | R | -1 to 1 |  | If a negative value is reported, add 32768 then divide by 1000 to find the lagging PF reported. If the number is positive just divide that number by 1000 to get the PF reported.
|  |  | Power Factor Total Lead Lag | Y | Y | Y | Y | Y | 3197 | --- | 1 | INT16 | R | -1 to 1 |  | If a negative value is reported, add 32768 then divide by 1000 to find the lagging PF reported. If the number is positive just divide that number by 1000 to get the PF reported.
| Energy |  |  | Y | Y | Y | Y | Y | 3200 | --- |  | --- | --- | --- | ---
|  | Accumulated Energy |  | Y | Y | Y | Y | Y | 3200 | --- |  | --- | --- | --- | ---
|  |  | Accumulated Energy Reset Date/Time | Y | Y | Y | Y | Y | 3200 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Active Energy Delivered (Into Load) | Y | Y | Y | Y | Y | 3204 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Received (Out of Load) | Y | Y | Y | Y | Y | 3208 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Delivered + Received | Y | Y | Y | Y | Y | 3212 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Delivered – Received | Y | Y | Y | Y | Y | 3216 | Wh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered | Y | Y | Y | Y | Y | 3220 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Received | Y | Y | Y | Y | Y | 3224 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered + Received | Y | Y | Y | Y | Y | 3228 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered – Received | Y | Y | Y | Y | Y | 3232 | VARh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered | Y | Y | Y | Y | Y | 3236 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Received | Y | Y | Y | Y | Y | 3240 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered + Received | Y | Y | Y | Y | Y | 3244 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered – Received | Y | Y | Y | Y | Y | 3248 | VAh | 4 | INT64 | R | --- | 0
| Demand |  |  | Y | Y | Y | Y | Y | 3701 | --- |  | --- | --- | --- | ---
|  | Demand System 1 (Power) |  | Y | Y | Y | Y | Y | 3701 | --- |  | --- | --- | --- | --- | Power
|  |  | Power Demand Method | Y | Y | Y | Y | Y | 3701 | --- | 1 | INT16U | RWC | 0-11 PM5350: 0-7 | 2 | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval
|  |  | Power Demand Interval Duration | Y | Y | Y | Y | Y | 3702 | minutes | 1 | INT16U | RWC | 1 – 60 | 15
|  |  | Power Demand Subinterval Duration | Y | Y | Y | Y | Y | 3703 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  |  | Power Demand Elapsed Time in Interval | Y | Y | Y | Y | Y | 3704 | seconds | 1 | INT16U | R | 0 – 3,600 | 0
|  |  | Power Demand Elapsed Time in Subinterval | Y | Y | Y | Y | Y | 3705 | seconds | 1 | INT16U | R | 0 – 3,600 | 0
|  |  | Power Demand Peak Reset Date/Time | Y | Y | Y | Y | Y | 3706 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Reserved | [5 empty] | 3710 | --- | 1 | INT16U | R |  | N/A
|  | Demand System 2 (Current) |  | Y | Y | Y | Y | Y | 3711 | --- |  | --- | --- | --- | --- | Current
|  |  | Current Demand Method | Y | Y | Y | Y | Y | 3711 | --- | 1 | INT16U | RWC | 0-11 PM5350: 0-7 | 2 | 0 = Thermal Demand 1 = Timed Interval Sliding Block 2 = Timed Interval Block 3 = Timed Interval Rolling Block 4 = Input Synchronized Block 5 = Input Synchronized Rolling Block 6 = Command Synchronized Block 7 = Command Synchronized Rolling Block 8 = Clock Synchronized Block 9 = Clock Synchronized Rolling Block 10 = Slave to System 1 (Power) Demand Interval 11 = Slave to Incremental Energy Interval
|  |  | Current Demand Interval Duration | Y | Y | Y | Y | Y | 3712 | minutes | 1 | INT16U | RWC | 1 – 60 | 15
|  |  | Current Demand Subinterval Duration | Y | Y | Y | Y | Y | 3713 | minutes | 1 | INT16U | RWC | 1 – 60 | 15 | The value must be evenly divisable into Interval Duration for Rolling Block. For Thermal and Fixed Block demand methods, this value must be same as Interval Duration.
|  |  | Current Demand Elapsed Time in Interval | Y | Y | Y | Y | Y | 3714 | seconds | 1 | INT16U | R | 0 – 3,600 | 0
|  |  | Current Demand Elapsed Time in Subinterval | Y | Y | Y | Y | Y | 3715 | seconds | 1 | INT16U | R | 0 – 3,600 | 0
|  |  | Current Demand Peak Reset Date/Time | Y | Y | Y | Y | Y | 3716 | --- | 4 | DATETIME | R | --- | N/A
|  | Demand Channel 1 (Active Power) |  | Y | Y | Y | Y | Y | 3761 | --- |  | --- | --- | --- | --- | Active Power Total
|  |  | Demand System Assignment | Y | Y | Y | Y | Y | 3761 | --- | 1 | INT16U | R | 0 – 6 | 1 | Power Demand
|  |  | Register Number of Metered Quantity | Y | Y | Y | Y | Y | 3762 | --- | 1 | INT16U | R | 1 – 32,767 | R_PTOT_50_60_CYC_RMS | Active Power Total
|  |  | Units Code | Y | Y | Y | Y | Y | 3763 | --- | 1 | INT16U | R | 0 – 100 | 12
|  |  | Last Demand | Y | Y | Y | Y | Y | 3764 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y | Y | Y | Y | 3766 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | Y | Y | Y | Y | Y | 3768 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y | Y | Y | Y | 3770 | kW | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | Y | Y | Y | Y | Y | 3772 | --- | 4 | DATETIME | R | --- | N/A
|  | Demand Channel 2 (Reactive Power) |  | Y | Y | Y | Y | Y | 3777 | --- |  | --- | --- | --- | --- | Reactive Power Total
|  |  | Demand System Assignment | Y | Y | Y | Y | Y | 3777 | --- | 1 | INT16U | R | 0 – 6 | 1 | Power Demand
|  |  | Register Number of Metered Quantity | Y | Y | Y | Y | Y | 3778 | --- | 1 | INT16U | R | 1 – 32,767 | R_QTOT_50_60_CYC_RMS | Reactive Power Total
|  |  | Units Code | Y | Y | Y | Y | Y | 3779 | --- | 1 | INT16U | R | 0 – 100 | 15
|  |  | Last Demand | Y | Y | Y | Y | Y | 3780 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y | Y | Y | Y | 3782 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | Y | Y | Y | Y | Y | 3784 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y | Y | Y | Y | 3786 | kVAR | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | Y | Y | Y | Y | Y | 3788 | --- | 4 | DATETIME | R | --- | N/A
|  | Demand Channel 3 (Apparent Power) |  | Y | Y | Y | Y | Y | 3793 | --- |  | --- | --- | --- | --- | Apparent Power Total
|  |  | Demand System Assignment | Y | Y | Y | Y | Y | 3793 | --- | 1 | INT16U | R | 0 – 6 | 1 | Power Demand
|  |  | Register Number of Metered Quantity | Y | Y | Y | Y | Y | 3794 | --- | 1 | INT16U | R | 1 – 32,767 | R_STOT_50_60_CYC_RMS | Apparent Power Total
|  |  | Units Code | Y | Y | Y | Y | Y | 3795 | --- | 1 | INT16U | R | 0 – 100 | 18
|  |  | Last Demand | Y | Y | Y | Y | Y | 3796 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y | Y | Y | Y | 3798 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | Y | Y | Y | Y | Y | 3800 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y | Y | Y | Y | 3802 | kVA | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | Y | Y | Y | Y | Y | 3804 | --- | 4 | DATETIME | R | --- | N/A
|  | Demand Channel 8 (Current Avg) |  | Y | Y | Y | Y | Y | 3873 | --- |  | --- | --- | --- | --- | Current, Average
|  |  | Demand System Assignment | Y | Y | Y | Y | Y | 3873 | --- | 1 | INT16U | R | 0 – 6 | 2 | Current Demand
|  |  | Register Number of Metered Quantity | Y | Y | Y | Y | Y | 3874 | --- | 1 | INT16U | R | 1 – 32,767 | R_IAVG_50_60_CYC_RMS | Current, Average
|  |  | Units Code | Y | Y | Y | Y | Y | 3875 | --- | 1 | INT16U | R | 0 – 100 | 6
|  |  | Last Demand | Y | Y | Y | Y | Y | 3876 | A | 2 | FLOAT32 | R | --- | 0
|  |  | Present Demand | Y | Y | Y | Y | Y | 3878 | A | 2 | FLOAT32 | R | --- | 0
|  |  | Predicted Demand | Y | Y | Y | Y | Y | 3880 | A | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand | Y | Y | Y | Y | Y | 3882 | A | 2 | FLOAT32 | R | --- | 0
|  |  | Peak Demand DateTime | Y | Y | Y | Y | Y | 3884 | --- | 4 | DATETIME | R | --- | N/A
|  | Miscellaneous Demand Setup & Data | [7 empty] | --- |  | --- | --- | --- | ---
|  |  | Clock Sync Time of Day | Y | Y | Y | Y | Y | 4147 | --- | 1 | INT16U | RWC | 0-2359 | 0 | Time of day to which the demand interval is to be synchronized. Applies to demand intervals configured as Clock Synchronized. Default = midnight.
| Energy TOU/MT |  |  |  | Y | Y | Y | Y
|  | Time-of-Use/Mult-Tariff Energy |  |  | Y | Y | Y | Y
|  |  | TOU/MT Mode |  | Y | Y | Y | Y | 4190 | --- | 1 | INT16U | RWC | 0 - 2 | 0
|  |  | TOU/MT Energy Active Rate |  | Y | Y | Y | Y | 4191 | --- | 1 | INT16U | R | 0 – 8 | 0
|  |  | TOU/MT Energy Reset Date/Time |  | Y | Y | Y | Y | 4192 | --- | 4 | DATETIME | R | --- | N/A
|  |  | Active Energy Delivered Rate 1 |  | Y | Y | Y | Y | 4196 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Delivered Rate 2 |  | Y | Y | Y | Y | 4200 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Delivered Rate 3 |  | Y | Y | Y | Y | 4204 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Delivered Rate 4 |  | Y | Y | Y | Y | 4208 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Received Rate 1 |  | Y | Y | Y | Y | 4228 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Received Rate 2 |  | Y | Y | Y | Y | 4232 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Received Rate 3 |  | Y | Y | Y | Y | 4236 | Wh | 4 | INT64 | R | --- | 0
|  |  | Active Energy Received Rate 4 |  | Y | Y | Y | Y | 4240 | Wh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 1 |  | Y | Y | Y | Y | 4260 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 2 |  | Y | Y | Y | Y | 4264 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 3 |  | Y | Y | Y | Y | 4268 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 4 |  | Y | Y | Y | Y | 4272 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Received Rate 1 |  | Y | Y | Y | Y | 4292 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Received Rate 2 |  | Y | Y | Y | Y | 4296 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Received Rate 3 |  | Y | Y | Y | Y | 4300 | VARh | 4 | INT64 | R | --- | 0
|  |  | Reactive Energy Received Rate 4 |  | Y | Y | Y | Y | 4304 | VARh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 1 |  | Y | Y | Y | Y | 4324 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 2 |  | Y | Y | Y | Y | 4328 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 3 |  | Y | Y | Y | Y | 4332 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 4 |  | Y | Y | Y | Y | 4336 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Received Rate 1 |  | Y | Y | Y | Y | 4356 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Received Rate 2 |  | Y | Y | Y | Y | 4360 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Received Rate 3 |  | Y | Y | Y | Y | 4364 | VAh | 4 | INT64 | R | --- | 0
|  |  | Apparent Energy Received Rate 4 |  | Y | Y | Y | Y | 4368 | VAh | 4 | INT64 | R | --- | 0
|  |  | MT Day Type Rate 1 |  | Y | Y | Y | Y | 4516 | --- | 1 | INT16U | RWC | 1 -10 | 1 | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 1 |  | Y | Y | Y | Y | 4517 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT End Time Rate 1 |  | Y | Y | Y | Y | 4518 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT Start Month Rate1 |  | Y | Y | Y | Y | 4519 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT Start Day Rate 1 |  | Y | Y | Y | Y | 4520 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT End Month Rate 1 |  | Y | Y | Y | Y | 4521 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT End Day Rate 1 |  | Y | Y | Y | Y | 4522 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT Day Type Rate 2 |  | Y | Y | Y | Y | 4523 | --- | 1 | INT16U | RWC | 1 -10 | 1 | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 2 |  | Y | Y | Y | Y | 4524 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT End Time Rate 2 |  | Y | Y | Y | Y | 4525 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT Start Month Rate2 |  | Y | Y | Y | Y | 4526 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT Start Day Rate 2 |  | Y | Y | Y | Y | 4527 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT End Month Rate 2 |  | Y | Y | Y | Y | 4528 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT End Day Rate 2 |  | Y | Y | Y | Y | 4529 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT Day Type Rate 3 |  | Y | Y | Y | Y | 4530 | --- | 1 | INT16U | RWC | 1 -10 | 1 | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 3 |  | Y | Y | Y | Y | 4531 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT End Time Rate 3 |  | Y | Y | Y | Y | 4532 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT Start Month Rate3 |  | Y | Y | Y | Y | 4533 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT Start Day Rate 3 |  | Y | Y | Y | Y | 4534 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT End Month Rate 3 |  | Y | Y | Y | Y | 4535 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT End Day Rate 3 |  | Y | Y | Y | Y | 4536 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT Day Type Rate 4 |  | Y | Y | Y | Y | 4537 | --- | 1 | INT16U | RWC | 1 -10 | 1 | 1 = Everyday, 2-8 = Mon-Sunday, 9 = Weekday, 10 = Weekend
|  |  | MT Start Time Rate 4 |  | Y | Y | Y | Y | 4538 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT End Time Rate 4 |  | Y | Y | Y | Y | 4539 | --- | 1 | INT16U | RWC | 0-2359 | 0
|  |  | MT Start Month Rate4 |  | Y | Y | Y | Y | 4540 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT Start Day Rate 4 |  | Y | Y | Y | Y | 4541 | --- | 1 | INT16U | RWC | 0-31 | 0
|  |  | MT End Month Rate 4 |  | Y | Y | Y | Y | 4542 | --- | 1 | INT16U | RWC | 0-12 | 0
|  |  | MT End Day Rate 4 |  | Y | Y | Y | Y | 4543 | --- | 1 | INT16U | RWC | 0-31 | 0
Energy Multi Tariff and Multi Circuit - 32 bit floating point values | [8 empty] | 4800
| Energy Multi Tariff - 32 bit floating point values | [7 empty] | 4800
|  | MT Active Energy Delivered Rates - 32 bit floating point values |  |  | Y | Y | Y | Y | 4800
|  |  | Active Energy Delivered Rate 1 |  | Y | Y | Y | Y | 4800 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Delivered Rate 2 |  | Y | Y | Y | Y | 4802 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Delivered Rate 3 |  | Y | Y | Y | Y | 4804 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Delivered Rate 4 |  | Y | Y | Y | Y | 4806 | kWh | 2 | FLOAT32 | R | --- | 0
|  | MT Active Energy Received Rates - 32 bit floating point values |  |  | Y | Y | Y | Y |  | --- | --- | --- | --- | --- | ---
|  |  | Active Energy Received Rate 1 |  | Y | Y | Y | Y | 4816 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Received Rate 2 |  | Y | Y | Y | Y | 4818 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Received Rate 3 |  | Y | Y | Y | Y | 4820 | kWh | 2 | FLOAT32 | R | --- | 0
|  |  | Active Energy Received Rate 4 |  | Y | Y | Y | Y | 4822 | kWh | 2 | FLOAT32 | R | --- | 0
|  | MT Reactive Energy Delivered Rates - 32 bit floating point values |  |  | Y | Y | Y | Y |  | --- | --- | --- | --- | --- | ---
|  |  | Reactive Energy Delivered Rate 1 |  | Y | Y | Y | Y | 4832 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 2 |  | Y | Y | Y | Y | 4834 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 3 |  | Y | Y | Y | Y | 4836 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Delivered Rate 4 |  | Y | Y | Y | Y | 4838 | kVARh | 2 | FLOAT32 | R | --- | 0
|  | MT Reactive Energy Received Rates - 32 bit floating point values |  |  | Y | Y | Y | Y |  | --- | --- | --- | --- | --- | ---
|  |  | Reactive Energy Received Rate 1 |  | Y | Y | Y | Y | 4848 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Received Rate 2 |  | Y | Y | Y | Y | 4850 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Received Rate 3 |  | Y | Y | Y | Y | 4852 | kVARh | 2 | FLOAT32 | R | --- | 0
|  |  | Reactive Energy Received Rate 4 |  | Y | Y | Y | Y | 4854 | kVARh | 2 | FLOAT32 | R | --- | 0
|  | MT Apparent Energy Delivered Rates - 32 bit floating point values |  |  | Y | Y | Y | Y |  | --- | --- | --- | --- | --- | ---
|  |  | Apparent Energy Delivered Rate 1 |  | Y | Y | Y | Y | 4864 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 2 |  | Y | Y | Y | Y | 4866 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 3 |  | Y | Y | Y | Y | 4868 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Delivered Rate 4 |  | Y | Y | Y | Y | 4870 | kVAh | 2 | FLOAT32 | R | --- | 0
|  | MT Apparent Energy Received Rates - 32 bit floating point values |  |  | Y | Y | Y | Y |  | --- | --- | --- | --- | --- | ---
|  |  | Apparent Energy Received Rate 1 |  | Y | Y | Y | Y | 4880 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Received Rate 2 |  | Y | Y | Y | Y | 4882 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Received Rate 3 |  | Y | Y | Y | Y | 4884 | kVAh | 2 | FLOAT32 | R | --- | 0
|  |  | Apparent Energy Received Rate 4 |  | Y | Y | Y | Y | 4886 | kVAh | 2 | FLOAT32 | R | --- | 0
Command Interface |  |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
| Protected Command Interface |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Command parameters |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Requested Command | Y | Y | Y | Y | Y | 5000 | --- | 1 | INT16U | RW | 1 – 32767 | 0
|  |  | Command Semaphore | Y | Y | Y | Y | Y | 5001 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 001 | Y | Y | Y | Y | Y | 5002 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 002 | Y | Y | Y | Y | Y | 5003 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 003 | Y | Y | Y | Y | Y | 5004 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 004 | Y | Y | Y | Y | Y | 5005 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 005 | Y | Y | Y | Y | Y | 5006 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 006 | Y | Y | Y | Y | Y | 5007 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 007 | Y | Y | Y | Y | Y | 5008 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 008 | Y | Y | Y | Y | Y | 5009 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 009 | Y | Y | Y | Y | Y | 5010 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 010 | Y | Y | Y | Y | Y | 5011 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 011 | Y | Y | Y | Y | Y | 5012 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 012 | Y | Y | Y | Y | Y | 5013 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 013 | Y | Y | Y | Y | Y | 5014 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 014 | Y | Y | Y | Y | Y | 5015 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 015 | Y | Y | Y | Y | Y | 5016 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 016 | Y | Y | Y | Y | Y | 5017 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 017 | Y | Y | Y | Y | Y | 5018 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 018 | Y | Y | Y | Y | Y | 5019 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 019 | Y | Y | Y | Y | Y | 5020 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 020 | Y | Y | Y | Y | Y | 5021 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 021 | Y | Y | Y | Y | Y | 5022 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 022 | Y | Y | Y | Y | Y | 5023 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 023 | Y | Y | Y | Y | Y | 5024 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 024 | Y | Y | Y | Y | Y | 5025 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 025 | Y | Y | Y | Y | Y | 5026 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 026 | Y | Y | Y | Y | Y | 5027 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 027 | Y | Y | Y | Y | Y | 5028 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 028 | Y | Y | Y | Y | Y | 5029 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 029 | Y | Y | Y | Y | Y | 5030 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 030 | Y | Y | Y | Y | Y | 5031 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 031 | Y | Y | Y | Y | Y | 5032 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 032 | Y | Y | Y | Y | Y | 5033 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 033 | Y | Y | Y | Y | Y | 5034 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 034 | Y | Y | Y | Y | Y | 5035 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 035 | Y | Y | Y | Y | Y | 5036 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 036 | Y | Y | Y | Y | Y | 5037 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 037 | Y | Y | Y | Y | Y | 5038 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 038 | Y | Y | Y | Y | Y | 5039 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 039 | Y | Y | Y | Y | Y | 5040 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 040 | Y | Y | Y | Y | Y | 5041 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 041 | Y | Y | Y | Y | Y | 5042 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 042 | Y | Y | Y | Y | Y | 5043 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 043 | Y | Y | Y | Y | Y | 5044 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 044 | Y | Y | Y | Y | Y | 5045 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 045 | Y | Y | Y | Y | Y | 5046 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 046 | Y | Y | Y | Y | Y | 5047 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 047 | Y | Y | Y | Y | Y | 5048 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 048 | Y | Y | Y | Y | Y | 5049 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 049 | Y | Y | Y | Y | Y | 5050 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 050 | Y | Y | Y | Y | Y | 5051 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 051 | Y | Y | Y | Y | Y | 5052 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 052 | Y | Y | Y | Y | Y | 5053 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 053 | Y | Y | Y | Y | Y | 5054 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 054 | Y | Y | Y | Y | Y | 5055 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 055 | Y | Y | Y | Y | Y | 5056 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 056 | Y | Y | Y | Y | Y | 5057 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 057 | Y | Y | Y | Y | Y | 5058 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 058 | Y | Y | Y | Y | Y | 5059 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 059 | Y | Y | Y | Y | Y | 5060 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 060 | Y | Y | Y | Y | Y | 5061 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 061 | Y | Y | Y | Y | Y | 5062 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 062 | Y | Y | Y | Y | Y | 5063 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 063 | Y | Y | Y | Y | Y | 5064 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 064 | Y | Y | Y | Y | Y | 5065 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 065 | Y | Y | Y | Y | Y | 5066 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 066 | Y | Y | Y | Y | Y | 5067 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 067 | Y | Y | Y | Y | Y | 5068 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 068 | Y | Y | Y | Y | Y | 5069 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 069 | Y | Y | Y | Y | Y | 5070 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 070 | Y | Y | Y | Y | Y | 5071 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 071 | Y | Y | Y | Y | Y | 5072 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 072 | Y | Y | Y | Y | Y | 5073 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 073 | Y | Y | Y | Y | Y | 5074 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 074 | Y | Y | Y | Y | Y | 5075 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 075 | Y | Y | Y | Y | Y | 5076 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 076 | Y | Y | Y | Y | Y | 5077 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 077 | Y | Y | Y | Y | Y | 5078 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 078 | Y | Y | Y | Y | Y | 5079 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 079 | Y | Y | Y | Y | Y | 5080 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 080 | Y | Y | Y | Y | Y | 5081 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 081 | Y | Y | Y | Y | Y | 5082 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 082 | Y | Y | Y | Y | Y | 5083 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 083 | Y | Y | Y | Y | Y | 5084 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 084 | Y | Y | Y | Y | Y | 5085 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 085 | Y | Y | Y | Y | Y | 5086 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 086 | Y | Y | Y | Y | Y | 5087 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 087 | Y | Y | Y | Y | Y | 5088 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 088 | Y | Y | Y | Y | Y | 5089 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 089 | Y | Y | Y | Y | Y | 5090 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 090 | Y | Y | Y | Y | Y | 5091 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 091 | Y | Y | Y | Y | Y | 5092 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 092 | Y | Y | Y | Y | Y | 5093 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 093 | Y | Y | Y | Y | Y | 5094 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 094 | Y | Y | Y | Y | Y | 5095 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 095 | Y | Y | Y | Y | Y | 5096 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 096 | Y | Y | Y | Y | Y | 5097 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 097 | Y | Y | Y | Y | Y | 5098 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 098 | Y | Y | Y | Y | Y | 5099 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 099 | Y | Y | Y | Y | Y | 5100 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 100 | Y | Y | Y | Y | Y | 5101 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 101 | Y | Y | Y | Y | Y | 5102 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 102 | Y | Y | Y | Y | Y | 5103 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 103 | Y | Y | Y | Y | Y | 5104 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 104 | Y | Y | Y | Y | Y | 5105 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 105 | Y | Y | Y | Y | Y | 5106 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 106 | Y | Y | Y | Y | Y | 5107 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 107 | Y | Y | Y | Y | Y | 5108 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 108 | Y | Y | Y | Y | Y | 5109 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 109 | Y | Y | Y | Y | Y | 5110 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 110 | Y | Y | Y | Y | Y | 5111 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 111 | Y | Y | Y | Y | Y | 5112 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 112 | Y | Y | Y | Y | Y | 5113 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 113 | Y | Y | Y | Y | Y | 5114 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 114 | Y | Y | Y | Y | Y | 5115 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 115 | Y | Y | Y | Y | Y | 5116 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 116 | Y | Y | Y | Y | Y | 5117 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 117 | Y | Y | Y | Y | Y | 5118 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 118 | Y | Y | Y | Y | Y | 5119 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 119 | Y | Y | Y | Y | Y | 5120 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 120 | Y | Y | Y | Y | Y | 5121 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 121 | Y | Y | Y | Y | Y | 5122 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 122 | Y | Y | Y | Y | Y | 5123 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 123 | Y | Y | Y | Y | Y | 5124 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Status | Y | Y | Y | Y | Y | 5125 | --- | 1 | INT16U | R | 0 – 32767 | 0
|  |  | Command Result | Y | Y | Y | Y | Y | 5126 | --- | 1 | INT16U | R | --- | 0 | 0 = Valid Operation 3000 = Invalid Command 3001 = Invalid Parameter 3002 = Invalid Number of Parameters 3003 = Invalid Password 3004 = Command Failed Security Check 3005 = Invalid Command Interface 3006 = Revenue Security Active 3007 = Operation Not Performed 3008 = Invalid ID 3009 = Feature Not Supported 3010 = Invalid Semaphore 6000 = Invalid Control Mode 6001 = Digital Output Disabled 8000 = File System Error
|  |  | Command Data 001 | Y | Y | Y | Y | Y | 5127 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 002 | Y | Y | Y | Y | Y | 5128 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 003 | Y | Y | Y | Y | Y | 5129 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 004 | Y | Y | Y | Y | Y | 5130 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 005 | Y | Y | Y | Y | Y | 5131 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 006 | Y | Y | Y | Y | Y | 5132 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 007 | Y | Y | Y | Y | Y | 5133 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 008 | Y | Y | Y | Y | Y | 5134 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 009 | Y | Y | Y | Y | Y | 5135 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 010 | Y | Y | Y | Y | Y | 5136 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 011 | Y | Y | Y | Y | Y | 5137 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 012 | Y | Y | Y | Y | Y | 5138 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 013 | Y | Y | Y | Y | Y | 5139 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 014 | Y | Y | Y | Y | Y | 5140 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 015 | Y | Y | Y | Y | Y | 5141 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 016 | Y | Y | Y | Y | Y | 5142 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 017 | Y | Y | Y | Y | Y | 5143 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 018 | Y | Y | Y | Y | Y | 5144 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 019 | Y | Y | Y | Y | Y | 5145 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 020 | Y | Y | Y | Y | Y | 5146 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 021 | Y | Y | Y | Y | Y | 5147 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 022 | Y | Y | Y | Y | Y | 5148 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 023 | Y | Y | Y | Y | Y | 5149 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 024 | Y | Y | Y | Y | Y | 5150 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 025 | Y | Y | Y | Y | Y | 5151 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 026 | Y | Y | Y | Y | Y | 5152 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 027 | Y | Y | Y | Y | Y | 5153 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 028 | Y | Y | Y | Y | Y | 5154 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 029 | Y | Y | Y | Y | Y | 5155 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 030 | Y | Y | Y | Y | Y | 5156 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 031 | Y | Y | Y | Y | Y | 5157 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 032 | Y | Y | Y | Y | Y | 5158 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 033 | Y | Y | Y | Y | Y | 5159 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 034 | Y | Y | Y | Y | Y | 5160 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 035 | Y | Y | Y | Y | Y | 5161 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 036 | Y | Y | Y | Y | Y | 5162 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 037 | Y | Y | Y | Y | Y | 5163 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 038 | Y | Y | Y | Y | Y | 5164 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 039 | Y | Y | Y | Y | Y | 5165 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 040 | Y | Y | Y | Y | Y | 5166 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 041 | Y | Y | Y | Y | Y | 5167 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 042 | Y | Y | Y | Y | Y | 5168 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 043 | Y | Y | Y | Y | Y | 5169 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 044 | Y | Y | Y | Y | Y | 5170 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 045 | Y | Y | Y | Y | Y | 5171 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 046 | Y | Y | Y | Y | Y | 5172 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 047 | Y | Y | Y | Y | Y | 5173 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 048 | Y | Y | Y | Y | Y | 5174 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 049 | Y | Y | Y | Y | Y | 5175 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 050 | Y | Y | Y | Y | Y | 5176 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 051 | Y | Y | Y | Y | Y | 5177 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 052 | Y | Y | Y | Y | Y | 5178 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 053 | Y | Y | Y | Y | Y | 5179 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 054 | Y | Y | Y | Y | Y | 5180 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 055 | Y | Y | Y | Y | Y | 5181 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 056 | Y | Y | Y | Y | Y | 5182 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 057 | Y | Y | Y | Y | Y | 5183 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 058 | Y | Y | Y | Y | Y | 5184 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 059 | Y | Y | Y | Y | Y | 5185 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 060 | Y | Y | Y | Y | Y | 5186 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 061 | Y | Y | Y | Y | Y | 5187 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 062 | Y | Y | Y | Y | Y | 5188 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 063 | Y | Y | Y | Y | Y | 5189 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 064 | Y | Y | Y | Y | Y | 5190 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 065 | Y | Y | Y | Y | Y | 5191 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 066 | Y | Y | Y | Y | Y | 5192 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 067 | Y | Y | Y | Y | Y | 5193 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 068 | Y | Y | Y | Y | Y | 5194 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 069 | Y | Y | Y | Y | Y | 5195 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 070 | Y | Y | Y | Y | Y | 5196 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 071 | Y | Y | Y | Y | Y | 5197 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 072 | Y | Y | Y | Y | Y | 5198 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 073 | Y | Y | Y | Y | Y | 5199 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 074 | Y | Y | Y | Y | Y | 5200 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 075 | Y | Y | Y | Y | Y | 5201 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 076 | Y | Y | Y | Y | Y | 5202 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 077 | Y | Y | Y | Y | Y | 5203 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 078 | Y | Y | Y | Y | Y | 5204 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 079 | Y | Y | Y | Y | Y | 5205 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 080 | Y | Y | Y | Y | Y | 5206 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 081 | Y | Y | Y | Y | Y | 5207 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 082 | Y | Y | Y | Y | Y | 5208 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 083 | Y | Y | Y | Y | Y | 5209 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 084 | Y | Y | Y | Y | Y | 5210 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 085 | Y | Y | Y | Y | Y | 5211 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 086 | Y | Y | Y | Y | Y | 5212 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 087 | Y | Y | Y | Y | Y | 5213 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 088 | Y | Y | Y | Y | Y | 5214 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 089 | Y | Y | Y | Y | Y | 5215 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 090 | Y | Y | Y | Y | Y | 5216 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 091 | Y | Y | Y | Y | Y | 5217 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 092 | Y | Y | Y | Y | Y | 5218 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 093 | Y | Y | Y | Y | Y | 5219 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 094 | Y | Y | Y | Y | Y | 5220 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 095 | Y | Y | Y | Y | Y | 5221 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 096 | Y | Y | Y | Y | Y | 5222 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 097 | Y | Y | Y | Y | Y | 5223 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 098 | Y | Y | Y | Y | Y | 5224 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 099 | Y | Y | Y | Y | Y | 5225 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 100 | Y | Y | Y | Y | Y | 5226 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 101 | Y | Y | Y | Y | Y | 5227 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 102 | Y | Y | Y | Y | Y | 5228 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 103 | Y | Y | Y | Y | Y | 5229 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 104 | Y | Y | Y | Y | Y | 5230 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 105 | Y | Y | Y | Y | Y | 5231 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 106 | Y | Y | Y | Y | Y | 5232 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 107 | Y | Y | Y | Y | Y | 5233 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 108 | Y | Y | Y | Y | Y | 5234 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 109 | Y | Y | Y | Y | Y | 5235 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 110 | Y | Y | Y | Y | Y | 5236 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 111 | Y | Y | Y | Y | Y | 5237 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 112 | Y | Y | Y | Y | Y | 5238 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 113 | Y | Y | Y | Y | Y | 5239 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 114 | Y | Y | Y | Y | Y | 5240 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 115 | Y | Y | Y | Y | Y | 5241 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 116 | Y | Y | Y | Y | Y | 5242 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 117 | Y | Y | Y | Y | Y | 5243 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 118 | Y | Y | Y | Y | Y | 5244 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 119 | Y | Y | Y | Y | Y | 5245 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 120 | Y | Y | Y | Y | Y | 5246 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 121 | Y | Y | Y | Y | Y | 5247 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 122 | Y | Y | Y | Y | Y | 5248 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 123 | Y | Y | Y | Y | Y | 5249 | --- | 1 | INT16U | R | --- | 0
| Unprotected Command Interface |  |  | Y | Y | Y | Y | Y | 5250 | --- |  | --- | --- | --- | ---
|  | Command parameters |  | Y | Y | Y | Y | Y | 5250 | --- |  | --- | --- | --- | ---
|  |  | Requested Command | Y | Y | Y | Y | Y | 5250 | --- | 1 | INT16U | RW | 1 – 32767 | 0
|  |  | Command Parameter 001 | Y | Y | Y | Y | Y | 5252 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 002 | Y | Y | Y | Y | Y | 5253 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 003 | Y | Y | Y | Y | Y | 5254 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 004 | Y | Y | Y | Y | Y | 5255 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 005 | Y | Y | Y | Y | Y | 5256 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 006 | Y | Y | Y | Y | Y | 5257 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 007 | Y | Y | Y | Y | Y | 5258 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 008 | Y | Y | Y | Y | Y | 5259 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 009 | Y | Y | Y | Y | Y | 5260 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 010 | Y | Y | Y | Y | Y | 5261 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 011 | Y | Y | Y | Y | Y | 5262 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 012 | Y | Y | Y | Y | Y | 5263 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 013 | Y | Y | Y | Y | Y | 5264 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 014 | Y | Y | Y | Y | Y | 5265 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 015 | Y | Y | Y | Y | Y | 5266 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 016 | Y | Y | Y | Y | Y | 5267 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 017 | Y | Y | Y | Y | Y | 5268 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 018 | Y | Y | Y | Y | Y | 5269 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 019 | Y | Y | Y | Y | Y | 5270 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 020 | Y | Y | Y | Y | Y | 5271 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 021 | Y | Y | Y | Y | Y | 5272 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 022 | Y | Y | Y | Y | Y | 5273 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 023 | Y | Y | Y | Y | Y | 5274 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 024 | Y | Y | Y | Y | Y | 5275 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 025 | Y | Y | Y | Y | Y | 5276 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 026 | Y | Y | Y | Y | Y | 5277 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 027 | Y | Y | Y | Y | Y | 5278 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 028 | Y | Y | Y | Y | Y | 5279 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 029 | Y | Y | Y | Y | Y | 5280 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 030 | Y | Y | Y | Y | Y | 5281 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 031 | Y | Y | Y | Y | Y | 5282 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 032 | Y | Y | Y | Y | Y | 5283 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 033 | Y | Y | Y | Y | Y | 5284 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 034 | Y | Y | Y | Y | Y | 5285 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 035 | Y | Y | Y | Y | Y | 5286 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 036 | Y | Y | Y | Y | Y | 5287 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 037 | Y | Y | Y | Y | Y | 5288 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 038 | Y | Y | Y | Y | Y | 5289 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 039 | Y | Y | Y | Y | Y | 5290 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 040 | Y | Y | Y | Y | Y | 5291 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 041 | Y | Y | Y | Y | Y | 5292 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 042 | Y | Y | Y | Y | Y | 5293 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 043 | Y | Y | Y | Y | Y | 5294 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 044 | Y | Y | Y | Y | Y | 5295 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 045 | Y | Y | Y | Y | Y | 5296 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 046 | Y | Y | Y | Y | Y | 5297 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 047 | Y | Y | Y | Y | Y | 5298 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 048 | Y | Y | Y | Y | Y | 5299 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 049 | Y | Y | Y | Y | Y | 5300 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 050 | Y | Y | Y | Y | Y | 5301 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 051 | Y | Y | Y | Y | Y | 5302 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 052 | Y | Y | Y | Y | Y | 5303 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 053 | Y | Y | Y | Y | Y | 5304 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 054 | Y | Y | Y | Y | Y | 5305 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 055 | Y | Y | Y | Y | Y | 5306 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 056 | Y | Y | Y | Y | Y | 5307 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 057 | Y | Y | Y | Y | Y | 5308 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 058 | Y | Y | Y | Y | Y | 5309 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 059 | Y | Y | Y | Y | Y | 5310 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 060 | Y | Y | Y | Y | Y | 5311 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 061 | Y | Y | Y | Y | Y | 5312 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 062 | Y | Y | Y | Y | Y | 5313 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 063 | Y | Y | Y | Y | Y | 5314 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 064 | Y | Y | Y | Y | Y | 5315 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 065 | Y | Y | Y | Y | Y | 5316 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 066 | Y | Y | Y | Y | Y | 5317 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 067 | Y | Y | Y | Y | Y | 5318 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 068 | Y | Y | Y | Y | Y | 5319 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 069 | Y | Y | Y | Y | Y | 5320 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 070 | Y | Y | Y | Y | Y | 5321 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 071 | Y | Y | Y | Y | Y | 5322 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 072 | Y | Y | Y | Y | Y | 5323 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 073 | Y | Y | Y | Y | Y | 5324 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 074 | Y | Y | Y | Y | Y | 5325 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 075 | Y | Y | Y | Y | Y | 5326 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 076 | Y | Y | Y | Y | Y | 5327 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 077 | Y | Y | Y | Y | Y | 5328 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 078 | Y | Y | Y | Y | Y | 5329 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 079 | Y | Y | Y | Y | Y | 5330 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 080 | Y | Y | Y | Y | Y | 5331 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 081 | Y | Y | Y | Y | Y | 5332 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 082 | Y | Y | Y | Y | Y | 5333 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 083 | Y | Y | Y | Y | Y | 5334 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 084 | Y | Y | Y | Y | Y | 5335 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 085 | Y | Y | Y | Y | Y | 5336 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 086 | Y | Y | Y | Y | Y | 5337 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 087 | Y | Y | Y | Y | Y | 5338 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 088 | Y | Y | Y | Y | Y | 5339 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 089 | Y | Y | Y | Y | Y | 5340 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 090 | Y | Y | Y | Y | Y | 5341 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 091 | Y | Y | Y | Y | Y | 5342 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 092 | Y | Y | Y | Y | Y | 5343 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 093 | Y | Y | Y | Y | Y | 5344 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 094 | Y | Y | Y | Y | Y | 5345 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 095 | Y | Y | Y | Y | Y | 5346 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 096 | Y | Y | Y | Y | Y | 5347 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 097 | Y | Y | Y | Y | Y | 5348 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 098 | Y | Y | Y | Y | Y | 5349 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 099 | Y | Y | Y | Y | Y | 5350 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 100 | Y | Y | Y | Y | Y | 5351 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 101 | Y | Y | Y | Y | Y | 5352 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 102 | Y | Y | Y | Y | Y | 5353 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 103 | Y | Y | Y | Y | Y | 5354 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 104 | Y | Y | Y | Y | Y | 5355 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 105 | Y | Y | Y | Y | Y | 5356 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 106 | Y | Y | Y | Y | Y | 5357 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 107 | Y | Y | Y | Y | Y | 5358 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 108 | Y | Y | Y | Y | Y | 5359 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 109 | Y | Y | Y | Y | Y | 5360 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 110 | Y | Y | Y | Y | Y | 5361 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 111 | Y | Y | Y | Y | Y | 5362 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 112 | Y | Y | Y | Y | Y | 5363 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 113 | Y | Y | Y | Y | Y | 5364 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 114 | Y | Y | Y | Y | Y | 5365 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 115 | Y | Y | Y | Y | Y | 5366 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 116 | Y | Y | Y | Y | Y | 5367 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 117 | Y | Y | Y | Y | Y | 5368 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 118 | Y | Y | Y | Y | Y | 5369 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 119 | Y | Y | Y | Y | Y | 5370 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 120 | Y | Y | Y | Y | Y | 5371 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 121 | Y | Y | Y | Y | Y | 5372 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 122 | Y | Y | Y | Y | Y | 5373 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Parameter 123 | Y | Y | Y | Y | Y | 5374 | --- | 1 | INT16U | RW | --- | 0
|  |  | Command Status | Y | Y | Y | Y | Y | 5375 | --- | 1 | INT16U | R | 0 – 32767 | 0
|  |  | Command Result | Y | Y | Y | Y | Y | 5376 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 001 | Y | Y | Y | Y | Y | 5377 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 002 | Y | Y | Y | Y | Y | 5378 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 003 | Y | Y | Y | Y | Y | 5379 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 004 | Y | Y | Y | Y | Y | 5380 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 005 | Y | Y | Y | Y | Y | 5381 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 006 | Y | Y | Y | Y | Y | 5382 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 007 | Y | Y | Y | Y | Y | 5383 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 008 | Y | Y | Y | Y | Y | 5384 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 009 | Y | Y | Y | Y | Y | 5385 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 010 | Y | Y | Y | Y | Y | 5386 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 011 | Y | Y | Y | Y | Y | 5387 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 012 | Y | Y | Y | Y | Y | 5388 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 013 | Y | Y | Y | Y | Y | 5389 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 014 | Y | Y | Y | Y | Y | 5390 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 015 | Y | Y | Y | Y | Y | 5391 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 016 | Y | Y | Y | Y | Y | 5392 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 017 | Y | Y | Y | Y | Y | 5393 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 018 | Y | Y | Y | Y | Y | 5394 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 019 | Y | Y | Y | Y | Y | 5395 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 020 | Y | Y | Y | Y | Y | 5396 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 021 | Y | Y | Y | Y | Y | 5397 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 022 | Y | Y | Y | Y | Y | 5398 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 023 | Y | Y | Y | Y | Y | 5399 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 024 | Y | Y | Y | Y | Y | 5400 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 025 | Y | Y | Y | Y | Y | 5401 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 026 | Y | Y | Y | Y | Y | 5402 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 027 | Y | Y | Y | Y | Y | 5403 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 028 | Y | Y | Y | Y | Y | 5404 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 029 | Y | Y | Y | Y | Y | 5405 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 030 | Y | Y | Y | Y | Y | 5406 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 031 | Y | Y | Y | Y | Y | 5407 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 032 | Y | Y | Y | Y | Y | 5408 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 033 | Y | Y | Y | Y | Y | 5409 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 034 | Y | Y | Y | Y | Y | 5410 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 035 | Y | Y | Y | Y | Y | 5411 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 036 | Y | Y | Y | Y | Y | 5412 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 037 | Y | Y | Y | Y | Y | 5413 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 038 | Y | Y | Y | Y | Y | 5414 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 039 | Y | Y | Y | Y | Y | 5415 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 040 | Y | Y | Y | Y | Y | 5416 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 041 | Y | Y | Y | Y | Y | 5417 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 042 | Y | Y | Y | Y | Y | 5418 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 043 | Y | Y | Y | Y | Y | 5419 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 044 | Y | Y | Y | Y | Y | 5420 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 045 | Y | Y | Y | Y | Y | 5421 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 046 | Y | Y | Y | Y | Y | 5422 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 047 | Y | Y | Y | Y | Y | 5423 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 048 | Y | Y | Y | Y | Y | 5424 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 049 | Y | Y | Y | Y | Y | 5425 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 050 | Y | Y | Y | Y | Y | 5426 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 051 | Y | Y | Y | Y | Y | 5427 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 052 | Y | Y | Y | Y | Y | 5428 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 053 | Y | Y | Y | Y | Y | 5429 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 054 | Y | Y | Y | Y | Y | 5430 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 055 | Y | Y | Y | Y | Y | 5431 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 056 | Y | Y | Y | Y | Y | 5432 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 057 | Y | Y | Y | Y | Y | 5433 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 058 | Y | Y | Y | Y | Y | 5434 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 059 | Y | Y | Y | Y | Y | 5435 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 060 | Y | Y | Y | Y | Y | 5436 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 061 | Y | Y | Y | Y | Y | 5437 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 062 | Y | Y | Y | Y | Y | 5438 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 063 | Y | Y | Y | Y | Y | 5439 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 064 | Y | Y | Y | Y | Y | 5440 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 065 | Y | Y | Y | Y | Y | 5441 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 066 | Y | Y | Y | Y | Y | 5442 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 067 | Y | Y | Y | Y | Y | 5443 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 068 | Y | Y | Y | Y | Y | 5444 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 069 | Y | Y | Y | Y | Y | 5445 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 070 | Y | Y | Y | Y | Y | 5446 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 071 | Y | Y | Y | Y | Y | 5447 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 072 | Y | Y | Y | Y | Y | 5448 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 073 | Y | Y | Y | Y | Y | 5449 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 074 | Y | Y | Y | Y | Y | 5450 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 075 | Y | Y | Y | Y | Y | 5451 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 076 | Y | Y | Y | Y | Y | 5452 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 077 | Y | Y | Y | Y | Y | 5453 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 078 | Y | Y | Y | Y | Y | 5454 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 079 | Y | Y | Y | Y | Y | 5455 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 080 | Y | Y | Y | Y | Y | 5456 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 081 | Y | Y | Y | Y | Y | 5457 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 082 | Y | Y | Y | Y | Y | 5458 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 083 | Y | Y | Y | Y | Y | 5459 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 084 | Y | Y | Y | Y | Y | 5460 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 085 | Y | Y | Y | Y | Y | 5461 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 086 | Y | Y | Y | Y | Y | 5462 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 087 | Y | Y | Y | Y | Y | 5463 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 088 | Y | Y | Y | Y | Y | 5464 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 089 | Y | Y | Y | Y | Y | 5465 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 090 | Y | Y | Y | Y | Y | 5466 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 091 | Y | Y | Y | Y | Y | 5467 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 092 | Y | Y | Y | Y | Y | 5468 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 093 | Y | Y | Y | Y | Y | 5469 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 094 | Y | Y | Y | Y | Y | 5470 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 095 | Y | Y | Y | Y | Y | 5471 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 096 | Y | Y | Y | Y | Y | 5472 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 097 | Y | Y | Y | Y | Y | 5473 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 098 | Y | Y | Y | Y | Y | 5474 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 099 | Y | Y | Y | Y | Y | 5475 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 100 | Y | Y | Y | Y | Y | 5476 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 101 | Y | Y | Y | Y | Y | 5477 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 102 | Y | Y | Y | Y | Y | 5478 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 103 | Y | Y | Y | Y | Y | 5479 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 104 | Y | Y | Y | Y | Y | 5480 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 105 | Y | Y | Y | Y | Y | 5481 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 106 | Y | Y | Y | Y | Y | 5482 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 107 | Y | Y | Y | Y | Y | 5483 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 108 | Y | Y | Y | Y | Y | 5484 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 109 | Y | Y | Y | Y | Y | 5485 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 110 | Y | Y | Y | Y | Y | 5486 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 111 | Y | Y | Y | Y | Y | 5487 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 112 | Y | Y | Y | Y | Y | 5488 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 113 | Y | Y | Y | Y | Y | 5489 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 114 | Y | Y | Y | Y | Y | 5490 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 115 | Y | Y | Y | Y | Y | 5491 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 116 | Y | Y | Y | Y | Y | 5492 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 117 | Y | Y | Y | Y | Y | 5493 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 118 | Y | Y | Y | Y | Y | 5494 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 119 | Y | Y | Y | Y | Y | 5495 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 120 | Y | Y | Y | Y | Y | 5496 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 121 | Y | Y | Y | Y | Y | 5497 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 122 | Y | Y | Y | Y | Y | 5498 | --- | 1 | INT16U | R | --- | 0
|  |  | Command Data 123 | Y | Y | Y | Y | Y | 5499 | --- | 1 | INT16U | R | --- | 0
| Command Semaphore | [7 empty] | 5680 | --- | 1 | INT16U | RW | --- | ---
HMI |  |  |  | Y | Y | Y | Y | Y | 6000 | --- |  | --- | --- | --- | ---
| Setup |  |  | Y | Y | Y | Y | Y | 6000 | --- |  | --- | --- | --- | ---
|  | Basic HMI Setup |  | Y | Y | Y | Y | Y | 6000 | --- |  | --- | --- | --- | ---
|  |  | HMI Model Present | Y | Y | Y | Y | Y | 6000 | --- | 1 | INT16U | R | 0 – 1 | 0 | 0 = No HMI Connected 1 = 128x128 Dot Matrix LCD HMI connected
|  |  | HMI Contrast Setting | Y | Y | Y | Y | Y | 6001 | --- | 1 | INT16U | RWC | 1 – 9 | 5 | 1 = Brightest…9 = Dimmest
|  |  | HMI Brightness Setting | [5 empty] | 6002 | --- | 1 | INT16U | RWC | 0 – 7 | 0 | 0 = Brightest...7 = Dimmest
|  |  | HMI Language | Y | Y | Y | Y | Y | 6003 | --- | 1 | INT16U | RWC | 0 – 12 | 0 | 0 = EnglishUS 1 = EnglishUK 2 = French 3 = Spanish 4 = German 5 = Italian 6 = Polish 7 = Portuguese 8 = Turkish 9 = Chinese 10 = Russian 11 = Arabic 12 = Dutch
|  |  | HMI Date Format | Y | Y | Y | Y | Y | 6004 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = MM/DD/YYYY 1 = YYYY/MM/DD 2 = DD/MM/YYYY
|  |  | HMI Time Format | Y | Y | Y | Y | Y | 6005 | --- | 1 | INT16U | RWC | 0 – 1 | 0 | 0 = 2400hr 1 = AM/PM
|  |  | HMI IEC/IEEE Mode | Y | Y | Y | Y | Y | 6006 | --- | 1 | INT16U | RWC | 0 – 1 | 0 | 0 = IEC 1 = IEEE
|  |  | HMI Screen Timeout | Y | Y | Y | Y | Y | 6007 | minutes | 1 | INT16U | RWC | 0 – 60 | 0 | 0 = disabled
|  |  | HMI Backlight Timeout | Y | Y | Y | Y | Y | 6008 | minutes | 1 | INT16U | RWC | 0 – 60 | 5 | 0 = disabled
|  | Alternate Languages Available | [6 empty] | 6079 | --- |  | --- | --- | --- | ---
|  |  | HMI Language 01 | Y | Y | Y | Y | Y | 6079 | --- | 1 | INT16U | R | 0 – 20 | 0 | 0 = EnglishUS EnglishUS is always available. 1 = EnglishUK 2 = French 3 = Spanish 4 = German 5 = Italian 6 = Polish 7 = Portuguese 8 = Turkish 9 = Chinese 10 = Russian 11 = Arabic 12 = Dutch
|  |  | HMI Language 02 | Y | Y | Y | Y | Y | 6080 | --- | 1 | INT16U | R | 0 – 20 | 0
|  |  | HMI Language 03 | Y | Y | Y | Y | Y | 6081 | --- | 1 | INT16U | R | 0 – 20 | 0
|  |  | HMI Language 04 | Y | Y | Y | Y | Y | 6082 | --- | 1 | INT16U | R | 0 – 20 | 0
|  |  | HMI Language 05 | Y | Y | Y | Y | Y | 6083 | --- | 1 | INT16U | R | 0 – 20 | 0
|  |  | HMI Language 06 | Y | Y | Y | Y | Y | 6084 | --- | 1 | INT16U | R | 0 – 20 | 0
|  |  | HMI Language 07 | Y | Y | Y | Y | Y | 6085 | --- | 1 | INT16U | R | 0 – 20 | 0
|  |  | HMI Language 08 | Y | Y | Y | Y | Y | 6086 | --- | 1 | INT16U | R | 0 – 20 | 0
Communications |  |  |  | Y | Y | Y |  |  |  | --- |  | --- | --- | --- | ---
| RS-485 |  |  | Y | Y | Y |  |  |  | --- |  | --- | --- | --- | ---
|  | RS-485 Base Unit |  | Y | Y | Y |  |  |  | --- |  | --- | --- | --- | ---
|  |  | RS-485 Comm Port (M/S) Protocol | Y | Y | Y |  |  | 6500 | --- | 1 | INT16U | RWC | 0 – 3 | 0 | 0 = Modbus 1 = Jbus 2 = Modbus ASCII 8-Bit 3 = Modbus ASCII 7-Bit
|  |  | RS-485 Comm Port (M/S) Address | Y | Y | Y |  |  | 6501 | --- | 1 | INT16U | RWC | 1 – 255 | 1 | Valid Addresses: Modbus: 1 – 247 Jbus: 1 – 255
|  |  | RS-485 Comm Port (M/S) Baud Rate | Y | Y | Y |  |  | 6502 | --- | 1 | INT16U | RWC | 0 – 2 | 1 | 0 = 9600 1 = 19200 2 = 38400
|  |  | RS-485 Comm Port (M/S) Parity | Y | Y | Y |  |  | 6503 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = Even 1 = Odd 2 = None
Inputs & Outputs |  |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
| Multi-tariff Setup |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Number of Multi-tariff Rates Active |  |  | Y | Y | Y | Y | 7012 | --- | 1 | INT16U | RWC | 1 – 4 | 1
|  | Number of Digital Inputs Used to Control Multi-tariff |  |  | Y | Y | Y | Y | 7013 | --- | 1 | INT16U | RWC | 1 – 4 | 1
| Demand Sync Setup |  |  |  | Y | Y | Y | Y | 7020 | --- |  | --- | --- | --- | ---
|  | Digital Input Associations With Demand Systems |  |  | Y | Y | Y | Y | 7020 | --- |  | --- | --- | --- | ---
|  |  | Demand System 1 (Power) |  | Y | Y | Y | Y | 7020 | --- | 1 | INT16U | RWC | 0 – 68 | 0
|  |  | Demand System 2 (Current) |  | Y | Y | Y | Y | 7021 | --- | 1 | INT16U | RWC | 0 – 68 | 0
|  | Digital Output Associations With Demand Systems |  |  | Y | Y | Y | Y | 7026 | --- |  | --- | --- | --- | ---
|  |  | Demand System 1 (Power) |  | Y | Y | Y | Y | 7026 | --- | 1 | INT16U | RWC | 0 – 68 | 0
|  |  | Demand System 2 (Current) |  | Y | Y | Y | Y | 7027 | --- | 1 | INT16U | RWC | 0 – 68 | 0
| Digital Inputs Setup |  |  |  | Y | Y | Y | Y | 7273 | --- |  | --- | --- | --- | ---
|  | Base Unit - Digital Input DI1 |  |  | Y | Y | Y | Y | 7273 | --- |  | --- | --- | --- | ---
|  |  | Type |  | Y | Y | Y | Y | 7273 | --- | 1 | INT16U | R | 100 – 199 | 102 | First digit (1) indicates point is digital input Second digit indicates the digital input module type Second digit can be used to identify specific hardware options. 0 = Generic digital input Third digit indicates input type 1 = AC 2 = DC
|  |  | Control Mode |  | Y | Y | Y | Y | 7274 | --- | 1 | INT16U | RWC | 0 – 5 | 0 | 0 = Normal (Alarm) 1 = Demand Interval Sync Pulse 2 = Multi-tariff Control 3 = Input Metering 4 = Conditional Energy Control 5 = Incremental Energy Reset
|  |  | Label |  | Y | Y | Y | Y | 7275 | --- | 20 | UTF8 | RWC | --- | "Digital Input DI1"
|  |  | Debounce Time |  | Y | Y | Y | Y | 7295 | msec | 1 | INT16U | RWC | 10 – 1000 | 10 | Must be entered in increments of 10ms.
|  | Base Unit - Digital Input DI2 |  |  | Y | Y | Y | Y | 7297 | --- |  | --- | --- | --- | ---
|  |  | Type |  | Y | Y | Y | Y | 7297 | --- | 1 | INT16U | R | 100 – 199 | 102
|  |  | Control Mode |  | Y | Y | Y | Y | 7298 | --- | 1 | INT16U | RWC | 0 – 5 | 0
|  |  | Label |  | Y | Y | Y | Y | 7299 | --- | 20 | UTF8 | RWC | --- | "Digital Input DI2"
|  |  | Debounce Time |  | Y | Y | Y | Y | 7319 | msec | 1 | INT16U | RWC | 10 – 1000 | 10 | Must be entered in increments of 10ms.
| Digital Inputs Status |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | On/Off Status |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Digital Input Status – Base Unit |  | Y | Y | Y | Y | 8905 | --- | 2 | BITMAP | R | 0x00000000 – 0x0000000F | 0x00000000
|  | Base Unit - Digital Input DI1 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Count |  | Y | Y | Y | Y | 8915 | --- | 2 | INT32U | R | --- | 0
|  |  | On Time |  | Y | Y | Y | Y | 8917 | seconds | 2 | INT32U | R | --- | 0
|  | Base Unit - Digital Input DI2 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Count |  | Y | Y | Y | Y | 8919 | --- | 2 | INT32U | R | --- | 0
|  |  | On Time |  | Y | Y | Y | Y | 8921 | seconds | 2 | INT32U | R | --- | 0
| Digital Outputs Setup |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Base Unit - Digital Output DO1 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Type |  | Y | Y | Y | Y | 9187 | --- | 1 | INT16U | R | 201 – 299 | 201 | First digit (2) indicates point is digital output Second digit indicates module type 0 = Generic Digital output Third digit indicates output type 1 = solid state relay 2 = electromechanical relay
|  |  | Label |  | Y | Y | Y | Y | 9188 | --- | 20 | UTF8 | RWC | --- | "Digital Output DO1"
|  |  | Enable/Disable | [5 empty] | 9208 | --- | 1 | INT16U | RWC | 0 – 1 | 1 | 0 = Disable, 1 = Enable
|  |  | Behavioral Mode |  | Y | Y | Y | Y | 9209 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = Normal (forced by a control mode of Energy) 1 = Timed (forced by a control mode of Demand Sync) 2 = Coil Hold
|  |  | On Time For Timed Mode |  | Y | Y | Y | Y | 9210 | seconds | 1 | INT16U | RWC | --- | 1 | The time for the output to remain energized when the output is energized in timed mode.
|  | Base Unit - Digital Output DO2 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Type |  | Y | Y | Y | Y | 9211 | --- | 1 | INT16U | R | 201 – 299 | 201
|  |  | Label |  | Y | Y | Y | Y | 9212 | --- | 20 | UTF8 | RWC | --- | "Digital Output DO2"
|  |  | Enable/Disable | [5 empty] | 9232 | --- | 1 | INT16U | RWC | 0 – 1 | 1 | 0 = Disable, 1 = Enable
|  |  | Behavioral Mode |  | Y | Y | Y | Y | 9233 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = Normal 1 = Timed 2 = Coil Hold
|  |  | On Time For Timed Mode |  | Y | Y | Y | Y | 9234 | seconds | 1 | INT16U | RWC | --- | 1 | The time for the output to remain energized when the output is energized in timed mode.
| Relay | Base Unit - Digital Output DO3 |  |  |  | Y |  | Y |  | --- |  | --- | --- | --- | ---
|  |  | Type |  |  | Y |  | Y | 9235 | --- | 1 | INT16U | R | 201 – 299 | 202
|  |  | Label |  |  | Y |  | Y | 9236 | --- | 20 | UTF8 | RWC | --- | "Relay Output 01"
|  |  | Enable/Disable | [5 empty] | 9256 | --- | 1 | INT16U | RWC | 0 – 1 | 1 | 0 = Disable, 1 = Enable
|  |  | Behavioral Mode |  |  | Y |  | Y | 9257 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = Normal 1 = Timed 2 = Coil Hold
|  |  | On Time For Timed Mode |  |  | Y |  | Y | 9258 | seconds | 1 | INT16U | RWC | --- | 1 | The time for the output to remain energized when the output is energized in timed mode.
| Relay | Base Unit - Digital Output DO4 |  |  |  | Y |  | Y |  | --- |  | --- | --- | --- | ---
|  |  | Type |  |  | Y |  | Y | 9259 | --- | 1 | INT16U | R | 201 – 299 | 202
|  |  | Label |  |  | Y |  | Y | 9260 | --- | 20 | UTF8 | RWC | --- | "Relay output 02"
|  |  | Enable/Disable | [5 empty] | 9280 | --- | 1 | INT16U | RWC | 0 – 1 | 1 | 0 = Disable, 1 = Enable
|  |  | Behavioral Mode |  |  | Y |  | Y | 9281 | --- | 1 | INT16U | RWC | 0 – 2 | 0 | 0 = Normal 1 = Timed 2 = Coil Hold
|  |  | On Time For Timed Mode |  |  | Y |  | Y | 9282 | seconds | 1 | INT16U | RWC | --- | 1 | The time for the output to remain energized when the output is energized in timed mode.
| Digital Outputs Status |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | On/Off Status |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Digital Output Status – Base Unit |  | Y | Y | Y | Y | 9667 | --- | 1 | BITMAP | R | 0x0000 – 0x000F | 0x0000
|  |  | Digital Output Status – Option Slot A | [5 empty] | 9668 | --- | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000
|  |  | Digital Output Status – Option Slot B | [5 empty] | 9669 | --- | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000
|  |  | Digital Output Status – Option Slot C | [5 empty] | 9670 | --- | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000
|  |  | Digital Output Status – Option Slot D | [5 empty] | 9671 | --- | 1 | BITMAP | R | 0x0000 – 0xFFFF | 0x0000
|  | Base Unit - Digital Output DO1 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Operating Mode Status |  | Y | Y | Y | Y | 9672 | --- | 1 | INT16U | R | 0 – 1 | 0 | 0 = Normal, 1 = Override Operating Mode is changed by command. Override is considered a temporary condition used for troubleshooting. The state is volatile. That is to say that if the meter resets, the digital output will revert to normal operation.
|  |  | Control Mode Status |  | Y | Y | Y | Y | 9673 | --- | 1 | INT16U | R | 0 – 3 | 0 | 0 = External 1 = Demand Sync 2 = Alarm 3 = Energy (Energy control modes are not available for electromechanical relays.)
|  |  | Behavioral Mode Status |  | Y | Y | Y | Y | 9674 | --- | 1 | INT16U | R | 0 – 2 | 0 | 0 = Normal 1 = Timed 2 = Coil Hold (Behavioral Mode will be forced to Normal when in Override Operating Mode.)
|  |  | Count |  | Y | Y | Y | Y | 9675 | --- | 2 | INT32U | R | --- | 0
|  |  | On Time |  | Y | Y | Y | Y | 9677 | seconds | 2 | INT32U | R | --- | 0
|  | Base Unit - Digital Output DO2 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Operating Mode Status |  | Y | Y | Y | Y | 9680 | --- | 1 | INT16U | R | 0 – 1 | 0
|  |  | Control Mode Status |  | Y | Y | Y | Y | 9681 | --- | 1 | INT16U | R | 0 – 3 | 0
|  |  | Behavioral Mode Status |  | Y | Y | Y | Y | 9682 | --- | 1 | INT16U | R | 0 – 2 | 0
|  |  | Count |  | Y | Y | Y | Y | 9683 | --- | 2 | INT32U | R | --- | 0
|  |  | On Time |  | Y | Y | Y | Y | 9685 | seconds | 2 | INT32U | R | --- | 0
| Relay | Base Unit - Digital Output DO3 |  |  |  | Y |  | Y |  | --- |  | --- | --- | --- | ---
|  |  | Operating Mode Status |  |  | Y |  | Y | 9688 | --- | 1 | INT16U | R | 0 – 1 | 0
|  |  | Control Mode Status |  |  | Y |  | Y | 9689 | --- | 1 | INT16U | R | 0 – 3 | 0
|  |  | Behavioral Mode Status |  |  | Y |  | Y | 9690 | --- | 1 | INT16U | R | 0 – 2 | 0
|  |  | Count |  |  | Y |  | Y | 9691 | --- | 2 | INT32U | R | --- | 0
|  |  | On Time |  |  | Y |  | Y | 9693 | seconds | 2 | INT32U | R | --- | 0
| Relay | Base Unit - Digital Output DO4 |  |  |  | Y |  | Y |  | --- |  | --- | --- | --- | ---
|  |  | Operating Mode Status |  |  | Y |  | Y | 9696 | --- | 1 | INT16U | R | 0 – 1 | 0
|  |  | Control Mode Status |  |  | Y |  | Y | 9697 | --- | 1 | INT16U | R | 0 – 3 | 0
|  |  | Behavioral Mode Status |  |  | Y |  | Y | 9698 | --- | 1 | INT16U | R | 0 – 2 | 0
|  |  | Count |  |  | Y |  | Y | 9699 | --- | 2 | INT32U | R | --- | 0
|  |  | On Time |  |  | Y |  | Y | 9701 | seconds | 2 | INT32U | R | --- | 0
Alarms |  |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
| Alarm Status |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Detected Priority Status |  | Y | Y | Y | Y | Y | 11010 | --- |  | --- | --- | --- | ---
|  |  | Detected Priority Status Bitmap | Y | Y | Y | Y | Y | 11010 | --- | 1 | BITMAP | R | 0x0000 - 0x001F | 0 | Bit 01 = 1 if any priority 1-3 alarm is active Bit 02 = 1 if a “High” (1) priority alarm is active Bit 03 = 1 if a “Medium” (2) priority alarm is active Bit 04 = 1 if a “Low” (3) priority alarm is active Bit 05 = 1 if a "None" (0) priority alarm is active
|  | Enabled Alarm Bitmaps |  | Y | Y | Y | Y | Y | 11040 | --- |  | --- | --- | --- | ---
|  |  | Standard – 1 second 1 | Y | Y | Y | Y | Y | 11040 | --- | 1 | BITMAP | R |  | 0 | 0 = Disabled; 1 = Enabled
|  |  | Standard – 1 second 2 | Y | Y | Y | Y | Y | 11041 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – 1 second 3 | Y | Y | Y | Y | Y | 11042 | --- | 1 | BITMAP | R |  | 0
|  |  | Custom – 1 second | Y | Y | Y | Y | Y | 11043 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – High Speed 1 | Y | Y | Y | Y | Y | 11044 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – High Speed 2 | Y | Y | Y | Y | Y | 11045 | --- | 1 | BITMAP | R |  | 0
|  |  | Custom – High Speed | Y | Y | Y | Y | Y | 11046 | --- | 1 | BITMAP | R |  | 0
|  |  | Disturbance | Y | Y | Y | Y | Y | 11047 | --- | 1 | BITMAP | R |  | 0
|  |  | Transient | Y | Y | Y | Y | Y | 11048 | --- | 1 | BITMAP | R |  | 0
|  |  | Waveshape | Y | Y | Y | Y | Y | 11049 | --- | 1 | BITMAP | R |  | 0
|  |  | Unary | Y | Y | Y | Y | Y | 11050 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 1 | Y | Y | Y | Y | Y | 11051 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 2 | Y | Y | Y | Y | Y | 11052 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 3 | Y | Y | Y | Y | Y | 11053 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 4 | Y | Y | Y | Y | Y | 11054 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 5 | Y | Y | Y | Y | Y | 11055 | --- | 1 | BITMAP | R |  | 0
|  |  | Binary | Y | Y | Y | Y | Y | 11056 | --- | 1 | BITMAP | R |  | 0
|  |  | Time_of_day | Y | Y | Y | Y | Y | 11057 | --- | 1 | BITMAP | R |  | 0
|  |  | Logic | Y | Y | Y | Y | Y | 11058 | --- | 1 | BITMAP | R |  | 0
|  | Detected Alarm Bitmaps |  | Y | Y | Y | Y | Y | 11059 | --- |  | --- | --- | --- | ---
|  |  | Standard – 1 second Group 1 | Y | Y | Y | Y | Y | 11059 | --- | 1 | BITMAP | R |  | 0 | 0 = Not Detected; 1 = Detected
|  |  | Standard – 1 second Group 2 | Y | Y | Y | Y | Y | 11060 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – 1 second Group 3 | Y | Y | Y | Y | Y | 11061 | --- | 1 | BITMAP | R |  | 0
|  |  | Custom – 1 second | Y | Y | Y | Y | Y | 11062 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – High Speed Group 1 | Y | Y | Y | Y | Y | 11063 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – High Speed Group 2 | Y | Y | Y | Y | Y | 11064 | --- | 1 | BITMAP | R |  | 0
|  |  | Custom – High Speed | Y | Y | Y | Y | Y | 11065 | --- | 1 | BITMAP | R |  | 0
|  |  | Disturbance | Y | Y | Y | Y | Y | 11066 | --- | 1 | BITMAP | R |  | 0
|  |  | Transient | Y | Y | Y | Y | Y | 11067 | --- | 1 | BITMAP | R |  | 0
|  |  | Waveshape | Y | Y | Y | Y | Y | 11068 | --- | 1 | BITMAP | R |  | 0
|  |  | Unary | Y | Y | Y | Y | Y | 11069 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital Group 1 | Y | Y | Y | Y | Y | 11070 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital Group 2 | Y | Y | Y | Y | Y | 11071 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital Group 3 | Y | Y | Y | Y | Y | 11072 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital Group 4 | Y | Y | Y | Y | Y | 11073 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital Group 5 | Y | Y | Y | Y | Y | 11074 | --- | 1 | BITMAP | R |  | 0
|  |  | Binary | Y | Y | Y | Y | Y | 11075 | --- | 1 | BITMAP | R |  | 0
|  |  | Time_of_day | Y | Y | Y | Y | Y | 11076 | --- | 1 | BITMAP | R |  | 0
|  |  | Logic | Y | Y | Y | Y | Y | 11077 | --- | 1 | BITMAP | R |  | 0
|  | Unacknowledged High Priority Alarm Bitmaps |  | Y | Y | Y | Y | Y | 11078 | --- |  | --- | --- | --- | ---
|  |  | Standard – 1 second 1 | Y | Y | Y | Y | Y | 11078 | --- | 1 | BITMAP | R |  | 0 | 0 = Acknowledged; 1 = Unacknowledged
|  |  | Standard – 1 second 2 | Y | Y | Y | Y | Y | 11079 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – 1 second 3 | Y | Y | Y | Y | Y | 11080 | --- | 1 | BITMAP | R |  | 0
|  |  | Custom – 1 second | Y | Y | Y | Y | Y | 11081 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – High Speed 1 | Y | Y | Y | Y | Y | 11082 | --- | 1 | BITMAP | R |  | 0
|  |  | Standard – High Speed 2 | Y | Y | Y | Y | Y | 11083 | --- | 1 | BITMAP | R |  | 0
|  |  | Custom – High Speed | Y | Y | Y | Y | Y | 11084 | --- | 1 | BITMAP | R |  | 0
|  |  | Disturbance | Y | Y | Y | Y | Y | 11085 | --- | 1 | BITMAP | R |  | 0
|  |  | Transient | Y | Y | Y | Y | Y | 11086 | --- | 1 | BITMAP | R |  | 0
|  |  | Waveshape | Y | Y | Y | Y | Y | 11087 | --- | 1 | BITMAP | R |  | 0
|  |  | Unary | Y | Y | Y | Y | Y | 11088 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 1 | Y | Y | Y | Y | Y | 11089 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 2 | Y | Y | Y | Y | Y | 11090 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 3 | Y | Y | Y | Y | Y | 11091 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 4 | Y | Y | Y | Y | Y | 11092 | --- | 1 | BITMAP | R |  | 0
|  |  | Digital 5 | Y | Y | Y | Y | Y | 11093 | --- | 1 | BITMAP | R |  | 0
|  |  | Binary | Y | Y | Y | Y | Y | 11094 | --- | 1 | BITMAP | R |  | 0
|  |  | Time_of_day | Y | Y | Y | Y | Y | 11095 | --- | 1 | BITMAP | R |  | 0
|  |  | Logic | Y | Y | Y | Y | Y | 11096 | --- | 1 | BITMAP | R |  | 0
| Alarm Event Queue |  |  | Y | Y | Y | Y | Y | 11111 | --- |  | --- | --- | --- | ---
|  |  | Version of Event Queue | Y | Y | Y | Y | Y | 11111 | --- | 1 | INT16U | R |  | 0
|  |  | Event Types to Log | [5 empty] | 11112 |  | 1 | INT16U | RWC | 0x0000 - 0xFFFF | 0xFFFF
|  |  | Size of Event Queue | Y | Y | Y | Y | Y | 11113 | --- | 1 | INT16U | R |  | 100
|  |  | Number of Entries in Event Queue | Y | Y | Y | Y | Y | 11114 | --- | 1 | INT16U | R | 0 – 100 | 0
|  |  | Entry Number of Most Recent Event | Y | Y | Y | Y | Y | 11115 | --- | 1 | INT16U | R |  | 0 | Rolls over from 65535 to 0.
|  | Entry 001 |  | Y | Y | Y | Y | Y | 11116 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11116 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11117 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11121 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11122 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11123 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11127 | --- | 1 | INT16U | R |  | N/A
|  | Entry 002 |  | Y | Y | Y | Y | Y | 11128 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11128 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11129 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11133 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11134 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11135 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11139 | --- | 1 | INT16U | R |  | N/A
|  | Entry 003 |  | Y | Y | Y | Y | Y | 11140 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11140 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11141 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11145 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11146 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11147 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11151 | --- | 1 | INT16U | R |  | N/A
|  | Entry 004 |  | Y | Y | Y | Y | Y | 11152 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11152 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11153 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11157 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11158 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11159 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11163 | --- | 1 | INT16U | R |  | N/A
|  | Entry 005 |  | Y | Y | Y | Y | Y | 11164 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11164 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11165 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11169 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11170 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11171 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11175 | --- | 1 | INT16U | R |  | N/A
|  | Entry 006 |  | Y | Y | Y | Y | Y | 11176 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11176 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11177 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11181 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11182 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11183 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11187 | --- | 1 | INT16U | R |  | N/A
|  | Entry 007 |  | Y | Y | Y | Y | Y | 11188 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11188 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11189 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11193 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11194 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11195 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11199 | --- | 1 | INT16U | R |  | N/A
|  | Entry 008 |  | Y | Y | Y | Y | Y | 11200 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11200 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11201 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11205 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11206 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11207 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11211 | --- | 1 | INT16U | R |  | N/A
|  | Entry 009 |  | Y | Y | Y | Y | Y | 11212 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11212 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11213 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11217 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11218 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11219 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11223 | --- | 1 | INT16U | R |  | N/A
|  | Entry 010 |  | Y | Y | Y | Y | Y | 11224 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11224 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11225 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11229 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11230 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11231 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11235 | --- | 1 | INT16U | R |  | N/A
|  | Entry 011 |  | Y | Y | Y | Y | Y | 11236 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11236 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11237 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11241 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11242 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11243 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11247 | --- | 1 | INT16U | R |  | N/A
|  | Entry 012 |  | Y | Y | Y | Y | Y | 11248 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11248 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11249 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11253 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11254 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11255 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11259 | --- | 1 | INT16U | R |  | N/A
|  | Entry 013 |  | Y | Y | Y | Y | Y | 11260 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11260 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11261 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11265 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11266 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11267 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11271 | --- | 1 | INT16U | R |  | N/A
|  | Entry 014 |  | Y | Y | Y | Y | Y | 11272 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11272 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11273 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11277 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11278 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11279 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11283 | --- | 1 | INT16U | R |  | N/A
|  | Entry 015 |  | Y | Y | Y | Y | Y | 11284 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11284 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11285 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11289 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11290 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11291 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11295 | --- | 1 | INT16U | R |  | N/A
|  | Entry 016 |  | Y | Y | Y | Y | Y | 11296 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11296 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11297 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11301 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11302 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11303 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11307 | --- | 1 | INT16U | R |  | N/A
|  | Entry 017 |  | Y | Y | Y | Y | Y | 11308 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11308 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11309 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11313 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11314 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11315 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11319 | --- | 1 | INT16U | R |  | N/A
|  | Entry 018 |  | Y | Y | Y | Y | Y | 11320 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11320 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11321 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11325 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11326 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11327 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11331 | --- | 1 | INT16U | R |  | N/A
|  | Entry 019 |  | Y | Y | Y | Y | Y | 11332 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11332 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11333 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11337 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11338 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11339 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11343 | --- | 1 | INT16U | R |  | N/A
|  | Entry 020 |  | Y | Y | Y | Y | Y | 11344 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11344 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11345 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11349 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11350 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11351 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11355 | --- | 1 | INT16U | R |  | N/A
|  | Entry 021 |  | Y | Y | Y | Y | Y | 11356 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11356 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11357 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11361 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11362 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11363 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11367 | --- | 1 | INT16U | R |  | N/A
|  | Entry 022 |  | Y | Y | Y | Y | Y | 11368 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11368 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11369 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11373 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11374 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11375 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11379 | --- | 1 | INT16U | R |  | N/A
|  | Entry 023 |  | Y | Y | Y | Y | Y | 11380 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11380 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11381 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11385 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11386 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11387 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11391 | --- | 1 | INT16U | R |  | N/A
|  | Entry 024 |  | Y | Y | Y | Y | Y | 11392 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11392 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11393 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11397 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11398 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11399 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11403 | --- | 1 | INT16U | R |  | N/A
|  | Entry 025 |  | Y | Y | Y | Y | Y | 11404 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11404 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11405 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11409 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11410 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11411 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11415 | --- | 1 | INT16U | R |  | N/A
|  | Entry 026 |  | Y | Y | Y | Y | Y | 11416 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11416 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11417 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11421 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11422 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11423 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11427 | --- | 1 | INT16U | R |  | N/A
|  | Entry 027 |  | Y | Y | Y | Y | Y | 11428 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11428 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11429 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11433 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11434 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11435 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11439 | --- | 1 | INT16U | R |  | N/A
|  | Entry 028 |  | Y | Y | Y | Y | Y | 11440 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11440 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11441 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11445 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11446 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11447 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11451 | --- | 1 | INT16U | R |  | N/A
|  | Entry 029 |  | Y | Y | Y | Y | Y | 11452 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11452 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11453 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11457 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11458 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11459 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11463 | --- | 1 | INT16U | R |  | N/A
|  | Entry 030 |  | Y | Y | Y | Y | Y | 11464 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11464 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11465 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11469 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11470 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11471 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11475 | --- | 1 | INT16U | R |  | N/A
|  | Entry 031 |  | Y | Y | Y | Y | Y | 11476 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11476 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11477 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11481 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11482 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11483 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11487 | --- | 1 | INT16U | R |  | N/A
|  | Entry 032 |  | Y | Y | Y | Y | Y | 11488 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11488 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11489 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11493 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11494 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11495 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11499 | --- | 1 | INT16U | R |  | N/A
|  | Entry 033 |  | Y | Y | Y | Y | Y | 11500 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11500 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11501 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11505 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11506 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11507 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11511 | --- | 1 | INT16U | R |  | N/A
|  | Entry 034 |  | Y | Y | Y | Y | Y | 11512 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11512 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11513 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11517 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11518 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11519 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11523 | --- | 1 | INT16U | R |  | N/A
|  | Entry 035 |  | Y | Y | Y | Y | Y | 11524 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11524 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11525 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11529 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11530 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11531 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11535 | --- | 1 | INT16U | R |  | N/A
|  | Entry 036 |  | Y | Y | Y | Y | Y | 11536 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11536 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11537 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11541 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11542 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11543 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11547 | --- | 1 | INT16U | R |  | N/A
|  | Entry 037 |  | Y | Y | Y | Y | Y | 11548 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11548 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11549 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11553 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11554 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11555 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11559 | --- | 1 | INT16U | R |  | N/A
|  | Entry 038 |  | Y | Y | Y | Y | Y | 11560 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11560 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11561 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11565 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11566 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11567 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11571 | --- | 1 | INT16U | R |  | N/A
|  | Entry 039 |  | Y | Y | Y | Y | Y | 11572 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11572 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11573 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11577 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11578 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11579 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11583 | --- | 1 | INT16U | R |  | N/A
|  | Entry 040 |  | Y | Y | Y | Y | Y | 11584 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 11584 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 11585 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 11589 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 11590 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 11591 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 11595 | --- | 1 | INT16U | R |  | N/A
[10 empty] | --- |  | --- | --- | --- | ---
| Alarm History Log |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Size of History Log | Y | Y | Y | Y | Y | 12316 | --- | 1 | INT16U | R |  | 25
|  |  | Number of Entries in History Log | Y | Y | Y | Y | Y | 12317 | --- | 1 | INT16U | R |  | 0
|  |  | Entry Number of Most Recent Event | Y | Y | Y | Y | Y | 12318 | --- | 1 | INT16U | R |  | 0 | Value rolls over from 65535 (0xFFFF) to 0.
|  | Entry 001 |  | Y | Y | Y | Y | Y | 12319 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12319 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12320 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12324 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12325 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12326 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12330 | --- | 1 | INT16U | R |  | N/A
|  | Entry 002 |  | Y | Y | Y | Y | Y | 12331 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12331 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12332 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12336 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12337 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12338 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12342 | --- | 1 | INT16U | R |  | N/A
|  | Entry 003 |  | Y | Y | Y | Y | Y | 12343 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12343 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12344 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12348 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12349 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12350 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12354 | --- | 1 | INT16U | R |  | N/A
|  | Entry 004 |  | Y | Y | Y | Y | Y | 12355 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12355 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12356 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12360 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12361 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12362 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12366 | --- | 1 | INT16U | R |  | N/A
|  | Entry 005 |  | Y | Y | Y | Y | Y | 12367 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12367 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12368 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12372 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12373 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12374 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12378 | --- | 1 | INT16U | R |  | N/A
|  | Entry 006 |  | Y | Y | Y | Y | Y | 12379 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12379 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12380 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12384 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12385 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12386 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12390 | --- | 1 | INT16U | R |  | N/A
|  | Entry 007 |  | Y | Y | Y | Y | Y | 12391 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12391 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12392 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12396 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12397 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12398 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12402 | --- | 1 | INT16U | R |  | N/A
|  | Entry 008 |  | Y | Y | Y | Y | Y | 12403 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12403 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12404 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12408 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12409 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12410 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12414 | --- | 1 | INT16U | R |  | N/A
|  | Entry 009 |  | Y | Y | Y | Y | Y | 12415 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12415 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12416 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12420 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12421 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12422 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12426 | --- | 1 | INT16U | R |  | N/A
|  | Entry 010 |  | Y | Y | Y | Y | Y | 12427 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12427 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12428 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12432 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12433 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12434 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12438 | --- | 1 | INT16U | R |  | N/A
|  | Entry 011 |  | Y | Y | Y | Y | Y | 12439 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12439 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12440 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12444 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12445 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12446 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12450 | --- | 1 | INT16U | R |  | N/A
|  | Entry 012 |  | Y | Y | Y | Y | Y | 12451 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12451 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12452 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12456 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12457 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12458 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12462 | --- | 1 | INT16U | R |  | N/A
|  | Entry 013 |  | Y | Y | Y | Y | Y | 12463 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12463 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12464 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12468 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12469 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12470 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12474 | --- | 1 | INT16U | R |  | N/A
|  | Entry 014 |  | Y | Y | Y | Y | Y | 12475 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12475 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12476 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12480 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12481 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12482 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12486 | --- | 1 | INT16U | R |  | N/A
|  | Entry 015 |  | Y | Y | Y | Y | Y | 12487 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12487 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12488 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12492 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12493 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12494 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12498 | --- | 1 | INT16U | R |  | N/A
|  | Entry 016 |  | Y | Y | Y | Y | Y | 12499 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12499 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12500 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12504 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12505 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12506 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12510 | --- | 1 | INT16U | R |  | N/A
|  | Entry 017 |  | Y | Y | Y | Y | Y | 12511 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12511 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12512 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12516 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12517 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12518 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12522 | --- | 1 | INT16U | R |  | N/A
|  | Entry 018 |  | Y | Y | Y | Y | Y | 12523 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12523 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12524 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12528 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12529 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12530 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12534 | --- | 1 | INT16U | R |  | N/A
|  | Entry 019 |  | Y | Y | Y | Y | Y | 12535 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12535 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12536 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12540 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12541 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12542 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12546 | --- | 1 | INT16U | R |  | N/A
|  | Entry 020 |  | Y | Y | Y | Y | Y | 12547 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12547 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12548 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12552 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12553 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12554 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12558 | --- | 1 | INT16U | R |  | N/A
|  | Entry 021 |  | Y | Y | Y | Y | Y | 12559 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12559 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12560 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12564 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12565 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12566 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12570 | --- | 1 | INT16U | R |  | N/A
|  | Entry 022 |  | Y | Y | Y | Y | Y | 12571 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12571 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12572 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12576 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12577 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12578 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12582 | --- | 1 | INT16U | R |  | N/A
|  | Entry 023 |  | Y | Y | Y | Y | Y | 12583 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12583 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12584 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12588 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12589 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12590 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12594 | --- | 1 | INT16U | R |  | N/A
|  | Entry 024 |  | Y | Y | Y | Y | Y | 12595 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12595 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12596 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12600 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12601 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12602 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12606 | --- | 1 | INT16U | R |  | N/A
|  | Entry 025 |  | Y | Y | Y | Y | Y | 12607 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12607 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12608 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12612 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12613 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12614 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12618 | --- | 1 | INT16U | R |  | N/A
|  | Entry 026 |  | Y | Y | Y | Y | Y | 12619 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12619 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12620 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12624 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12625 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12626 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12630 | --- | 1 | INT16U | R |  | N/A
|  | Entry 027 |  | Y | Y | Y | Y | Y | 12631 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12631 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12632 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12636 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12637 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12638 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12642 | --- | 1 | INT16U | R |  | N/A
|  | Entry 028 |  | Y | Y | Y | Y | Y | 12643 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12643 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12644 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12648 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12649 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12650 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12654 | --- | 1 | INT16U | R |  | N/A
|  | Entry 029 |  | Y | Y | Y | Y | Y | 12655 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12655 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12656 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12660 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12661 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12662 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12666 | --- | 1 | INT16U | R |  | N/A
|  | Entry 030 |  | Y | Y | Y | Y | Y | 12667 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12667 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12668 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12672 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12673 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12674 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12678 | --- | 1 | INT16U | R |  | N/A
|  | Entry 031 |  | Y | Y | Y | Y | Y | 12679 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12679 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12680 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12684 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12685 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12686 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12690 | --- | 1 | INT16U | R |  | N/A
|  | Entry 032 |  | Y | Y | Y | Y | Y | 12691 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12691 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12692 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12696 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12697 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12698 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12702 | --- | 1 | INT16U | R |  | N/A
|  | Entry 033 |  | Y | Y | Y | Y | Y | 12703 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12703 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12704 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12708 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12709 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12710 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12714 | --- | 1 | INT16U | R |  | N/A
|  | Entry 034 |  | Y | Y | Y | Y | Y | 12715 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12715 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12716 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12720 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12721 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12722 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12726 | --- | 1 | INT16U | R |  | N/A
|  | Entry 035 |  | Y | Y | Y | Y | Y | 12727 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12727 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12728 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12732 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12733 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12734 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12738 | --- | 1 | INT16U | R |  | N/A
|  | Entry 036 |  | Y | Y | Y | Y | Y | 12739 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12739 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12740 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12744 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12745 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12746 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12750 | --- | 1 | INT16U | R |  | N/A
|  | Entry 037 |  | Y | Y | Y | Y | Y | 12751 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12751 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12752 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12756 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12757 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12758 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12762 | --- | 1 | INT16U | R |  | N/A
|  | Entry 038 |  | Y | Y | Y | Y | Y | 12763 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12763 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12764 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12768 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12769 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12770 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12774 | --- | 1 | INT16U | R |  | N/A
|  | Entry 039 |  | Y | Y | Y | Y | Y | 12775 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12775 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12776 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12780 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12781 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12782 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12786 | --- | 1 | INT16U | R |  | N/A
|  | Entry 040 |  | Y | Y | Y | Y | Y | 12787 | --- |  | --- | --- | --- | ---
|  |  | Entry Number | Y | Y | Y | Y | Y | 12787 | --- | 1 | INT16U | R |  | N/A
|  |  | Date/Time | Y | Y | Y | Y | Y | 12788 | --- | 4 | DATETIME | R |  | N/A
|  |  | Record Type | Y | Y | Y | Y | Y | 12792 | --- | 1 | INT16U | R |  | N/A | The high byte shall be 0xFF The low byte Indicates datatype of Value. 0x0000 Boolean 0x0010 INT16U 0x0011 INT16 0x0020 INT32U 0x0021 INT32 0x0030 INT64U 0x0031 INT64 0x0040 FLOAT32 0x0041 FLOAT64
|  |  | Register Number or Event Code | Y | Y | Y | Y | Y | 12793 | --- | 1 | INT16U | R |  | N/A | See Event Codes for secondary events and Alarm Attributes for Primary events
|  |  | Value | Y | Y | Y | Y | Y | 12794 | --- | 4 | INT16U | R |  | N/A
|  |  | Sequence Number | Y | Y | Y | Y | Y | 12798 | --- | 1 | INT16U | R |  | N/A
| Alarm Counters |  |  | Y | Y | Y | Y | Y | 13519 | --- |  | --- | --- | --- | ---
|  | Summary |  | Y | Y | Y | Y | Y | 13519 | --- |  | --- | --- | --- | ---
|  |  | Total Counter | Y | Y | Y | Y | Y | 13519 | --- | 1 | INT16U | R | --- | 0
|  |  | Low Priority Counter | Y | Y | Y | Y | Y | 13520 | --- | 1 | INT16U | R | --- | 0
|  |  | Medium Priority Counter | Y | Y | Y | Y | Y | 13521 | --- | 1 | INT16U | R | --- | 0
|  |  | High Priority Counter | Y | Y | Y | Y | Y | 13522 | --- | 1 | INT16U | R | --- | 0
|  | 1-Second Alarms - Standard |  | Y | Y | Y | Y | Y | 13523 | --- |  | --- | --- | --- | ---
|  |  | Over Current, Phase | Y | Y | Y | Y | Y | 13523 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Under Current, Phase | Y | Y | Y | Y | Y | 13524 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Current, Neutral | Y | Y | Y | Y | Y | 13525 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Current, Ground | Y | Y | Y | Y | Y | 13526 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Voltage, L-L | Y | Y | Y | Y | Y | 13527 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Under Voltage, L-L | Y | Y | Y | Y | Y | 13528 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Voltage, L-N | Y | Y | Y | Y | Y | 13529 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Under Voltage, L-N | Y | Y | Y | Y | Y | 13530 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Power, Active | Y | Y | Y | Y | Y | 13531 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Power, Reactive | Y | Y | Y | Y | Y | 13532 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Power, Apparent | Y | Y | Y | Y | Y | 13533 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Lead Power Factor, True | Y | Y | Y | Y | Y | 13534 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Lag Power Factor, True | Y | Y | Y | Y | Y | 13535 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Lead Power Factor, Displacement | Y | Y | Y | Y | Y | 13536 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Lag Power Factor, Displacement | Y | Y | Y | Y | Y | 13537 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Active Power, Present | Y | Y | Y | Y | Y | 13538 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Active Power, Last | Y | Y | Y | Y | Y | 13539 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Active Power, Predicted | Y | Y | Y | Y | Y | 13540 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Reactive Power, Present | Y | Y | Y | Y | Y | 13541 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Reactive Power, Last | Y | Y | Y | Y | Y | 13542 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Reactive Power, Predicted | Y | Y | Y | Y | Y | 13543 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Apparent Power, Present | Y | Y | Y | Y | Y | 13544 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Apparent Power, Last | Y | Y | Y | Y | Y | 13545 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Demand, Apparent Power, Predicted | Y | Y | Y | Y | Y | 13546 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Frequency | Y | Y | Y | Y | Y | 13547 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Under Frequency | Y | Y | Y | Y | Y | 13548 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Voltage Unbalance | Y | Y | Y | Y | Y | 13549 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Over Voltage Total Harmonic Distortion | Y | Y | Y | Y | Y | 13550 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Phase Loss | Y | Y | Y | Y | Y | 13551 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  | Unary Alarms |  | Y | Y | Y | Y | Y | 13623 | --- |  | --- | --- | --- | ---
|  |  | Meter Powerup (Control Power Loss) | Y | Y | Y | Y | Y | 13623 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Meter Reset | Y | Y | Y | Y | Y | 13624 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Meter Diagnostic | Y | Y | Y | Y | Y | 13625 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Phase Reversal | Y | Y | Y | Y | Y | 13626 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  | Digital Alarms |  |  | Y | Y | Y | Y | 13633 | --- |  | --- | --- | --- | ---
|  |  | Digital Alarm DI1 |  | Y | Y | Y | Y | 13633 | --- | 1 | INT16U | R | 0 – 9999 | 0
|  |  | Digital Alarm DI2 |  | Y | Y | Y | Y | 13634 | --- | 1 | INT16U | R | 0 – 9999 | 0
| 1-Second Alarms - Standard |  |  | Y | Y | Y | Y | Y | 14000 | --- |  | --- | --- | --- | ---
|  | Over Current, Phase |  | Y | Y | Y | Y | Y | 14000 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14000 | --- | 2 | INT32U | RWC |  | 0x10848B80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14002 | --- | 1 | INT16U | R |  | R_IA_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14003 | --- | 1 | INT16U | R |  | R_IB_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14004 | --- | 1 | INT16U | R |  | R_IC_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14005 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14007 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14009 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14011 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14013 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  |  | Digital Outputs to Associate – Option Modules | [5 empty] | 14014 | --- | 4 | BITMAP | RWC |  | 0
|  |  | Datalogs to Trigger | [5 empty] | 14018 | --- | 1 | BITMAP | RWC |  | 0
|  |  | Waveform Capture to Trigger | [5 empty] | 14019 | --- | 1 | BITMAP | RWC |  | 0
|  | Under Current, Phase |  | Y | Y | Y | Y | Y | 14020 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14020 | --- | 2 | INT32U | RWC |  | 0x11048B80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14022 | --- | 1 | INT16U | R |  | R_IA_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14023 | --- | 1 | INT16U | R |  | R_IB_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14024 | --- | 1 | INT16U | R |  | R_IC_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14025 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14027 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14029 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14031 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14033 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Current, Neutral |  | Y | Y | Y | Y | Y | 14040 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14040 | --- | 2 | INT32U | RWC |  | 0x10849400 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14042 | --- | 1 | INT16U | R |  | R_IN_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14043 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14044 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14045 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14047 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14049 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14051 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14053 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Current, Ground | [6 empty] | 14060 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14060 | --- | 2 | INT32U | RWC |  | 0x10849C80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14062 | --- | 1 | INT16U | R |  | R_IG_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14063 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14064 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14065 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum current that can be reported under the present configuration of CT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14067 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14069 | A | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14071 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14073 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Voltage, L-L |  | Y | Y | Y | Y | Y | 14080 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14080 | --- | 2 | INT32U | RWC |  | 0x1082AB80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14082 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14083 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14084 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14085 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14087 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14089 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14091 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14093 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Under Voltage, L-L |  | Y | Y | Y | Y | Y | 14100 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14100 | --- | 2 | INT32U | RWC |  | 0x1102AB80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14102 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14103 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14104 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14105 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14107 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14109 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum dropout setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14111 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14113 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Voltage, L-N |  | Y | Y | Y | Y | Y | 14120 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14120 | --- | 2 | INT32U | RWC |  | 0x1082A380 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14122 | --- | 1 | INT16U | R |  | R_VAN_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14123 | --- | 1 | INT16U | R |  | R_VBN_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14124 | --- | 1 | INT16U | R |  | R_VCN_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14125 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14127 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14129 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14131 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14133 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Under Voltage, L-N |  | Y | Y | Y | Y | Y | 14140 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14140 | --- | 2 | INT32U | RWC |  | 0x1102A380 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14142 | --- | 1 | INT16U | R |  | R_VAN_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14143 | --- | 1 | INT16U | R |  | R_VBN_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14144 | --- | 1 | INT16U | R |  | R_VCN_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14145 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14147 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14149 | V | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum dropout setpoint allowed is the maximum voltage that can be reported under the present configuration of VT ratio.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14151 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14153 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Power, Active |  | Y | Y | Y | Y | Y | 14160 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14160 | --- | 2 | INT32U | RWC |  | 0x10875580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14162 | --- | 1 | INT16U | R |  | R_PTOT_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14163 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14164 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14165 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14167 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14169 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14171 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14173 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Power, Reactive |  | Y | Y | Y | Y | Y | 14180 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14180 | --- | 2 | INT32U | RWC |  | 0x10895580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14182 | --- | 1 | INT16U | R |  | R_QTOT_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14183 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14184 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14185 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14187 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14189 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14191 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14193 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Power, Apparent |  | Y | Y | Y | Y | Y | 14200 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14200 | --- | 2 | INT32U | RWC |  | 0x108B5580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14202 | --- | 1 | INT16U | R |  | R_STOT_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14203 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14204 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14205 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14207 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14209 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14211 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14213 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Leading Power Factor, True |  | Y | Y | Y | Y | Y | 14220 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14220 | --- | 2 | INT32U | RWC |  | 0x118EC380 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14222 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_TRUE
|  |  | Source Register B | Y | Y | Y | Y | Y | 14223 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_TRUE
|  |  | Source Register C | Y | Y | Y | Y | Y | 14224 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_TRUE
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14225 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14227 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14229 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14231 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14233 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Lagging Power Factor, True |  | Y | Y | Y | Y | Y | 14240 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14240 | --- | 2 | INT32U | RWC |  | 0x120EC380 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14242 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_TRUE
|  |  | Source Register B | Y | Y | Y | Y | Y | 14243 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_TRUE
|  |  | Source Register C | Y | Y | Y | Y | Y | 14244 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_TRUE
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14245 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14247 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14249 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14251 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14253 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Leading Power Factor, Displacement |  | Y | Y | Y | Y | Y | 14260 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14260 | --- | 2 | INT32U | RWC |  | 0x118ECB80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14262 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_DISP
|  |  | Source Register B | Y | Y | Y | Y | Y | 14263 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_DISP
|  |  | Source Register C | Y | Y | Y | Y | Y | 14264 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_DISP
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14265 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14267 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14269 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14271 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14273 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Lagging Power Factor, Displacement |  | Y | Y | Y | Y | Y | 14280 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14280 | --- | 2 | INT32U | RWC |  | 0x120ECB80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14282 | --- | 1 | INT16U | R |  | R_PFA_50_60_CYC_DISP
|  |  | Source Register B | Y | Y | Y | Y | Y | 14283 | --- | 1 | INT16U | R |  | R_PFB_50_60_CYC_DISP
|  |  | Source Register C | Y | Y | Y | Y | Y | 14284 | --- | 1 | INT16U | R |  | R_PFC_50_60_CYC_DISP
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14285 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14287 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14289 | --- | 2 | FLOAT32 | RWC |  | 0
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14291 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14293 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Active Power, Present |  | Y | Y | Y | Y | Y | 14300 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14300 | --- | 2 | INT32U | RWC |  | 0x1086E580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14302 | --- | 1 | INT16U | R |  | R_DMD_CH_01_PRES
|  |  | Source Register B | Y | Y | Y | Y | Y | 14303 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14304 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14305 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14307 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14309 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14311 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14313 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Active Power, Last |  | Y | Y | Y | Y | Y | 14320 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14320 | --- | 2 | INT32U | RWC |  | 0x1086D580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14322 | --- | 1 | INT16U | R |  | R_DMD_CH_01_LAST
|  |  | Source Register B | Y | Y | Y | Y | Y | 14323 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14324 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14325 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14327 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14329 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14331 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14333 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Active Power, Predicted |  | Y | Y | Y | Y | Y | 14340 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14340 | --- | 2 | INT32U | RWC |  | 0x1086DD80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14342 | --- | 1 | INT16U | R |  | R_DMD_CH_01_PREDICTED
|  |  | Source Register B | Y | Y | Y | Y | Y | 14343 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14344 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14345 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14347 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14349 | kW | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14351 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14353 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Reactive Power, Present |  | Y | Y | Y | Y | Y | 14360 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14360 | --- | 2 | INT32U | RWC |  | 0x1088E580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14362 | --- | 1 | INT16U | R |  | R_DMD_CH_02_PRES
|  |  | Source Register B | Y | Y | Y | Y | Y | 14363 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14364 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14365 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14367 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14369 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14371 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14373 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Reactive Power, Last |  | Y | Y | Y | Y | Y | 14380 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14380 | --- | 2 | INT32U | RWC |  | 0x1088D580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14382 | --- | 1 | INT16U | R |  | R_DMD_CH_02_LAST
|  |  | Source Register B | Y | Y | Y | Y | Y | 14383 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14384 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14385 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14387 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14389 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14391 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14393 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Reactive Power, Predicted |  | Y | Y | Y | Y | Y | 14400 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14400 | --- | 2 | INT32U | RWC |  | 0x1088DD80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14402 | --- | 1 | INT16U | R |  | R_DMD_CH_02_PREDICTED
|  |  | Source Register B | Y | Y | Y | Y | Y | 14403 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14404 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14405 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14407 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14409 | kVAR | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14411 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14413 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Apparent Power, Present |  | Y | Y | Y | Y | Y | 14420 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14420 | --- | 2 | INT32U | RWC |  | 0x108AE580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14422 | --- | 1 | INT16U | R |  | R_DMD_CH_03_PRES
|  |  | Source Register B | Y | Y | Y | Y | Y | 14423 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14424 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14425 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14427 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14429 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14431 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14433 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Apparent Power, Last |  | Y | Y | Y | Y | Y | 14440 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14440 | --- | 2 | INT32U | RWC |  | 0x108AD580 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14442 | --- | 1 | INT16U | R |  | R_DMD_CH_03_LAST
|  |  | Source Register B | Y | Y | Y | Y | Y | 14443 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14444 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14445 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14447 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14449 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14451 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14453 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Demand, Apparent Power, Predicted |  | Y | Y | Y | Y | Y | 14460 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14460 | --- | 2 | INT32U | RWC |  | 0x108ADD80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14462 | --- | 1 | INT16U | R |  | R_DMD_CH_03_PREDICTED
|  |  | Source Register B | Y | Y | Y | Y | Y | 14463 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14464 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14465 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | The maximum pickup setpoint allowed is the maximum power that can be reported under the present configuration of CT and VT ratio.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14467 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14469 | kVA | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14471 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14473 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Frequency |  | Y | Y | Y | Y | Y | 14480 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14480 | --- | 2 | INT32U | RWC |  | 0x108C0000 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14482 | --- | 1 | INT16U | R |  | R_FREQ_50_60_CYC_AVG
|  |  | Source Register B | Y | Y | Y | Y | Y | 14483 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14484 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14485 | Hz | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14487 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14489 | Hz | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14491 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14493 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Under Frequency |  | Y | Y | Y | Y | Y | 14500 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14500 | --- | 2 | INT32U | RWC |  | 0x110C0000 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14502 | --- | 1 | INT16U | R |  | R_FREQ_50_60_CYC_AVG
|  |  | Source Register B | Y | Y | Y | Y | Y | 14503 | --- | 1 | INT16U | R |  | N/A
|  |  | Source Register C | Y | Y | Y | Y | Y | 14504 | --- | 1 | INT16U | R |  | N/A
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14505 | Hz | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14507 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14509 | Hz | 2 | FLOAT32 | RWC |  | 0
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14511 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14513 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Voltage Unbalance |  | Y | Y | Y | Y | Y | 14520 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14520 | --- | 2 | INT32U | RWC |  | 0x1082BB80 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14522 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_UNB
|  |  | Source Register B | Y | Y | Y | Y | Y | 14523 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_UNB
|  |  | Source Register C | Y | Y | Y | Y | Y | 14524 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_UNB
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14525 | % | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14527 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14529 | % | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14531 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14533 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Over Voltage Total Harmonic Distortion |  | Y | Y | Y | Y | Y | 14540 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14540 | --- | 2 | INT32U | RWC |  | 0x1082B000 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14542 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_THD
|  |  | Source Register B | Y | Y | Y | Y | Y | 14543 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_THD
|  |  | Source Register C | Y | Y | Y | Y | Y | 14544 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_THD
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14545 | % | 2 | FLOAT32 | RWC |  | 0
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14547 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14549 | % | 2 | FLOAT32 | RWC | See User Notes | 0 | Must be < Pickup Setpoint.
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14551 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14553 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
|  | Phase Loss |  | Y | Y | Y | Y | Y | 14560 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 14560 | --- | 2 | INT32U | RWC |  | 0x12820380 | See Alarm Attributes for details.
|  |  | Source Register A | Y | Y | Y | Y | Y | 14562 | --- | 1 | INT16U | R |  | R_VAB_50_60_CYC_RMS
|  |  | Source Register B | Y | Y | Y | Y | Y | 14563 | --- | 1 | INT16U | R |  | R_VBC_50_60_CYC_RMS
|  |  | Source Register C | Y | Y | Y | Y | Y | 14564 | --- | 1 | INT16U | R |  | R_VCA_50_60_CYC_RMS
|  |  | Pickup Setpoint | Y | Y | Y | Y | Y | 14565 | V | 2 | FLOAT32 | RWC |  | 0 | Must be < Dropout Setpoint.
|  |  | Pickup Time Delay | Y | Y | Y | Y | Y | 14567 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Dropout Setpoint | Y | Y | Y | Y | Y | 14569 | V | 2 | FLOAT32 | RWC | See User Notes | 0
|  |  | Dropout Time Delay | Y | Y | Y | Y | Y | 14571 | seconds | 2 | INT32U | RWC | --- | 0
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 14573 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5310, the maximum value is 0x0003. Bit0 and Bit1 used for 2 digital outputs For PM5330/31, the maximum value is 0x000F. Bit0 and Bit1 used for 2 Digital Outputs Bit2 and Bit3 used for 2 Relays Outputs
| Unary Alarms |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Meter Power Up (Control Power Loss) |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 16200 | --- | 2 | INT32U | RWC | --- | 0x84000019 | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 16202 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Meter Reset |  | Y | Y | Y | Y | Y | 16210 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 16210 | --- | 2 | INT32U | RWC | --- | 0x84800019 | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 16212 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Meter Diagnostic |  | Y | Y | Y | Y | Y | 16220 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 16220 | --- | 2 | INT32U | RWC | --- | 0x851A0000 | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 16222 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Phase Reversal |  | Y | Y | Y | Y | Y | 16230 | --- |  | --- | --- | --- | ---
|  |  | Attributes | Y | Y | Y | Y | Y | 16230 | --- | 2 | INT32U | RWC | --- | 0x83000000 | See Alarm Attributes for details.
|  |  | Digital Outputs to Associate – Standard | Y | Y | Y | Y | Y | 16232 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
| Digital Alarms |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Digital Alarm DI1 |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Attributes |  | Y | Y | Y | Y | 16300 | --- | 2 | INT32U | RWC | --- | 0x95900800 | See Alarm Attributes for details.
|  |  | Pickup Time Delay |  | Y | Y | Y | Y | 16302 | seconds | 2 | INT32U | RWC | --- | ---
|  |  | Dropout Time Delay |  | Y | Y | Y | Y | 16304 | seconds | 2 | INT32U | RWC | --- | ---
|  |  | Digital Outputs to Associate – Standard |  | Y | Y | Y | Y | 16306 | --- | 1 | BITMAP | RWC | --- | --- | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
|  | Digital Alarm DI2 |  |  | Y | Y | Y | Y | 16314 | --- |  | --- | --- | --- | ---
|  |  | Attributes |  | Y | Y | Y | Y | 16314 | --- | 2 | INT32U | RWC | --- | 0x95901000 | See Alarm Attributes for details.
|  |  | Pickup Time Delay |  | Y | Y | Y | Y | 16316 | seconds | 2 | INT32U | RWC | --- | ---
|  |  | Dropout Time Delay |  | Y | Y | Y | Y | 16318 | seconds | 2 | INT32U | RWC | --- | ---
|  |  | Digital Outputs to Associate – Standard |  | Y | Y | Y | Y | 16320 | --- | 1 | BITMAP | RWC |  | 0 | Bitmap of digital outputs to associate with this alarm. Bitmap is right-justified with the least significant bit associated with digital output ID of 1. For PM5xxx series, the maximum value is 0x0003. (There are 2 digital outputs.)
Files |  |  |  |  | Y | Y | Y | Y |  | --- | 0 | --- | --- | --- | ---
| Datalogs |  |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Energy Log |  |  | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Logging Status |  | Y | Y | Y | Y | 19000 | --- | 1 | INT16U | RWC | 0-1 | 0 | 0 = Disabled, 1 = Enabled
|  |  | Allocated File Size |  | Y | Y | Y | Y | 19001 | --- | 1 | INT16U | R | --- | 0 | Max number of records in file
|  |  | Allocated Record Size |  | Y | Y | Y | Y | 19002 | --- | 1 | INT16U | R | --- | 0 | Record length in registers
|  |  | Record Management Method |  | Y | Y | Y | Y | 19003 | --- | 1 | INT16U | RWC | 0-1 | 0 | 0 = Circular, 1 = Fill and hold
|  |  | File Status |  | Y | Y | Y | Y | 19004 | --- | 1 | INT16U | R | --- | 0 | 0 = OK, 200 = Internal failure, 210 = Disabled due to config 220 = Disabled due to Null config.
|  |  | Number of records in file |  | Y | Y | Y | Y | 19005 | --- | 1 | INT16U | R | --- | 0 | Number of records wriiten, resets to 0 on file clear
|  |  | First Record Sequence Number |  | Y | Y | Y | Y | 19006 | --- | 1 | INT16U | R | --- | 0 | First record in log
|  |  | Last Record Sequence Number |  | Y | Y | Y | Y | 19007 | --- | 1 | INT16U | R | --- | 0 | Last record in the log
|  |  | Topic Mode |  | Y | Y | Y | Y | 19008 | --- | 1 | INT16U | RWC | --- | 1 | 0 = Power data model, 1 = Modbus register format
|  |  | Start Time |  | Y | Y | Y | Y | 19009 | Minuites | 1 | INT16U | RWC | --- | 0 | Not used in PM5500
|  |  | Stop Time |  | Y | Y | Y | Y | 19010 | seconds | 1 | INT16U | RWC | --- | 1440 | Not used in PM5500
|  |  | Interval Control Minutes |  | Y | Y | Y | Y | 19011 | Minuites | 1 | INT16U | RWC | 1,5,10,15,30,60.1440 | 15
|  |  | Interval Control Seconds |  | Y | Y | Y | Y | 19012 | seconds | 1 | INT16U | RWC | 0-59 | 0
|  |  | Date/Time Last clear |  | Y | Y | Y | Y | 19013 | --- | 4 | DATETIME | RWC | --- | N/A
|  |  | Record Item 1 |  | Y | Y | Y | Y | 19017 | --- | 1 | INT16U | RWC | --- | 0
|  |  | Record Item 2 |  | Y | Y | Y | Y | 19018 | --- | 1 | INT16U | RWC | --- | 0
Diagnostics |  |  |  | Y | Y | Y | Y | Y | 20000 | --- |  | --- | --- | --- | ---
| Self-Test Results |  |  | Y | Y | Y | Y | Y | 20000 | --- |  | --- | --- | --- | ---
|  | Processor Loading |  | Y | Y | Y | Y | Y | 20000 | --- |  | --- | --- | --- | ---
|  |  | Processor Loading | Y | Y | Y | Y | Y | 20000 | % | 1 | INT16U | R | 0 – 100 | 0
|  | Miscellaneous Self-Test |  | Y | Y | Y | Y | Y | 20003 | --- |  | --- | --- | --- | ---
|  |  | Meter Self-Test | Y | Y | Y | Y | Y | 20003 | --- | 5 | BITMAP | R |  | 0x0000 0000 0000 0000 0000 | 0 = OK, 1 = Error Detected Bit 01 = Summary ( on if any other bit is on - Maintenance Icon shown on HMI ) Bit 02 = RAM Failure Bit 03 = NVRAM Failure Bit 04 = RTC Failure Bit 05 = Calibration Failure Bit 06 = Clipping Detected Bit 07 = Over-Running Energy Pulse Output Bit 08-16 Not Used
Meter Data (Advanced) |  |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Frequency | Frequency 1 Cycle | Y | Y | Y | Y | Y | 21016 | Hz | 2 | FLOAT32 | R | 42 – 70
| Power Quality |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  | Total Harmonic Distortion, Current |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | THD Current A | Y | Y | Y | Y | Y | 21300 | % | 2 | FLOAT32 | R | 0 – 100 | --- | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | THD Current B | Y | Y | Y | Y | Y | 21302 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Current C | Y | Y | Y | Y | Y | 21304 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Current N | Y | Y | Y | Y | Y | 21306 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Current G | Y | Y | Y | Y | Y | 21308 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Current A | Y | Y | Y | Y | Y | 21310 | % | 2 | FLOAT32 | R | 0 – 100 | --- | thd = (RMS of harmonics / total RMS) * 100
|  |  | thd Current B | Y | Y | Y | Y | Y | 21312 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Current C | Y | Y | Y | Y | Y | 21314 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Current N | Y | Y | Y | Y | Y | 21316 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Current G | Y | Y | Y | Y | Y | 21318 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  | Total Demand Distortion | Total Demand Distortion | Y | Y | Y | Y | Y | 21320 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  | Total Harmonic Distortion, Voltage |  | Y | Y | Y | Y | Y | 21322 | --- |  | --- | --- | --- | ---
|  |  | THD Voltage A-B | Y | Y | Y | Y | Y | 21322 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage B-C | Y | Y | Y | Y | Y | 21324 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage C-A | Y | Y | Y | Y | Y | 21326 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage L-L | Y | Y | Y | Y | Y | 21328 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage A-N | Y | Y | Y | Y | Y | 21330 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage B-N | Y | Y | Y | Y | Y | 21332 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage C-N | Y | Y | Y | Y | Y | 21334 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage N-G | [5 empty] | 21336 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | THD Voltage L-N | Y | Y | Y | Y | Y | 21338 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage A-B | Y | Y | Y | Y | Y | 21340 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage B-C | Y | Y | Y | Y | Y | 21342 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage C-A | Y | Y | Y | Y | Y | 21344 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage L-L | Y | Y | Y | Y | Y | 21346 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage A-N | Y | Y | Y | Y | Y | 21348 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage B-N | Y | Y | Y | Y | Y | 21350 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage C-N | Y | Y | Y | Y | Y | 21352 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage N-G | [5 empty] | 21354 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  |  | thd Voltage L-N | Y | Y | Y | Y | Y | 21356 | % | 2 | FLOAT32 | R | 0 – 100 | ---
| Harmonics |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
Harmonic Magnitudes and Angles, Voltage A-B
|  |  | Voltage A-B, H1 Magnitude, % | Y | Y | Y | Y | Y | 21712 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H2 Magnitude, % | Y | Y | Y | Y | Y | 21718 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H3 Magnitude, % | Y | Y | Y | Y | Y | 21724 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H4 Magnitude, % | Y | Y | Y | Y | Y | 21730 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H5 Magnitude, % | Y | Y | Y | Y | Y | 21736 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H6 Magnitude, % | Y | Y | Y | Y | Y | 21742 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H7 Magnitude, % | Y | Y | Y | Y | Y | 21748 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H8 Magnitude, % | Y | Y | Y | Y | Y | 21754 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H9 Magnitude, % | Y | Y | Y | Y | Y | 21760 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H10 Magnitude, % | Y | Y | Y | Y | Y | 21766 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H11 Magnitude, % | Y | Y | Y | Y | Y | 21772 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H12 Magnitude, % | Y | Y | Y | Y | Y | 21778 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H13 Magnitude, % | Y | Y | Y | Y | Y | 21784 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H14 Magnitude, % | Y | Y | Y | Y | Y | 21790 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H15 Magnitude, % | Y | Y | Y | Y | Y | 21796 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H16 Magnitude, % |  | Y | Y | Y | Y | 21802 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H17 Magnitude, % |  | Y | Y | Y | Y | 21808 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H18 Magnitude, % |  | Y | Y | Y | Y | 21814 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H19 Magnitude, % |  | Y | Y | Y | Y | 21820 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H20 Magnitude, % |  | Y | Y | Y | Y | 21826 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H21 Magnitude, % |  | Y | Y | Y | Y | 21832 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H22 Magnitude, % |  | Y | Y | Y | Y | 21838 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H23 Magnitude, % |  | Y | Y | Y | Y | 21844 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H24 Magnitude, % |  | Y | Y | Y | Y | 21850 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H25 Magnitude, % |  | Y | Y | Y | Y | 21856 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H26 Magnitude, % |  | Y | Y | Y | Y | 21862 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H27 Magnitude, % |  | Y | Y | Y | Y | 21868 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H28 Magnitude, % |  | Y | Y | Y | Y | 21874 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H29 Magnitude, % |  | Y | Y | Y | Y | 21880 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H30 Magnitude, % |  | Y | Y | Y | Y | 21886 | % | 2 | FLOAT32 | R
|  |  | Voltage A-B, H31 Magnitude, % |  | Y | Y | Y | Y | 21892 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Voltage B-C | [6 empty] | 22090 | --- |  | --- | --- | --- | ---
|  |  | Voltage B-C, H1 Magnitude, % | Y | Y | Y | Y | Y | 22100 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H2 Magnitude, % | Y | Y | Y | Y | Y | 22106 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H3 Magnitude, % | Y | Y | Y | Y | Y | 22112 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H4 Magnitude, % | Y | Y | Y | Y | Y | 22118 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H5 Magnitude, % | Y | Y | Y | Y | Y | 22124 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H6 Magnitude, % | Y | Y | Y | Y | Y | 22130 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H7 Magnitude, % | Y | Y | Y | Y | Y | 22136 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H8 Magnitude, % | Y | Y | Y | Y | Y | 22142 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H9 Magnitude, % | Y | Y | Y | Y | Y | 22148 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H10 Magnitude, % | Y | Y | Y | Y | Y | 22154 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H11 Magnitude, % | Y | Y | Y | Y | Y | 22160 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H12 Magnitude, % | Y | Y | Y | Y | Y | 22166 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H13 Magnitude, % | Y | Y | Y | Y | Y | 22172 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H14 Magnitude, % | Y | Y | Y | Y | Y | 22178 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H15 Magnitude, % | Y | Y | Y | Y | Y | 22184 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H16 Magnitude, % |  | Y | Y | Y | Y | 22190 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H17 Magnitude, % |  | Y | Y | Y | Y | 22196 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H18 Magnitude, % |  | Y | Y | Y | Y | 22202 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H19 Magnitude, % |  | Y | Y | Y | Y | 22208 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H20 Magnitude, % |  | Y | Y | Y | Y | 22214 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H21 Magnitude, % |  | Y | Y | Y | Y | 22220 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H22 Magnitude, % |  | Y | Y | Y | Y | 22226 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H23 Magnitude, % |  | Y | Y | Y | Y | 22232 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H24 Magnitude, % |  | Y | Y | Y | Y | 22238 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H25 Magnitude, % |  | Y | Y | Y | Y | 22244 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H26 Magnitude, % |  | Y | Y | Y | Y | 22250 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H27 Magnitude, % |  | Y | Y | Y | Y | 22256 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H28 Magnitude, % |  | Y | Y | Y | Y | 22262 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H29 Magnitude, % |  | Y | Y | Y | Y | 22268 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H30 Magnitude, % |  | Y | Y | Y | Y | 22274 | % | 2 | FLOAT32 | R
|  |  | Voltage B-C, H31 Magnitude, % |  | Y | Y | Y | Y | 22280 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Voltage C-A | [6 empty] | 22478 | --- |  | --- | --- | --- | ---
|  |  | Voltage C-A, H1 Magnitude, % | Y | Y | Y | Y | Y | 22488 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H2 Magnitude, % | Y | Y | Y | Y | Y | 22494 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H3 Magnitude, % | Y | Y | Y | Y | Y | 22500 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H4 Magnitude, % | Y | Y | Y | Y | Y | 22506 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H5 Magnitude, % | Y | Y | Y | Y | Y | 22512 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H6 Magnitude, % | Y | Y | Y | Y | Y | 22518 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H7 Magnitude, % | Y | Y | Y | Y | Y | 22524 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H8 Magnitude, % | Y | Y | Y | Y | Y | 22530 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H9 Magnitude, % | Y | Y | Y | Y | Y | 22536 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H10 Magnitude, % | Y | Y | Y | Y | Y | 22542 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H11 Magnitude, % | Y | Y | Y | Y | Y | 22548 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H12 Magnitude, % | Y | Y | Y | Y | Y | 22554 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H13 Magnitude, % | Y | Y | Y | Y | Y | 22560 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H14 Magnitude, % | Y | Y | Y | Y | Y | 22566 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H15 Magnitude, % | Y | Y | Y | Y | Y | 22572 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H16 Magnitude, % |  | Y | Y | Y | Y | 22578 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H17 Magnitude, % |  | Y | Y | Y | Y | 22584 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H18 Magnitude, % |  | Y | Y | Y | Y | 22590 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H19 Magnitude, % |  | Y | Y | Y | Y | 22596 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H20 Magnitude, % |  | Y | Y | Y | Y | 22602 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H21 Magnitude, % |  | Y | Y | Y | Y | 22608 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H22 Magnitude, % |  | Y | Y | Y | Y | 22614 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H23 Magnitude, % |  | Y | Y | Y | Y | 22620 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H24 Magnitude, % |  | Y | Y | Y | Y | 22626 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H25 Magnitude, % |  | Y | Y | Y | Y | 22632 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H26 Magnitude, % |  | Y | Y | Y | Y | 22638 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H27 Magnitude, % |  | Y | Y | Y | Y | 22644 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H28 Magnitude, % |  | Y | Y | Y | Y | 22650 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H29 Magnitude, % |  | Y | Y | Y | Y | 22656 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H30 Magnitude, % |  | Y | Y | Y | Y | 22662 | % | 2 | FLOAT32 | R
|  |  | Voltage C-A, H31 Magnitude, % |  | Y | Y | Y | Y | 22668 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Voltage A-N | [6 empty] | 22866 | --- |  | --- | --- | --- | ---
|  |  | Voltage A-N, H1 Magnitude, % | Y | Y | Y | Y | Y | 22876 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H2 Magnitude, % | Y | Y | Y | Y | Y | 22882 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H3 Magnitude, % | Y | Y | Y | Y | Y | 22888 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H4 Magnitude, % | Y | Y | Y | Y | Y | 22894 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H5 Magnitude, % | Y | Y | Y | Y | Y | 22900 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H6 Magnitude, % | Y | Y | Y | Y | Y | 22906 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H7 Magnitude, % | Y | Y | Y | Y | Y | 22912 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H8 Magnitude, % | Y | Y | Y | Y | Y | 22918 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H9 Magnitude, % | Y | Y | Y | Y | Y | 22924 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H10 Magnitude, % | Y | Y | Y | Y | Y | 22930 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H11 Magnitude, % | Y | Y | Y | Y | Y | 22936 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H12 Magnitude, % | Y | Y | Y | Y | Y | 22942 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H13 Magnitude, % | Y | Y | Y | Y | Y | 22948 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H14 Magnitude, % | Y | Y | Y | Y | Y | 22954 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H15 Magnitude, % | Y | Y | Y | Y | Y | 22960 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H16 Magnitude, % |  | Y | Y | Y | Y | 22966 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H17 Magnitude, % |  | Y | Y | Y | Y | 22972 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H18 Magnitude, % |  | Y | Y | Y | Y | 22978 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H19 Magnitude, % |  | Y | Y | Y | Y | 22984 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H20 Magnitude, % |  | Y | Y | Y | Y | 22990 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H21 Magnitude, % |  | Y | Y | Y | Y | 22996 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H22 Magnitude, % |  | Y | Y | Y | Y | 23002 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H23 Magnitude, % |  | Y | Y | Y | Y | 23008 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H24 Magnitude, % |  | Y | Y | Y | Y | 23014 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H25 Magnitude, % |  | Y | Y | Y | Y | 23020 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H26 Magnitude, % |  | Y | Y | Y | Y | 23026 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H27 Magnitude, % |  | Y | Y | Y | Y | 23032 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H28 Magnitude, % |  | Y | Y | Y | Y | 23038 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H29 Magnitude, % |  | Y | Y | Y | Y | 23044 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H30 Magnitude, % |  | Y | Y | Y | Y | 23050 | % | 2 | FLOAT32 | R
|  |  | Voltage A-N, H31 Magnitude, % |  | Y | Y | Y | Y | 23056 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Voltage B-N | [7 empty] | --- |  | --- | --- | --- | ---
|  |  | Voltage B-N, H1 Magnitude, % | Y | Y | Y | Y | Y | 23264 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H2 Magnitude, % | Y | Y | Y | Y | Y | 23270 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H3 Magnitude, % | Y | Y | Y | Y | Y | 23276 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H4 Magnitude, % | Y | Y | Y | Y | Y | 23282 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H5 Magnitude, % | Y | Y | Y | Y | Y | 23288 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H6 Magnitude, % | Y | Y | Y | Y | Y | 23294 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H7 Magnitude, % | Y | Y | Y | Y | Y | 23300 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H8 Magnitude, % | Y | Y | Y | Y | Y | 23306 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H9 Magnitude, % | Y | Y | Y | Y | Y | 23312 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H10 Magnitude, % | Y | Y | Y | Y | Y | 23318 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H11 Magnitude, % | Y | Y | Y | Y | Y | 23324 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H12 Magnitude, % | Y | Y | Y | Y | Y | 23330 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H13 Magnitude, % | Y | Y | Y | Y | Y | 23336 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H14 Magnitude, % | Y | Y | Y | Y | Y | 23342 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H15 Magnitude, % | Y | Y | Y | Y | Y | 23348 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H16 Magnitude, % |  | Y | Y | Y | Y | 23354 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H17 Magnitude, % |  | Y | Y | Y | Y | 23360 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H18 Magnitude, % |  | Y | Y | Y | Y | 23366 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H19 Magnitude, % |  | Y | Y | Y | Y | 23372 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H20 Magnitude, % |  | Y | Y | Y | Y | 23378 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H21 Magnitude, % |  | Y | Y | Y | Y | 23384 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H22 Magnitude, % |  | Y | Y | Y | Y | 23390 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H23 Magnitude, % |  | Y | Y | Y | Y | 23396 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H24 Magnitude, % |  | Y | Y | Y | Y | 23402 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H25 Magnitude, % |  | Y | Y | Y | Y | 23408 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H26 Magnitude, % |  | Y | Y | Y | Y | 23414 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H27 Magnitude, % |  | Y | Y | Y | Y | 23420 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H28 Magnitude, % |  | Y | Y | Y | Y | 23426 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H29 Magnitude, % |  | Y | Y | Y | Y | 23432 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H30 Magnitude, % |  | Y | Y | Y | Y | 23438 | % | 2 | FLOAT32 | R
|  |  | Voltage B-N, H31 Magnitude, % |  | Y | Y | Y | Y | 23444 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Voltage C-N | [6 empty] | 23642 | --- |  | --- | --- | --- | ---
|  |  | Voltage C-N, H1 Magnitude, % | Y | Y | Y | Y | Y | 23652 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H2 Magnitude, % | Y | Y | Y | Y | Y | 23658 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H3 Magnitude, % | Y | Y | Y | Y | Y | 23664 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H4 Magnitude, % | Y | Y | Y | Y | Y | 23670 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H5 Magnitude, % | Y | Y | Y | Y | Y | 23676 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H6 Magnitude, % | Y | Y | Y | Y | Y | 23682 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H7 Magnitude, % | Y | Y | Y | Y | Y | 23688 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H8 Magnitude, % | Y | Y | Y | Y | Y | 23694 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H9 Magnitude, % | Y | Y | Y | Y | Y | 23700 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H10 Magnitude, % | Y | Y | Y | Y | Y | 23706 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H11 Magnitude, % | Y | Y | Y | Y | Y | 23712 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H12 Magnitude, % | Y | Y | Y | Y | Y | 23718 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H13 Magnitude, % | Y | Y | Y | Y | Y | 23724 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H14 Magnitude, % | Y | Y | Y | Y | Y | 23730 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H15 Magnitude, % | Y | Y | Y | Y | Y | 23736 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H16 Magnitude, % |  | Y | Y | Y | Y | 23742 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H17 Magnitude, % |  | Y | Y | Y | Y | 23748 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H18 Magnitude, % |  | Y | Y | Y | Y | 23754 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H19 Magnitude, % |  | Y | Y | Y | Y | 23760 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H20 Magnitude, % |  | Y | Y | Y | Y | 23766 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H21 Magnitude, % |  | Y | Y | Y | Y | 23772 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H22 Magnitude, % |  | Y | Y | Y | Y | 23778 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H23 Magnitude, % |  | Y | Y | Y | Y | 23784 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H24 Magnitude, % |  | Y | Y | Y | Y | 23790 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H25 Magnitude, % |  | Y | Y | Y | Y | 23796 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H26 Magnitude, % |  | Y | Y | Y | Y | 23802 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H27 Magnitude, % |  | Y | Y | Y | Y | 23808 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H28 Magnitude, % |  | Y | Y | Y | Y | 23814 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H29 Magnitude, % |  | Y | Y | Y | Y | 23820 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H30 Magnitude, % |  | Y | Y | Y | Y | 23826 | % | 2 | FLOAT32 | R
|  |  | Voltage C-N, H31 Magnitude, % |  | Y | Y | Y | Y | 23832 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Current, Phase A | [6 empty] | 24418 | --- |  | --- | --- | --- | ---
|  |  | Current A, H1 Magnitude, % | Y | Y | Y | Y | Y | 24428 | % | 2 | FLOAT32 | R
|  |  | Current A, H2 Magnitude, % | Y | Y | Y | Y | Y | 24434 | % | 2 | FLOAT32 | R
|  |  | Current A, H3 Magnitude, % | Y | Y | Y | Y | Y | 24440 | % | 2 | FLOAT32 | R
|  |  | Current A, H4 Magnitude, % | Y | Y | Y | Y | Y | 24446 | % | 2 | FLOAT32 | R
|  |  | Current A, H5 Magnitude, % | Y | Y | Y | Y | Y | 24452 | % | 2 | FLOAT32 | R
|  |  | Current A, H6 Magnitude, % | Y | Y | Y | Y | Y | 24458 | % | 2 | FLOAT32 | R
|  |  | Current A, H7 Magnitude, % | Y | Y | Y | Y | Y | 24464 | % | 2 | FLOAT32 | R
|  |  | Current A, H8 Magnitude, % | Y | Y | Y | Y | Y | 24470 | % | 2 | FLOAT32 | R
|  |  | Current A, H9 Magnitude, % | Y | Y | Y | Y | Y | 24476 | % | 2 | FLOAT32 | R
|  |  | Current A, H10 Magnitude, % | Y | Y | Y | Y | Y | 24482 | % | 2 | FLOAT32 | R
|  |  | Current A, H11 Magnitude, % | Y | Y | Y | Y | Y | 24488 | % | 2 | FLOAT32 | R
|  |  | Current A, H12 Magnitude, % | Y | Y | Y | Y | Y | 24494 | % | 2 | FLOAT32 | R
|  |  | Current A, H13 Magnitude, % | Y | Y | Y | Y | Y | 24500 | % | 2 | FLOAT32 | R
|  |  | Current A, H14 Magnitude, % | Y | Y | Y | Y | Y | 24506 | % | 2 | FLOAT32 | R
|  |  | Current A, H15 Magnitude, % | Y | Y | Y | Y | Y | 24512 | % | 2 | FLOAT32 | R
|  |  | Current A, H16 Magnitude, % |  | Y | Y | Y | Y | 24518 | % | 2 | FLOAT32 | R
|  |  | Current A, H17 Magnitude, % |  | Y | Y | Y | Y | 24524 | % | 2 | FLOAT32 | R
|  |  | Current A, H18 Magnitude, % |  | Y | Y | Y | Y | 24530 | % | 2 | FLOAT32 | R
|  |  | Current A, H19 Magnitude, % |  | Y | Y | Y | Y | 24536 | % | 2 | FLOAT32 | R
|  |  | Current A, H20 Magnitude, % |  | Y | Y | Y | Y | 24542 | % | 2 | FLOAT32 | R
|  |  | Current A, H21 Magnitude, % |  | Y | Y | Y | Y | 24548 | % | 2 | FLOAT32 | R
|  |  | Current A, H22 Magnitude, % |  | Y | Y | Y | Y | 24554 | % | 2 | FLOAT32 | R
|  |  | Current A, H23 Magnitude, % |  | Y | Y | Y | Y | 24560 | % | 2 | FLOAT32 | R
|  |  | Current A, H24 Magnitude, % |  | Y | Y | Y | Y | 24566 | % | 2 | FLOAT32 | R
|  |  | Current A, H25 Magnitude, % |  | Y | Y | Y | Y | 24572 | % | 2 | FLOAT32 | R
|  |  | Current A, H26 Magnitude, % |  | Y | Y | Y | Y | 24578 | % | 2 | FLOAT32 | R
|  |  | Current A, H27 Magnitude, % |  | Y | Y | Y | Y | 24584 | % | 2 | FLOAT32 | R
|  |  | Current A, H28 Magnitude, % |  | Y | Y | Y | Y | 24590 | % | 2 | FLOAT32 | R
|  |  | Current A, H29 Magnitude, % |  | Y | Y | Y | Y | 24596 | % | 2 | FLOAT32 | R
|  |  | Current A, H30 Magnitude, % |  | Y | Y | Y | Y | 24602 | % | 2 | FLOAT32 | R
|  |  | Current A, H31 Magnitude, % |  | Y | Y | Y | Y | 24608 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Current, Phase B | [6 empty] | 24806 | --- |  | --- | --- | --- | ---
|  |  | Current B, H1 Magnitude, % | Y | Y | Y | Y | Y | 24816 | % | 2 | FLOAT32 | R
|  |  | Current B, H2 Magnitude, % | Y | Y | Y | Y | Y | 24822 | % | 2 | FLOAT32 | R
|  |  | Current B, H3 Magnitude, % | Y | Y | Y | Y | Y | 24828 | % | 2 | FLOAT32 | R
|  |  | Current B, H4 Magnitude, % | Y | Y | Y | Y | Y | 24834 | % | 2 | FLOAT32 | R
|  |  | Current B, H5 Magnitude, % | Y | Y | Y | Y | Y | 24840 | % | 2 | FLOAT32 | R
|  |  | Current B, H6 Magnitude, % | Y | Y | Y | Y | Y | 24846 | % | 2 | FLOAT32 | R
|  |  | Current B, H7 Magnitude, % | Y | Y | Y | Y | Y | 24852 | % | 2 | FLOAT32 | R
|  |  | Current B, H8 Magnitude, % | Y | Y | Y | Y | Y | 24858 | % | 2 | FLOAT32 | R
|  |  | Current B, H9 Magnitude, % | Y | Y | Y | Y | Y | 24864 | % | 2 | FLOAT32 | R
|  |  | Current B, H10 Magnitude, % | Y | Y | Y | Y | Y | 24870 | % | 2 | FLOAT32 | R
|  |  | Current B, H11 Magnitude, % | Y | Y | Y | Y | Y | 24876 | % | 2 | FLOAT32 | R
|  |  | Current B, H12 Magnitude, % | Y | Y | Y | Y | Y | 24882 | % | 2 | FLOAT32 | R
|  |  | Current B, H13 Magnitude, % | Y | Y | Y | Y | Y | 24888 | % | 2 | FLOAT32 | R
|  |  | Current B, H14 Magnitude, % | Y | Y | Y | Y | Y | 24894 | % | 2 | FLOAT32 | R
|  |  | Current B, H15 Magnitude, % | Y | Y | Y | Y | Y | 24900 | % | 2 | FLOAT32 | R
|  |  | Current B, H16 Magnitude, % |  | Y | Y | Y | Y | 24906 | % | 2 | FLOAT32 | R
|  |  | Current B, H17 Magnitude, % |  | Y | Y | Y | Y | 24912 | % | 2 | FLOAT32 | R
|  |  | Current B, H18 Magnitude, % |  | Y | Y | Y | Y | 24918 | % | 2 | FLOAT32 | R
|  |  | Current B, H19 Magnitude, % |  | Y | Y | Y | Y | 24924 | % | 2 | FLOAT32 | R
|  |  | Current B, H20 Magnitude, % |  | Y | Y | Y | Y | 24930 | % | 2 | FLOAT32 | R
|  |  | Current B, H21 Magnitude, % |  | Y | Y | Y | Y | 24936 | % | 2 | FLOAT32 | R
|  |  | Current B, H22 Magnitude, % |  | Y | Y | Y | Y | 24942 | % | 2 | FLOAT32 | R
|  |  | Current B, H23 Magnitude, % |  | Y | Y | Y | Y | 24948 | % | 2 | FLOAT32 | R
|  |  | Current B, H24 Magnitude, % |  | Y | Y | Y | Y | 24954 | % | 2 | FLOAT32 | R
|  |  | Current B, H25 Magnitude, % |  | Y | Y | Y | Y | 24960 | % | 2 | FLOAT32 | R
|  |  | Current B, H26 Magnitude, % |  | Y | Y | Y | Y | 24966 | % | 2 | FLOAT32 | R
|  |  | Current B, H27 Magnitude, % |  | Y | Y | Y | Y | 24972 | % | 2 | FLOAT32 | R
|  |  | Current B, H28 Magnitude, % |  | Y | Y | Y | Y | 24978 | % | 2 | FLOAT32 | R
|  |  | Current B, H29 Magnitude, % |  | Y | Y | Y | Y | 24984 | % | 2 | FLOAT32 | R
|  |  | Current B, H30 Magnitude, % |  | Y | Y | Y | Y | 24990 | % | 2 | FLOAT32 | R
|  |  | Current B, H31 Magnitude, % |  | Y | Y | Y | Y | 24996 | % | 2 | FLOAT32 | R
|  | Harmonic Magnitudes and Angles, Current, Phase C | [6 empty] | 25194 | --- |  | --- | --- | --- | ---
|  |  | Current C, H1 Magnitude, % | Y | Y | Y | Y | Y | 25204 | % | 2 | FLOAT32 | R
|  |  | Current C, H2 Magnitude, % | Y | Y | Y | Y | Y | 25210 | % | 2 | FLOAT32 | R
|  |  | Current C, H3 Magnitude, % | Y | Y | Y | Y | Y | 25216 | % | 2 | FLOAT32 | R
|  |  | Current C, H4 Magnitude, % | Y | Y | Y | Y | Y | 25222 | % | 2 | FLOAT32 | R
|  |  | Current C, H5 Magnitude, % | Y | Y | Y | Y | Y | 25228 | % | 2 | FLOAT32 | R
|  |  | Current C, H6 Magnitude, % | Y | Y | Y | Y | Y | 25234 | % | 2 | FLOAT32 | R
|  |  | Current C, H7 Magnitude, % | Y | Y | Y | Y | Y | 25240 | % | 2 | FLOAT32 | R
|  |  | Current C, H8 Magnitude, % | Y | Y | Y | Y | Y | 25246 | % | 2 | FLOAT32 | R
|  |  | Current C, H9 Magnitude, % | Y | Y | Y | Y | Y | 25252 | % | 2 | FLOAT32 | R
|  |  | Current C, H10 Magnitude, % | Y | Y | Y | Y | Y | 25258 | % | 2 | FLOAT32 | R
|  |  | Current C, H11 Magnitude, % | Y | Y | Y | Y | Y | 25264 | % | 2 | FLOAT32 | R
|  |  | Current C, H12 Magnitude, % | Y | Y | Y | Y | Y | 25270 | % | 2 | FLOAT32 | R
|  |  | Current C, H13 Magnitude, % | Y | Y | Y | Y | Y | 25276 | % | 2 | FLOAT32 | R
|  |  | Current C, H14 Magnitude, % | Y | Y | Y | Y | Y | 25282 | % | 2 | FLOAT32 | R
|  |  | Current C, H15 Magnitude, % | Y | Y | Y | Y | Y | 25288 | % | 2 | FLOAT32 | R
|  |  | Current C, H16 Magnitude, % |  | Y | Y | Y | Y | 25294 | % | 2 | FLOAT32 | R
|  |  | Current C, H17 Magnitude, % |  | Y | Y | Y | Y | 25300 | % | 2 | FLOAT32 | R
|  |  | Current C, H18 Magnitude, % |  | Y | Y | Y | Y | 25306 | % | 2 | FLOAT32 | R
|  |  | Current C, H19 Magnitude, % |  | Y | Y | Y | Y | 25312 | % | 2 | FLOAT32 | R
|  |  | Current C, H20 Magnitude, % |  | Y | Y | Y | Y | 25318 | % | 2 | FLOAT32 | R
|  |  | Current C, H21 Magnitude, % |  | Y | Y | Y | Y | 25324 | % | 2 | FLOAT32 | R
|  |  | Current C, H22 Magnitude, % |  | Y | Y | Y | Y | 25330 | % | 2 | FLOAT32 | R
|  |  | Current C, H23 Magnitude, % |  | Y | Y | Y | Y | 25336 | % | 2 | FLOAT32 | R
|  |  | Current C, H24 Magnitude, % |  | Y | Y | Y | Y | 25342 | % | 2 | FLOAT32 | R
|  |  | Current C, H25 Magnitude, % |  | Y | Y | Y | Y | 25348 | % | 2 | FLOAT32 | R
|  |  | Current C, H26 Magnitude, % |  | Y | Y | Y | Y | 25354 | % | 2 | FLOAT32 | R
|  |  | Current C, H27 Magnitude, % |  | Y | Y | Y | Y | 25360 | % | 2 | FLOAT32 | R
|  |  | Current C, H28 Magnitude, % |  | Y | Y | Y | Y | 25366 | % | 2 | FLOAT32 | R
|  |  | Current C, H29 Magnitude, % |  | Y | Y | Y | Y | 25372 | % | 2 | FLOAT32 | R
|  |  | Current C, H30 Magnitude, % |  | Y | Y | Y | Y | 25378 | % | 2 | FLOAT32 | R
|  |  | Current C, H31 Magnitude, % |  | Y | Y | Y | Y | 25384 | % | 2 | FLOAT32 | R
| Minimum Values |  |  | Y | Y | Y | Y | Y |  | --- |  | --- | --- | --- | ---
|  |  | Min/Max Reset Datetime | Y | Y | Y | Y | Y | 27214 | --- | 4 | DATETIME | R | --- | N/A
|  | Current |  | Y | Y | Y | Y | Y | 27218 | --- |  | --- | --- | --- | ---
|  |  | Min Current A | Y | Y | Y | Y | Y | 27218 | A | 2 | FLOAT32 | R
|  |  | Min Current B | Y | Y | Y | Y | Y | 27220 | A | 2 | FLOAT32 | R
|  |  | Min Current C | Y | Y | Y | Y | Y | 27222 | A | 2 | FLOAT32 | R
|  |  | Min Current N | Y | Y | Y | Y | Y | 27224 | A | 2 | FLOAT32 | R
|  |  | Min Current G | Y | Y | Y | Y | Y | 27226 | A | 2 | FLOAT32 | R
|  |  | Min Current Avg | Y | Y | Y | Y | Y | 27228 | A | 2 | FLOAT32 | R
|  | Current Unbalance |  | Y | Y | Y | Y | Y | 27230 | --- |  | --- | --- | --- | ---
|  |  | Min Current Unbalance A | Y | Y | Y | Y | Y | 27230 | % | 2 | FLOAT32 | R
|  |  | Min Current Unbalance B | Y | Y | Y | Y | Y | 27232 | % | 2 | FLOAT32 | R
|  |  | Min Current Unbalance C | Y | Y | Y | Y | Y | 27234 | % | 2 | FLOAT32 | R
|  |  | Min Current Unbalance Worst | Y | Y | Y | Y | Y | 27236 | % | 2 | FLOAT32 | R
|  | Voltage |  | Y | Y | Y | Y | Y | 27238 | --- |  | --- | --- | --- | ---
|  |  | Min Voltage A-B | Y | Y | Y | Y | Y | 27238 | V | 2 | FLOAT32 | R
|  |  | Min Voltage B-C | Y | Y | Y | Y | Y | 27240 | V | 2 | FLOAT32 | R
|  |  | Min Voltage C-A | Y | Y | Y | Y | Y | 27242 | V | 2 | FLOAT32 | R
|  |  | Min Voltage L-L Avg | Y | Y | Y | Y | Y | 27244 | V | 2 | FLOAT32 | R
|  |  | Min Voltage A-N | Y | Y | Y | Y | Y | 27246 | V | 2 | FLOAT32 | R
|  |  | Min Voltage B-N | Y | Y | Y | Y | Y | 27248 | V | 2 | FLOAT32 | R
|  |  | Min Voltage C-N | Y | Y | Y | Y | Y | 27250 | V | 2 | FLOAT32 | R
|  |  | Min Voltage N-G | [5 empty] | 27252 | V | 2 | FLOAT32 | R
|  |  | Min Voltage L-N Avg | Y | Y | Y | Y | Y | 27254 | V | 2 | FLOAT32 | R
|  | Voltage Unbalance |  | Y | Y | Y | Y | Y | 27256 | --- |  | --- | --- | --- | ---
|  |  | Min Voltage Unbalance A-B | Y | Y | Y | Y | Y | 27256 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance B-C | Y | Y | Y | Y | Y | 27258 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance C-A | Y | Y | Y | Y | Y | 27260 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance L-L Worst | Y | Y | Y | Y | Y | 27262 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance A-N | Y | Y | Y | Y | Y | 27264 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance B-N | Y | Y | Y | Y | Y | 27266 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance C-N | Y | Y | Y | Y | Y | 27268 | % | 2 | FLOAT32 | R
|  |  | Min Voltage Unbalance L-N Worst | Y | Y | Y | Y | Y | 27270 | % | 2 | FLOAT32 | R
|  | Power |  | Y | Y | Y | Y | Y | 27272 | --- |  | --- | --- | --- | ---
|  |  | Min Active Power A | Y | Y | Y | Y | Y | 27272 | kW | 2 | FLOAT32 | R
|  |  | Min Active Power B | Y | Y | Y | Y | Y | 27274 | kW | 2 | FLOAT32 | R
|  |  | Min Active Power C | Y | Y | Y | Y | Y | 27276 | kW | 2 | FLOAT32 | R
|  |  | Min Active Power Total | Y | Y | Y | Y | Y | 27278 | kW | 2 | FLOAT32 | R
|  |  | Min Reactive Power A | Y | Y | Y | Y | Y | 27280 | kVAR | 2 | FLOAT32 | R
|  |  | Min Reactive Power B | Y | Y | Y | Y | Y | 27282 | kVAR | 2 | FLOAT32 | R
|  |  | Min Reactive Power C | Y | Y | Y | Y | Y | 27284 | kVAR | 2 | FLOAT32 | R
|  |  | Min Reactive Power Total | Y | Y | Y | Y | Y | 27286 | kVAR | 2 | FLOAT32 | R
|  |  | Min Apparent Power A | Y | Y | Y | Y | Y | 27288 | kVA | 2 | FLOAT32 | R
|  |  | Min Apparent Power B | Y | Y | Y | Y | Y | 27290 | kVA | 2 | FLOAT32 | R
|  |  | Min Apparent Power C | Y | Y | Y | Y | Y | 27292 | kVA | 2 | FLOAT32 | R
|  |  | Min Apparent Power Total | Y | Y | Y | Y | Y | 27294 | kVA | 2 | FLOAT32 | R
|  | Power Factor |  | Y | Y | Y | Y | Y | 27306 | --- |  | --- | --- | --- | ---
|  |  | Min Power Factor A | Y | Y | Y | Y | Y | 27306 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Power Factor B | Y | Y | Y | Y | Y | 27308 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Power Factor C | Y | Y | Y | Y | Y | 27310 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Power Factor Total | Y | Y | Y | Y | Y | 27312 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Displacement Power Factor A | Y | Y | Y | Y | Y | 27314 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Displacement Power Factor B | Y | Y | Y | Y | Y | 27316 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Displacement Power Factor C | Y | Y | Y | Y | Y | 27318 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Min Displacement PF Total | Y | Y | Y | Y | Y | 27320 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  | Total Harmonic Distortion, Current |  | Y | Y | Y | Y | Y | 27338 | --- |  | --- | --- | --- | ---
|  |  | Min THD Current A | Y | Y | Y | Y | Y | 27338 | % | 2 | FLOAT32 | R | 0 – 100 |  | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | Min THD Current B | Y | Y | Y | Y | Y | 27340 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Current C | Y | Y | Y | Y | Y | 27342 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Current N | Y | Y | Y | Y | Y | 27344 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Current G | Y | Y | Y | Y | Y | 27346 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Current A | Y | Y | Y | Y | Y | 27348 | % | 2 | FLOAT32 | R | 0 – 100 |  | thd = (RMS of harmonics / total RMS) * 100
|  |  | Min thd Current B | Y | Y | Y | Y | Y | 27350 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Current C | Y | Y | Y | Y | Y | 27352 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Current N | Y | Y | Y | Y | Y | 27354 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Current G | Y | Y | Y | Y | Y | 27356 | % | 2 | FLOAT32 | R | 0 – 100
|  | Total Demand Distortion | Min Total Demand Distortion | Y | Y | Y | Y | Y | 27358 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  | Total Harmonic Distortion, Voltage |  | Y | Y | Y | Y | Y | 27360 | --- |  | --- | --- | --- | ---
|  |  | Min THD Voltage A-B | Y | Y | Y | Y | Y | 27360 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage B-C | Y | Y | Y | Y | Y | 27362 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage C-A | Y | Y | Y | Y | Y | 27364 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage L-L Avg | Y | Y | Y | Y | Y | 27366 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage A-N | Y | Y | Y | Y | Y | 27368 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage B-N | Y | Y | Y | Y | Y | 27370 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage C-N | Y | Y | Y | Y | Y | 27372 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage N-G | [5 empty] | 27374 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min THD Voltage L-N Avg | Y | Y | Y | Y | Y | 27376 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage A-B | Y | Y | Y | Y | Y | 27378 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage B-C | Y | Y | Y | Y | Y | 27380 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage C-A | Y | Y | Y | Y | Y | 27382 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage L-L Avg | Y | Y | Y | Y | Y | 27384 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage A-N | Y | Y | Y | Y | Y | 27386 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage B-N | Y | Y | Y | Y | Y | 27388 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage C-N | Y | Y | Y | Y | Y | 27390 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage N-G | [5 empty] | 27392 | % | 2 | FLOAT32 | R | 0 – 100
|  |  | Min thd Voltage L-N Avg | Y | Y | Y | Y | Y | 27394 | % | 2 | FLOAT32 | R | 0 – 100
|  | Frequency | Min Frequency | Y | Y | Y | Y | Y | 27616 | Hz | 2 | FLOAT32 | R | 42 – 70
| Maximum Values |  |  | Y | Y | Y | Y | Y | 27694 | --- |  | --- | --- | --- | ---
|  | Current |  | Y | Y | Y | Y | Y | 27694 | --- |  | --- | --- | --- | ---
|  |  | Max Current A | Y | Y | Y | Y | Y | 27694 | A | 2 | FLOAT32 | R
|  |  | Max Current B | Y | Y | Y | Y | Y | 27696 | A | 2 | FLOAT32 | R
|  |  | Max Current C | Y | Y | Y | Y | Y | 27698 | A | 2 | FLOAT32 | R
|  |  | Max Current N | Y | Y | Y | Y | Y | 27700 | A | 2 | FLOAT32 | R
|  |  | Max Current G | Y | Y | Y | Y | Y | 27702 | A | 2 | FLOAT32 | R
|  |  | Max Current Avg | Y | Y | Y | Y | Y | 27704 | A | 2 | FLOAT32 | R
|  | Current Unbalance |  | Y | Y | Y | Y | Y | 27706 | --- |  | --- | --- | --- | ---
|  |  | Max Current Unbalance A | Y | Y | Y | Y | Y | 27706 | % | 2 | FLOAT32 | R
|  |  | Max Current Unbalance B | Y | Y | Y | Y | Y | 27708 | % | 2 | FLOAT32 | R
|  |  | Max Current Unbalance C | Y | Y | Y | Y | Y | 27710 | % | 2 | FLOAT32 | R
|  |  | Max Current Unbalance Worst | Y | Y | Y | Y | Y | 27712 | % | 2 | FLOAT32 | R
|  | Voltage |  | Y | Y | Y | Y | Y | 27714 | --- |  | --- | --- | --- | ---
|  |  | Max Voltage A-B | Y | Y | Y | Y | Y | 27714 | V | 2 | FLOAT32 | R
|  |  | Max Voltage B-C | Y | Y | Y | Y | Y | 27716 | V | 2 | FLOAT32 | R
|  |  | Max Voltage C-A | Y | Y | Y | Y | Y | 27718 | V | 2 | FLOAT32 | R
|  |  | Max Voltage L-L Avg | Y | Y | Y | Y | Y | 27720 | V | 2 | FLOAT32 | R
|  |  | Max Voltage A-N | Y | Y | Y | Y | Y | 27722 | V | 2 | FLOAT32 | R
|  |  | Max Voltage B-N | Y | Y | Y | Y | Y | 27724 | V | 2 | FLOAT32 | R
|  |  | Max Voltage C-N | Y | Y | Y | Y | Y | 27726 | V | 2 | FLOAT32 | R
|  |  | Max Voltage, N-G | [5 empty] | 27728 | V | 2 | FLOAT32 | R
|  |  | Max Voltage L-N Avg | Y | Y | Y | Y | Y | 27730 | V | 2 | FLOAT32 | R
|  | Voltage Unbalance |  | Y | Y | Y | Y | Y | 27732 | --- |  | --- | --- | --- | ---
|  |  | Max Voltage Unbalance A-B | Y | Y | Y | Y | Y | 27732 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance B-C | Y | Y | Y | Y | Y | 27734 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance C-A | Y | Y | Y | Y | Y | 27736 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance L-L Worst | Y | Y | Y | Y | Y | 27738 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance A-N | Y | Y | Y | Y | Y | 27740 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance B-N | Y | Y | Y | Y | Y | 27742 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance C-N | Y | Y | Y | Y | Y | 27744 | % | 2 | FLOAT32 | R
|  |  | Max Voltage Unbalance L-N Worst | Y | Y | Y | Y | Y | 27746 | % | 2 | FLOAT32 | R
|  | Power |  | Y | Y | Y | Y | Y | 27748 | --- |  | --- | --- | --- | ---
|  |  | Max Active Power A | Y | Y | Y | Y | Y | 27748 | kW | 2 | FLOAT32 | R
|  |  | Max Active Power B | Y | Y | Y | Y | Y | 27750 | kW | 2 | FLOAT32 | R
|  |  | Max Active Power C | Y | Y | Y | Y | Y | 27752 | kW | 2 | FLOAT32 | R
|  |  | Max Active Power Total | Y | Y | Y | Y | Y | 27754 | kW | 2 | FLOAT32 | R
|  |  | Max Reactive Power A | Y | Y | Y | Y | Y | 27756 | kVAR | 2 | FLOAT32 | R
|  |  | Max Reactive Power B | Y | Y | Y | Y | Y | 27758 | kVAR | 2 | FLOAT32 | R
|  |  | Max Reactive Power C | Y | Y | Y | Y | Y | 27760 | kVAR | 2 | FLOAT32 | R
|  |  | Max Reactive Power Total | Y | Y | Y | Y | Y | 27762 | kVAR | 2 | FLOAT32 | R
|  |  | Max Apparent Power A | Y | Y | Y | Y | Y | 27764 | kVA | 2 | FLOAT32 | R
|  |  | Max Apparent Power B | Y | Y | Y | Y | Y | 27766 | kVA | 2 | FLOAT32 | R
|  |  | Max Apparent Power C | Y | Y | Y | Y | Y | 27768 | kVA | 2 | FLOAT32 | R
|  |  | Max Apparent Power Total | Y | Y | Y | Y | Y | 27770 | kVA | 2 | FLOAT32 | R
|  | Power Factor |  | Y | Y | Y | Y | Y | 27782 | --- |  | --- | --- | --- | ---
|  |  | Max Power Factor A | Y | Y | Y | Y | Y | 27782 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Power Factor B | Y | Y | Y | Y | Y | 27784 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Power Factor C | Y | Y | Y | Y | Y | 27786 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Power Factor Total | Y | Y | Y | Y | Y | 27788 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Displacement Power Factor A | Y | Y | Y | Y | Y | 27790 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Displacement Power Factor B | Y | Y | Y | Y | Y | 27792 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Displacement Power Factor C | Y | Y | Y | Y | Y | 27794 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  |  | Max Displacement PF Total | Y | Y | Y | Y | Y | 27796 | --- | 2 | 4Q FP PF | R | +/- 0.0 – 2.0
|  | Total Harmonic Distortion, Current |  | Y | Y | Y | Y | Y | 27814 | --- |  | --- | --- | --- | ---
|  |  | Max THD Current A | Y | Y | Y | Y | Y | 27814 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | THD = (RMS of harmonics / RMS of fundamental) * 100
|  |  | Max THD Current B | Y | Y | Y | Y | Y | 27816 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Current C | Y | Y | Y | Y | Y | 27818 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Current N | Y | Y | Y | Y | Y | 27820 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Current G | Y | Y | Y | Y | Y | 27822 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Current A | Y | Y | Y | Y | Y | 27824 | % | 2 | FLOAT32 | R | 0 – 100 | 0 | thd = (RMS of harmonics / total RMS) * 100
|  |  | Max thd Current B | Y | Y | Y | Y | Y | 27826 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Current C | Y | Y | Y | Y | Y | 27828 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Current N | Y | Y | Y | Y | Y | 27830 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Current G | Y | Y | Y | Y | Y | 27832 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  | Total Demand Distortion | Max Total Demand Distortion | Y | Y | Y | Y | Y | 27834 | % | 2 | FLOAT32 | R | 0 – 100 | ---
|  | Total Harmonic Distortion, Voltage |  | Y | Y | Y | Y | Y | 27836 | --- |  | --- | --- | --- | ---
|  |  | Max THD Voltage A-B | Y | Y | Y | Y | Y | 27836 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage B-C | Y | Y | Y | Y | Y | 27838 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage C-A | Y | Y | Y | Y | Y | 27840 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage L-L | Y | Y | Y | Y | Y | 27842 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage A-N | Y | Y | Y | Y | Y | 27844 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage B-N | Y | Y | Y | Y | Y | 27846 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage C-N | Y | Y | Y | Y | Y | 27848 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage N-G | [5 empty] | 27850 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max THD Voltage L-N | Y | Y | Y | Y | Y | 27852 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage A-B | Y | Y | Y | Y | Y | 27854 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage B-C | Y | Y | Y | Y | Y | 27856 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage C-A | Y | Y | Y | Y | Y | 27858 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage L-L | Y | Y | Y | Y | Y | 27860 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage A-N | Y | Y | Y | Y | Y | 27862 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage B-N | Y | Y | Y | Y | Y | 27864 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage C-N | Y | Y | Y | Y | Y | 27866 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage N-G | [5 empty] | 27868 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  |  | Max thd Voltage L-N | Y | Y | Y | Y | Y | 27870 | % | 2 | FLOAT32 | R | 0 – 100 | 0
|  | Frequency | Max Frequency | Y | Y | Y | Y | Y | 28092 | Hz | 2 | FLOAT32 | R | 42 – 70
Note on M2030: 11 alarms at 20 registers each
Note on P1: Native Range of Data Type unless noted otherwise.

## Coils
Category | Sub Cat 1 | Sub Cat 2 | Description Access Via Function Code 0x01 and 0x02 | PM5110_11 | PM5310 | PM5330_31 | PM5320 | PM5340_41 | Reference Register | Bit | Coil
Digital IO Status |  |  |  | R | Y | Y | Y | Y
| Digital Inputs |  |  | R | Y | Y | Y | Y
|  | Digital Input Status Validity - Base Unit |  | R | Y | Y | Y | Y
|  |  | Base Unit Digital Input 1 Validity | R | Y | Y | Y | Y | 2400 | 0 | 38400
|  |  | Base Unit Digital Input 2 Validity | R | Y | Y | Y | Y | 2400 | 1 | 38401
|  | Digital Input Status - Base Unit |  | R | Y | Y | Y | Y
|  |  | Base Unit Digital Input 1 | R | Y | Y | Y | Y | 2401 | 0 | 38416
|  |  | Base Unit Digital Input 2 | R | Y | Y | Y | Y | 2401 | 1 | 38417
| Digital Outputs |  |  | R | Y | Y | Y | Y
|  | Digital Output Status Validity - Base Unit |  | R | Y | Y | Y | Y
|  |  | Base Unit Digital Output 1 Validity | R | Y | Y | Y | Y | 2402 | 0 | 38432
|  |  | Base Unit Digital Output 2 Validity | R | Y | Y | Y | Y | 2402 | 1 | 38433
|  |  | Base Unit Digital Output 3 Validity | R | R | Y | R | Y | 2402 | 2 | 38434
|  |  | Base Unit Digital Output 4 Validity | R | R | Y | R | Y | 2402 | 3 | 38435
|  | Digital Output Status - Base Unit |  | R | Y | Y | Y | Y
|  |  | Base Unit Digital Output 1 | R | Y | Y | Y | Y | 2403 | 0 | 38448
|  |  | Base Unit Digital Output 2 | R | Y | Y | Y | Y | 2403 | 1 | 38449
|  |  | Base Unit Digital Output 3 | R | R | Y | R | Y | 2403 | 2 | 38450
|  |  | Base Unit Digital Output 4 | R | R | Y | R | Y | 2403 | 3 | 38451
Detected Alarm Status |  |  |  | Y | Y | Y | Y | Y
| Detected Status |  |  | Y | Y | Y | Y | Y
|  | Standard - 1 second Group 1 Validity |  | Y | Y | Y | Y | Y
|  |  | Over Current, Phase Validity | Y | Y | Y | Y | Y | 2420 | 0 | 38720
|  |  | Under Current, Phase Validity | Y | Y | Y | Y | Y | 2420 | 1 | 38721
|  |  | Over Current, Neutral Validity | Y | Y | Y | Y | Y | 2420 | 2 | 38722
|  |  | Over Current, Ground Validity | Y | Y | Y | Y | Y | 2420 | 3 | 38723
|  |  | Over Voltage, L-L Validity | Y | Y | Y | Y | Y | 2420 | 4 | 38724
|  |  | Under Voltage, L-L Validity | Y | Y | Y | Y | Y | 2420 | 5 | 38725
|  |  | Over Voltage, L-N Validity | Y | Y | Y | Y | Y | 2420 | 6 | 38726
|  |  | Under Voltage, L-N Validity | Y | Y | Y | Y | Y | 2420 | 7 | 38727
|  |  | Over Power, Active Validity | Y | Y | Y | Y | Y | 2420 | 8 | 38728
|  |  | Over Power, Reactive Validity | Y | Y | Y | Y | Y | 2420 | 9 | 38729
|  |  | Over Power, Apparent Validity | Y | Y | Y | Y | Y | 2420 | 10 | 38730
|  |  | Leading Power Factor, True Validity | Y | Y | Y | Y | Y | 2420 | 11 | 38731
|  |  | Lagging Power Factor, True Validity | Y | Y | Y | Y | Y | 2420 | 12 | 38732
|  |  | Leading Power Factor, Displacement Validity | Y | Y | Y | Y | Y | 2420 | 13 | 38733
|  |  | Lagging Power Factor, Displacement Validity | Y | Y | Y | Y | Y | 2420 | 14 | 38734
|  |  | Over Demand, Active Power, Present Validity | Y | Y | Y | Y | Y | 2420 | 15 | 38735
|  | Standard - 1 second Group 1 |  | Y | Y | Y | Y | Y
|  |  | Over Current, Phase | Y | Y | Y | Y | Y | 2421 | 0 | 38736
|  |  | Under Current, Phase | Y | Y | Y | Y | Y | 2421 | 1 | 38737
|  |  | Over Current, Neutral | Y | Y | Y | Y | Y | 2421 | 2 | 38738
|  |  | Over Current, Ground | Y | Y | Y | Y | Y | 2421 | 3 | 38739
|  |  | Over Voltage, L-L | Y | Y | Y | Y | Y | 2421 | 4 | 38740
|  |  | Under Voltage, L-L | Y | Y | Y | Y | Y | 2421 | 5 | 38741
|  |  | Over Voltage, L-N | Y | Y | Y | Y | Y | 2421 | 6 | 38742
|  |  | Under Voltage, L-N | Y | Y | Y | Y | Y | 2421 | 7 | 38743
|  |  | Over Power, Active | Y | Y | Y | Y | Y | 2421 | 8 | 38744
|  |  | Over Power, Reactive | Y | Y | Y | Y | Y | 2421 | 9 | 38745
|  |  | Over Power, Apparent | Y | Y | Y | Y | Y | 2421 | 10 | 38746
|  |  | Leading Power Factor, True | Y | Y | Y | Y | Y | 2421 | 11 | 38747
|  |  | Lagging Power Factor, True | Y | Y | Y | Y | Y | 2421 | 12 | 38748
|  |  | Leading Power Factor, Displacement | Y | Y | Y | Y | Y | 2421 | 13 | 38749
|  |  | Lagging Power Factor, Displacement | Y | Y | Y | Y | Y | 2421 | 14 | 38750
|  |  | Over Demand, Active Power, Present | Y | Y | Y | Y | Y | 2421 | 15 | 38751
|  | Standard - 1 second Group 2 Validity |  | Y | Y | Y | Y | Y
|  |  | Over Demand, Active Power, Last Validity | Y | Y | Y | Y | Y | 2422 | 0 | 38752
|  |  | Over Demand, Active Power, Predicted Validity | Y | Y | Y | Y | Y | 2422 | 1 | 38753
|  |  | Over Demand, Reactive Power, Present Validity | Y | Y | Y | Y | Y | 2422 | 2 | 38754
|  |  | Over Demand, Reactive Power, Last Validity | Y | Y | Y | Y | Y | 2422 | 3 | 38755
|  |  | Over Demand, Reactive Power, Predicted Validity | Y | Y | Y | Y | Y | 2422 | 4 | 38756
|  |  | Over Demand, Apparent Power, Present Validity | Y | Y | Y | Y | Y | 2422 | 5 | 38757
|  |  | Over Demand, Apparent Power, Last Validity | Y | Y | Y | Y | Y | 2422 | 6 | 38758
|  |  | Over Demand, Apparent Power, Predicted Validity | Y | Y | Y | Y | Y | 2422 | 7 | 38759
|  |  | Over Frequency Validity | Y | Y | Y | Y | Y | 2422 | 8 | 38760
|  |  | Under Frequency Validity | Y | Y | Y | Y | Y | 2422 | 9 | 38761
|  |  | Over Voltage Unbalance Validity | Y | Y | Y | Y | Y | 2422 | 10 | 38762
|  |  | Over Voltage Total Harmonic Distortion Validity | Y | Y | Y | Y | Y | 2422 | 11 | 38763
|  |  | Phase Loss Validity | Y | Y | Y | Y | Y | 2422 | 12 | 38764
|  | Standard - 1 second Group 2 |  | Y | Y | Y | Y | Y
|  |  | Over Demand, Active Power, Last | Y | Y | Y | Y | Y | 2423 | 0 | 38768
|  |  | Over Demand, Active Power, Predicted | Y | Y | Y | Y | Y | 2423 | 1 | 38769
|  |  | Over Demand, Reactive Power, Present | Y | Y | Y | Y | Y | 2423 | 2 | 38770
|  |  | Over Demand, Reactive Power, Last | Y | Y | Y | Y | Y | 2423 | 3 | 38771
|  |  | Over Demand, Reactive Power, Predicted | Y | Y | Y | Y | Y | 2423 | 4 | 38772
|  |  | Over Demand, Apparent Power, Present | Y | Y | Y | Y | Y | 2423 | 5 | 38773
|  |  | Over Demand, Apparent Power, Last | Y | Y | Y | Y | Y | 2423 | 6 | 38774
|  |  | Over Demand, Apparent Power, Predicted | Y | Y | Y | Y | Y | 2423 | 7 | 38775
|  |  | Over Frequency | Y | Y | Y | Y | Y | 2423 | 8 | 38776
|  |  | Under Frequency | Y | Y | Y | Y | Y | 2423 | 9 | 38777
|  |  | Over Voltage Unbalance | Y | Y | Y | Y | Y | 2423 | 10 | 38778
|  |  | Over Voltage Total Harmonic Distortion | Y | Y | Y | Y | Y | 2423 | 11 | 38779
|  |  | Phase Loss | Y | Y | Y | Y | Y | 2423 | 12 | 38780
|  | Unary Validity |  | Y | Y | Y | Y | Y
|  |  | Meter Power Up (Control Power Loss) Valdity | Y | Y | Y | Y | Y | 2440 | 0 | 39040
|  |  | Meter Reset Valdity | Y | Y | Y | Y | Y | 2440 | 1 | 39041
|  |  | Meter Diagnostic Valdity | Y | Y | Y | Y | Y | 2440 | 2 | 39042
|  |  | Phase Reversal Valdity | Y | Y | Y | Y | Y | 2440 | 3 | 39043
|  | Unary |  | Y | Y | Y | Y | Y
|  |  | Meter Power Up (Control Power Loss) | Y | Y | Y | Y | Y | 2441 | 0 | 39056
|  |  | Meter Reset | Y | Y | Y | Y | Y | 2441 | 1 | 39057
|  |  | Meter Diagnostic | Y | Y | Y | Y | Y | 2441 | 2 | 39058
|  |  | Phase Reversal | Y | Y | Y | Y | Y | 2441 | 3 | 39059
|  | Digital Group 1 Validity |  | R | Y | Y | Y | Y
|  |  | Digital Alarm DI1 Validity | R | Y | Y | Y | Y | 2442 | 0 | 39072
|  |  | Digital Alarm DI2 Validity | R | Y | Y | Y | Y | 2442 | 1 | 39073
|  | Digital Group 1 |  | R | Y | Y | Y | Y
|  |  | Digital Alarm DI1 | R | Y | Y | Y | Y | 2443 | 0 | 39088
|  |  | Digital Alarm DI2 | R | Y | Y | Y | Y | 2443 | 1 | 39089

## Commands
Subsystem | Command Name | Command Number | Command Tag | PM5110/11 | PM5310 | PM5330/31 | PM5320 | PM5340/41 | Parameters |  |  | User Notes | Allowed for Unprotected Command Interface
REGISTER_ACCESS (0-999) |  |  |  | Y | Y | Y | Y | Y
| Reset Subsystem(s) to Default | 1 | C_RESET_SUBSYS_TO_DEFAULT | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Subsystems) (3) Subsystem ID or -1 (For All Subsystems) |  |  | Subsystem IDs 0 = Register Access 1 = System 2 = Metering 3 = Commands 4 = HMI 5 = Communications 6 = IO 7 = Alarms 8 = Files 9 = Diagnostics 10 = Security
SYSTEM (1000-1999) |  |  |  | Y | Y | Y | Y | Y
| Warm Start Reset | 1000 | C_WARM_START_RESET | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  | This command does not provide a command status or result.
| Reset Power Fail Counter | 1002 | C_RESET_POWER_FAIL_COUNT | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Set Date/Time | 1003 | C_SET_DT | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Year (2000-2127) (3) Month (4) Day of Month (5) Hour (6) Minute (7) Second (8) Millisecond |  |  |  | Y
| Meter Name Setup | 1008 | C_METER_NAME_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2-21 ) Meter Name
| Set IP Parameters Address | 1501 | C_SET_IP_PARAM |  |  |  | Y | Y | (1) Command Semaphore (2-3) IP Address (4-5) Sub net Mask (6-7) Gateway ( For example Eg: 0xC0A8 and 0x0201 for 192.168.2.1) |  |  | This is applicable for meters having Ethernet as only communication Interface
| Set Default IP Param | 1502 | C_SET_IP_DEFAULT |  |  |  | Y | Y | (1) Command Semaphore
METERING (2000-2999) |  |  |  | Y | Y | Y | Y | Y
| Basic Meter Setup | 2000 | C_BASIC_METER_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Number of Phases (3) Number of Wires (4) Power System Configuration (5) Nominal Frequency (6-7) Nominal Voltage (8-9) Nominal Current (10-11) Nominal Power Factor (12) Normal Phase Rotation | (13) Number VTs (14-15) VT Primary (16) VT Secondary (17) Number CTs (18) CT Primary, Phase (19) CT Secondary, Phase (20) CT Primary, Neutral (21) CT Secondary, Neutral (22) CT Location for 1 CT Metering (23) VT Location for 1 VT Metering (24) VT Connection Type
| Demand System Setup | 2002 | C_DMD_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Demand System ID (3) Demand Method (4) Demand Interval Duration (5) Demand Subinterval Duration |  |  | Demand System ID 1 = Power 2 = Current 3 = Input Metering
| Energy Pulse Output Setup | 2003 | C_ENERGY_PULSE_OUTPUT_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Energy Channel (3) Digital Output ID (4-5) Pulse Weight (6) Energy Channel (7) Digital Output ID (8-9) Pulse Weight (10) Energy Channel (11) Digital Output ID (12-13) Pulse Weight |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 99 = Energy LED For PM5110/11 reference below parameters not applicable 1 = Digital Output S01 99 = Energy LED (10) Energy Channel = NaN (11) Digital Output ID = NaN (12-13) Pulse Weight = NaN
| Reset Cycle Count | 2007 | C_RESET_CYCLE_COUNT | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Multi-tariff Metering Control | 2008 | C_MULTITARIFF_CONTROL |  | Y | Y | Y | Y | (1) Command Semaphore (2) Active Rate (0-8) |  |  |  | Y
| Reset All Min/Max | 2009 | C_RESET_ALL_MIN_MAX | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset Active Load Timer | 2010 | C_RESET_ACTIVE_LOAD_TIMER | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset All Demands | 2011 | C_RESET_ALL_DMDS | Y | Y | Y | Y | Y | (1) Command Semaphore (2-5) Demand Reset Password |  |  | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset Current Demand | 2012 | C_RESET_CUR_DMD | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset Power Demand | 2013 | C_RESET_POWER_DMD | Y | Y | Y | Y | Y | (1) Command Semaphore (2-5) Demand Reset Password |  |  | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset All Peak Demands | 2015 | C_RESET_ALL_PEAK_DMDS | Y | Y | Y | Y | Y | (1) Command Semaphore (2-5) Demand Reset Password |  |  | The Demand Reset Password is verified if Revenue Security is active. | Y
| Reset Current Peak Demands | 2016 | C_RESET_CUR_PEAK_DMDS | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset Power Peak Demands | 2017 | C_RESET_POWER_PEAK_DMDS | Y | Y | Y | Y | Y | (1) Command Semaphore (2-5) Demand Reset Password |  |  | The Demand Reset Password is verified if Revenue Security is active. | Y
| Start New Demand Interval | 2019 | C_START_NEW_DMD_INTERVAL | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Bitmap of Demand Systems |  |  |  | Y
| Reset All Energies | 2020 | C_RESET_ALL_ENERGIES | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset All Accumulated Energies | 2021 | C_RESET_ALL_ACC_ENG | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset All Time-of-Use Multi-Tariff Energies | 2022 | C_RESET_ALL_TOU_MT_ENG |  | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset All Energy Pulse Output Channels | 2024 | C_RESET_ALL_ENG_PULSE_OUTPUT | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Meter Initialization | 2037 | C_METER_INIT | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  | Resets Energy, Demand, Demand peaks, Min/Max, Alarm counters, Alarm logs, Alarm event queue, IO Counters, IO Timers, Active Load Timer, Comm diagnostics, power fail counter, cycle counter Data logs (Scout only), and Waveform capture Files (Scout only).
| Energy / Alarm LED Enable | 2039 | C_ENERGY_LED_ENABLE | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 0 = Disable / 1 = Alarm / 2 = Energy
| TDD Setup | 2043 | C_TDD_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2-3) Peak Current Demand Over Last Year
| Active Load Timer Setup | 2044 | C_ACTIVE_LOAD_TIMER_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2-3) Active Load Timer Setpoint
| Set Multi-Tariff Mode | 2053 | C_MULTI_TARIFF_MODE |  | Y | Y | Y | Y | (1) Command Semaphore (2) Mode |  |  |  | N
| Set Multi-Tariff Rate Command | 2054 | C_MULTI_TARIFF_RATE |  | Y | Y | Y | Y | (1) Command Semaphore (2) Active Rate 0-8 |  |  | Only allow if mode is Command | Y
| Set Multi-Tariff Time of Day | 2055 | C_MULTI_TARIFF_TOD |  | Y | Y | Y | Y | (1) Command Semaphore (2) RATE 1 Day Type (3) RATE 1 Start Time (4) RATE 1 End Time (5) RATE 2 Day Type (6) RATE 2 Start Time (7) RATE 2 End Time (8) RATE 3 Day Type (9) RATE 3 Start Time (10) RATE 3 End Time (11) RATE 4 Day Type (12) RATE 4 Start Time (13) RATE 4 End Time (14) RATE 5 Day Type (15) RATE 5 Start Time (16) RATE 5 End Time (17) RATE 6 Day Type (18) RATE 6 Start Time (19) RATE 6 End Time (20) RATE 7 Day Type (21) RATE 7 Start Time (22) RATE 7 End Time (23) RATE 8 Day Type (24) RATE 8 Start Time (25) RATE 8 End Time | (26) RATE 1 Start Month (27) RATE 1 Start Day (28) RATE 1 End Month (29) RATE 1 End Day (30) RATE 2 Start Month (31) RATE 2 Start Day (32) RATE 2 End Month (33) RATE 2 End Day (34) RATE 3 Start Month (35) RATE 3 Start Day (36) RATE 3 End Month (37) RATE 3 End Day (38) RATE 4 Start Month (39) RATE 4 Start Day (40) RATE 4 End Month (41) RATE 4 End Day (42) RATE 5 Start Month (43) RATE 5 Start Day (44) RATE 5 End Month (45) RATE 5 End Day (46) RATE 6 Start Month (47) RATE 6 Start Day (48) RATE 6 End Month (49) RATE 6 End Day | (50) RATE 7 Start Month (51) RATE 7 Start Day (52) RATE 7 End Month (53) RATE 7 End Day (54) RATE 8 Start Month (55) RATE 8 Start Day (56) RATE 8 End Month (57) RATE 8 End Day |  | N
| Set Time for Demand Synch | 2063 | C_DMD_SYNCH_TIME | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Synch Time |  |  | Time is 0000 to 2359 | N
HMI (4000-4999) |  |  |  | Y | Y | Y | Y | Y
| HMI Setup | 4000 | C_HMI_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2) HMI Contrast Setting (3) HMI Backlight On/Off (4) HMI Language (5) HMI IEC/IEEE Mode (6) HMI Date Format (7) HMI Time Format (8) HMI Backlight Timeout (9) HMI Screen Timeout (10) HMI Energy Resolution (11) HMI Current Resolution (12) HMI Voltage Resulution (13) HMI Power Resolution
COMMUNICATIONS (5000-5999) |  |  |  | Y | Y | Y
| Communications Setup | 5000 | C_COMMS_SETUP | Y | Y | Y |  |  | (1) Command Semaphore (2) Communications Port ID (3) RS-485 Comm Port (M/S) Protocol (4) RS-485 Comm Port (M/S) Address (5) RS-485 Comm Port (M/S) Baud Rate (6) RS-485 Comm Port (M/S) Parity (7) RS-485 Comm Port (M/S) Modbus ASCII Default Timeout |  |  | Communications Port ID 1 = Standard RS-485 | Y
| Reset Comm Port Counters | 5001 | C_RESET_COMM_CHANNEL_COUNT | Y | Y | Y |  |  | (1) Command Semphore (2) Communications Port ID |  |  | Communications Port ID 1 = Standard RS-485 | Y
IO (6000-6999) |  |  |  | Y | Y | Y | Y | Y
| Digital Output Setup | 6000 | C_DO_SETUP |  | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Output ID (3-22) Label (23) Behavioral Mode (24) On Time For Timed Mode |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay)
| Digital Input Setup | 6001 | C_DI_SETUP |  | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Input ID (3-22) Label (23) Debounce Time |  |  | Digital Input ID 1 = Digital Input S01 2 = Digital Input S02
| De-energize Digital Output | 6002 | C_DE_ENERGIZE_DO | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Output ID |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay) | Y
| Energize Digital Output | 6003 | C_ENERGIZE_DO | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Output ID |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay) | Y
| Release Digital Output From Coil Hold | 6004 | C_RELEASE_DO_FROM_COIL_HOLD |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay) | Y
| Release Digital Output From Override Control | 6005 | C_RELEASE_DO_FROM_OVERRIDE |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay)
| Place Digital Output In Override Control | 6006 | C_PLACE_DO_IN_OVERRIDE |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02
| Reset Operation Counter for Digital Output | 6007 | C_RESET_COUNT_FOR_DO |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay) | Y
| Reset On-Time for Digital Output | 6008 | C_RESET_ON_TIME_FOR_DO |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Outputs) (3) Digital Output ID or -1 (For All Digital Outputs) |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay) | Y
| Reset Operation Counter for Digital Input | 6009 | C_RESET_COUNT_FOR_DI |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Inputs) (3) Digital Input ID or -1 (For All Digital Inputs) |  |  | Digital Input ID 1 = Digital Input S01 2 = Digital Input S02 | Y
| Reset On-Time for Digital Input | 6010 | C_RESET_ON_TIME_FOR_DI |  | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Digital Inputs) (3) Digital Input ID or -1 (For All Digital Inputs) |  |  | Digital Input ID 1 = Digital Input S01 2 = Digital Input S02 | Y
| Setup Digital Input to Demand Associations | 6011 | C_DI_SETUP_DEMAND |  | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Input ID for Demand System 1 (3) Digital Input ID for Demand System 2 (4) Digital Input ID for Demand System 3 (5) Digital Input ID for Demand System 4 (6) Digital Input ID for Demand System 5 (7) Digital Input ID for Demand System 6
| Setup Digital Output to Demand Associations | 6012 | C_DO_SETUP_DEMAND |  | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Output ID for Demand System 1 (3) Digital Output ID for Demand System 2 (4) Digital Output ID for Demand System 3 (5) Digital Output ID for Demand System 4 (6) Digital Output ID for Demand System 5 (7) Digital Output ID for Demand System 6
| Setup Digital Input to Multi-Tariff Associations | 6013 | C_DI_SETUP_MULTI_TARIFF |  | Y | Y | Y | Y | (1) Command Semaphore (2) Number of Multi-tariff Rates Active (3) Number of Digital Inputs Used to Control Multi-tariff |  |  |  | N
| De-energize Digital Output While in Override | 6015 | C_DE_ENERGIZE_DO_OVERRIDE |  | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Output ID |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay)
| Energize Digital Output While in Override | 6016 | C_ENERGIZE_DO_OVERRIDE |  | Y | Y | Y | Y | (1) Command Semaphore (2) Digital Output ID |  |  | Digital Output ID 1 = Digital Output S01 2 = Digital Output S02 3 = Digital Output S03(Relay) 4 = Digital Output S04(Relay)
ALARMS (7000-7999) |  |  |  | Y | Y | Y | Y | Y
| Over/Under Alarm Setup | 7000 | C_OVR_UND_ALM_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Alarm ID (3) Priority (0=None, 1=High, 2=Medium, 3=Low) (4) Setpoints (0 = Fixed, 1 = Variable) (5) Learning (0 = Not Learning, 1 = Learning) (6) Enable (0 = Disabled, 1 = Enabled) (7-8) Pickup Setpoint (9-10) Pickup Time Delay (11-12) Dropout Setpoint (13-14) Dropout Time Delay (15) Digital Outputs to Associate - Standard | (16-19) Digital Outputs to Associate - Options (Scout Only) (20) Datalogs to Trigger (Scout Only) (21) Waveform Capture to Trigger (Scout Only) |  | Alarm ID 1 = Over Current, Phase 2 = Under Current, Phase 3 = Over Current, Neutral 4 = Over Current, Ground 5 = Over Voltage, L-L 6 = Under Voltage, L-L 7 = Over Voltage, L-N 8 = Under Voltage, L-N 9 = Over Power, Active 10 = Over Power, Reactive 11 = Over Power, Apparent 12 = Leading Power Factor, True 13 = Lagging Power Factor, True 14 = Leading Power Factor, Displacement 15 = Lagging Power Factor, Displacement 16 = Over Demand, Active Power, Present 17 = Over Demand, Active Power, Last 18 = Over Demand, Active Power, Predicted 19 = Over Demand, Reactive Power, Present 20 = Over Demand, Reactive Power, Last 21 = Over Demand, Reactive Power, Predicted 22 = Over Demand, Apparent Power, Present 23 = Over Demand, Apparent Power, Last 24 = Over Demand, Apparent Power, Predicted 25 = Over Frequency 26 = Under Frequency 27 = Over Voltage Unbalance 28 = Over Voltage Total Harmonic Distortion 29 = Phase Loss 41 = Custom Alarm 1 42 = Custom Alarm 2 43 = Custom Alarm 3 44 = Custom Alarm 4 45 = Custom Alarm 5 46 = Custom Alarm 6 47 = Custom Alarm 7 48 = Custom Alarm 8 49 = Custom Alarm 9 50 = Custom Alarm 10
| Reset Alarm Counters | 7002 | C_RESET_ALM_COUNT | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Alarm Counters) (3) Alarm Counter ID or -1 (For All Alarm Counters) |  |  | Alarm ID 1-29 1-Second Standard 41-50 1-Second Custom 101-104 Unary 111-114 Digital
| Acknowledge Alarms | 7003 | C_ACK_ALMS | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Alarms) (3) Alarm ID or -1 (For All Alarms) |  |  |  | Y
| Disable Alarms | 7004 | C_DISABLE_ALMS | Y | Y | Y | Y | Y | (1) Command Semaphore (2) 1 or -1 (For All Alarms) (3) Alarm ID or -1 (For All Alarms)
| Reset Aggregated Alarm History | 7005 | C_RESET_REG_BASED_ALM_LOG | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Reset Event Queue | 7006 | C_RESET_EVENT_QUEUE | Y | Y | Y | Y | Y | (1) Command Semaphore |  |  |  | Y
| Digital Alarm Setup | 7007 | C_DIGITAL_ALARM_SETUP |  | Y | Y | Y | Y | (1) Command Semaphore (2) Alarm ID (3) Priority (0=None, 1=High, 2=Medium, 3=Low) (4) Enable (0 = Disabled, 1 = Enabled) (5) Subtype (0 = Off, 1 = On) (6-7) Pickup Time Delay (8-9) Dropout Time Delay (10) Digital Outputs to Associate - Standard | (11-14) Digital Outputs to Associate - Options (Scout Only) (15) Datalogs to Trigger (Scout Only) (16) Waveform Capture to Trigger (Scout Only) |  | Alarm ID 111 = Digital Input S01 112 = Digital Input S02 113 = Digital Input S03 114 = Digital Input S04
| Unary Alarm Setup | 7008 | C_UNARY_ALARM_SETUP | Y | Y | Y | Y | Y | (1) Command Semaphore (2) Alarm ID (3) Priority (0=None, 1=High, 2=Medium, 3=Low) (4) Enable (0 = Disabled, 1 = Enabled) (5) Digital Outputs to Associate - Standard | (6-9) Digital Outputs to Associate - Options (Scout Only) (10) Datalogs to Trigger (Scout Only) (11) Waveform Capture to Trigger (Scout Only) |  | Alarm ID 101 = Meter Power Up (Control Power Loss) 102 = Meter Reset 103 = Meter Diagnostics 104 = Phase Reversal
FILES (8000-8999)
| Enable Data Log | 8001 | C_ENABLE_DATA_LOG | Y | Y | Y | Y | Y | (1) Command Semaphore (2) File ID (3) Enable/Disable (0=Disable, 1=Enable)
| Setup Data Log | 8002 | C_SETUP_DATA LOG | Y | Y | Y | Y | Y | (1) Command Semaphore (2) File ID (3) Record Management Method (4) Topic List Reference (5) Start time (6) Stop time (7) Interval Control minutes (1,5,10,15,30,60,1440) (8) ID Item 1 (9) ID Item 2 (10) ID Item 3 (11) ID Item 4 (12) ID Item 5 (13) ID Item 6 (14) ID Item 7 (15) ID Item 8 (16) ID Item 9 (17) ID Item 10 (18) ID Item 11 (19) ID Item 12 (20) ID Item 13 (21) ID Item 14
| Clear Data Log | 8003 | C_CLEAR_DATA_LOG | Y | Y | Y | Y | Y | (1) Command Semaphore (2) File ID

## Data Types
Data Type | Description | Native Range | N/A Value | Notes
UTF8 | Alphanumeric | 0-3 bytes | 0x00
INT16 | Signed Integer, 16 bits | -32,768 - 32,767 | 0x8000
INT16U | Unsigned Integer, 16 bits | 0 - 65,535 | 0xFFFF
INT32 | Signed Integer, 32 bits | -2,147,483,648 – 2,147,483,647 | 0x80000000
INT32U | Unsigned Integer, 32 bits | 0 - 4,294,967,295 | 0xFFFFFFFF
INT64 | Signed Integer, 64 bits |  | 0x8000000000000000
FLOAT32 | Floating Point, 32 bits | +/- 1*10^38 | 0xFFC00000
FLOAT64 | Floating Point, 64 bits | +/-1.798*10^308 | 0xFFF8000000000000
BITMAP |  |  | 0x8000 Example for a status bitmap 1 register long. | For status bitmaps that are multiple registers long, the most significant bit will be set to indicate the entire bitmap is N/A.This does not apply to configuration bitmaps. So, in setup commands that include a bitmap as a parameter, the user must always include the desired value for these bitmaps.
DATETIME | DateTime | 1/1/2000 – 12/31/2127 | 0xFFFFFFFFFFFFFFFF | DateTime coding format using 4 words as per IEC 870-5-4 Word 1 b0-b6: Year (0 - 127) b7-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved Word 3 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 4 b0-b15: Millisecond (0 - 59999)
DATE | Date |  | 0xFFFFFFFF | Word 1 b0-b7: Year (0 - 99) b8-b15: Reserved Word 2 b0-b4: Day (1-31) b5-b7: Weekday (1-7, 0 if not used) b8-b11: Month (1-12) b12-b15: Reserved
TIME | Time |  | 0xFFFFFFFF | Word 1 b0-b5: Minutes (0-59) b6: Reserved b7: Time synchronization quality, 1 = non valid or non synchronization b8-b12: Hour (0-23) b13-b14: Reserved b15: 0 = Standard time, 1 = Daylight Savings Time Word 2 b0-b15: Millisecond (0 - 59999)
PORTAL | A portal provides a means to access data of a size up to 125 registers by doing a Modbus block read of a single register. This allows large data sets to be accessed without using a large number of registers. An example might be a data type of PORTAL100 located at register 1000. In order to read the 100 registers, the user would do a block read of 100 registers beginning at register 1000. The data at PORTAL100 could be stored in an internal format and presented to the user by the meter communications firmware as 100 16 bit quantities.
4Q FP PF | Four Quadrant Floating Point Power Factor | -2 - 2 | 0xFFC00000 | Power factor values are specially encoded floating point values. Angle of complex power = power factor register value 0° = 1 90° = 0 180° = -1 270° = 2 Q1: 0 < x < 1 Q2: -2 < x < -1 Q3: -1 < x < 0 Q4: 1 < x < 2 Pseudo code to decode PF Value if (rigVal > 1) { PF_Val = 2 - regVal; PF is leading } else if (regVal < -1) { PF_Val = -2-regVal PF is leading } else if ( abs(regVal) equals 1 ) { PF_Val = regVal PF is at unity } else { PF_Val = regVal PF is lagging }

## Units Codes
Code | Abbreviation | Description
0 |  | No Units
1 | % | Percentage
2 | °C | Degrees Celsius
3 | °F | Degrees Fahrenheit
4 | Deg | Degrees Angular
5 | Hz | Hertz
6 | A | amperes
7 | kA | Kilo Amperes
8 | V | Volts
9 | kV | Kilo Volts
10 | MV | Mega Volts
11 | W | Watts
12 | kW | Kilowatts
13 | MW | Megawatts
14 | VAR | Volt-Ampere Reactive
15 | kVAR | Kilo Volt-Ampere Reactive
16 | MVAR | Mega Volt-Ampere Reactive
17 | VA | Volt-Amperes
18 | kVA | Kilo Volt-Amperes
19 | MVA | Mega Volt-Amperes
20 | WH | Watt-Hour
21 | kWH | Kilowatt-Hour
22 | MWH | Megawatt-Hour
23 | VARH | Reactive Volt-Ampere Hour
24 | kVARH | Reactive Kilo Volt-Ampere Hour
25 | MVARH | Reactive Mega Volt-Ampere Hour
26 | VAH | Volt-Ampere Hours
27 | kVAH | Kilo Volt-Ampere Hours
28 | MVAH | Mega Volt-Ampere Hours
29 | Seconds | Seconds
30 | Minutes | Minutes
31 | Hours | Hours
32 | Bytes (RAM) | Bytes
33 | kBytes (RAM) | Kilobytes
34 | $ | Dollars
35 | gal | gallons
36 | gal/hr | gallons/hour
37 | gal/min | gallons/minute
38 | cfm | cubic feet/min
39 | PSI | PSI
40 | BTU | BTU
41 | L | liters
42 | ton-hours | ton-hours
43 | l/hr | liters/hour
44 | l/min | liters/min
45 | € | Euros
46 | ms | Milliseconds
47 | m³ | cubic-meters
48 | m³/sec | cubic-meters/sec
49 | m³/min | cubic-meters/min
50 | m³/hr | cubic-meters/hour
51 | Pa | pascals
52 | Bars | bar
53 | RPM | Revolutions/min
55 | BTU/hr | BTU/hour
56 | PSIG | Pounds/square inch gauge
57 | SCFM | Standard cubic feet/min
58 | MCF | Thousand cubic feet
59 | Therm | Therm
60 | SCFH | Standard cubic feet/hour
61 | PSIA | pounds/square inch absolute
62 | lbs | pounds
63 | kg | Kilogram
64 | klbs | Kilopounds
65 | lb/hr | pound/hour
66 | ton/hr | ton/hour
67 | kg/hr | Kilogram/hour
68 | in. Hg | inch of Mercury
69 | kPa | kiloPascals
70 | %RH | percentage of relative humidity
71 | MPH | miles per hour
72 | m/sec | meters/sec
73 | mV/cal/(cm²/min) | milliVolts/calorie/(square centimeters/min)
74 | in | inches
75 | mm | millimeter
76 | GWH | GigaWatt-Hour
77 | GVARH | Reactive Giga Volt-Ampere Hour
78 | GVAH | Giga Volt-Ampere Hours
79 | AH | Ampere-Hours
80 | kAH | Kiloamp-Hours
81 | Therm/hr | Therm/hour

## Alarm Attributes
Alarm Attributes
| type |  | subtype |  | parameter |  | modifier |  | phases |  | level |  | priority |  | setpoints |  | learning |  | enable
| Bits 28-31 |  | Bits 23-27 |  | Bits 17-22 |  | Bits 11-16 |  | Bits 07-10 |  | Bits 05-06 |  | Bits 03-04 |  | Bit 02 |  | Bit 01 |  | Bit 00
0 | NONE | 0 | NONE | 0 | NONE | 0 | NONE | 0 | NONE | 0 | LEVEL0 | 0 | NONE | 0 | FIXED | 0 | NOT_LEARNING | 0 | DISABLED
1 | STANDARD1S | 1 | OVER SIGNED | 1 | VOLTAGE | 1 | 1 | 1 | A | 1 | LEVEL1 | 1 | HIGH | 1 | VARIABLE | 1 | LEARNING | 1 | ENABLED
2 | CUSTOM1S | 2 | UNDER SIGNED | 2 | CURRENT | 2 | 2 | 2 | B | 2 | LEVEL2 | 2 | MEDIUM
3 | STANDARDHS | 3 | LEADING | 3 | ACTIVE_POWER | 3 | 3 | 3 | C | 3 | LEVEL3 | 3 | LOW
4 | CUSTOMHS | 4 | LAGGING | 4 | REACTIVE_POWER | 4 | 4 | 4 | AB
5 | DISTURBANCE | 5 | PHASELOSS | 5 | APPARENT_POWER | 5 | 5 | 5 | BC
6 | TRANSIENT | 6 | PHASEREV | 6 | FREQUENCY | 6 | 6 | 6 | CA
7 | WAVESHAPE | 7 | REVPOWER | 7 | POWER_FACTOR | 7 | 7 | 7 | ABC
8 | UNARY | 8 | POWERUP | 8 | STANDARD | 8 | 8 | 8 | N
9 | DIGITAL | 9 | RESET | 9 | OPTION_SLOT_A | 9 | 9 | 9 | G
A | BINARY | A | DIAGNOSTIC | A | OPTION_SLOT_B | A | 10 | A | NG
B | TIME_OF_DAY | B | OFF2ON | B | OPTION_SLOT_C | B | 11 | B | 3PHASE_TOTAL
C | LOGIC | C | ON2OFF | C | OPTION_SLOT_D | C | 12 | C | NOT_USED
D |  | D | SWELL | D | SELF_TEST | D | 13 | D | NOT_USED
E |  | E | SAG | E | HARMONIC | E | 14 | E | NOT_USED
F |  | F | AND | F | INTERHARMONIC | F | 15 | F | NOT_USED
|  | 10 | NAND | 10 | K_FACTOR | 10 | 16
|  | 11 | OR | 11 | FLICKER | 11 | PHASE
|  | 12 | NOR | 12 | ENERGY | 12 | NEUTRAL
|  | 13 | XOR | 13 | DATETIME | 13 | GROUND
|  | 14 | NOT | 14 | TEMPERATURE | 14 | LN
|  | 15 | OVER ABSOLUTE | 15 | INPUT_METERING_1 | 15 | LL
|  | 16 | UNDER ABSOLUTE | 16 | INPUT_METERING_2 | 16 | THD
|  | 17 |  | 17 | INPUT_METERING_3 | 17 | UNBALANCE
|  | 18 |  | 18 | INPUT_METERING_4 | 18 | TRUE
|  | 19 |  | 19 | INPUT_METERING_5 | 19 | DISPLACEMENT
|  | 1A |  | 1A | INPUT_METERING_6 | 1A | DEMAND_LAST
|  | 1B |  | 1B | INPUT_METERING_7 | 1B | DEMAND_PREDICTED
|  | 1C |  | 1C | INPUT_METERING_8 | 1C | DEMAND_PRESENT
|  | 1D |  | 1D | INPUT_METERING_9 | 1D | RMS
|  | 1E |  | 1E | INPUT_METERING_10 | 1E | FUNDAMENTAL
|  | 1F | NOT_USED | 1F |  | 1F | ANGLE
|  |  |  | 20 |  | 20 | DEMAND_PEAK
|  |  |  | 21 |  | 21 | CREST_FACTOR
|  |  |  | 22 |  | 22 | DISTORTION
|  |  |  | 23 |  | 23 | INSTANTANEOUS
|  |  |  | 24 |  | 24 | SHORT_TERM
|  |  |  | 25 |  | 25 | LONG_TERM
|  |  |  | 26 |  | 26 | POSITIVE_SEQUENCE
|  |  |  | 27 |  | 27 | NEGATIVE_SEQUENCE
|  |  |  | 28 |  | 28 | ZERO_SEQUENCE
|  |  |  | 29 |  | 29 | TREND
|  |  |  | 2A |  | 2A | 3_PHASE
|  |  |  | 2B |  | 2B | ACCUMULATED
|  |  |  | 2C |  | 2C | CONDITIONAL
|  |  |  | 2D |  | 2D | INCREMENTAL
|  |  |  | 2E |  | 2E | TOU_RATE_1
|  |  |  | 2F |  | 2F | TOU_RATE_2
|  |  |  | 30 |  | 30 | TOU_RATE_3
|  |  |  | 31 |  | 31 | TOU_RATE_4
|  |  |  | 32 |  | 32
|  |  |  | 33 |  | 33
|  |  |  | 34 |  | 34
|  |  |  | 35 |  | 35
|  |  |  | 36 |  | 36
|  |  |  | 37 |  | 37
|  |  |  | 38 |  | 38
|  |  |  | 39 |  | 39
|  |  |  | 3A |  | 3A
|  |  |  | 3B |  | 3B
|  |  |  | 3C |  | 3C
|  |  |  | 3D | USER_DEFINED1 | 3D | USER_DEFINED1
|  |  |  | 3E | USER_DEFINED2 | 3E | USER_DEFINED2
|  |  |  | 3F | USER_DEFINED3 | 3F | USER_DEFINED3

## Event Codes
Event Code
| category |  | eventType |  | phases |  | direction
| Bits 12-15 |  | Bits 08-11 |  | Bits 04-07 |  | Bits 00-03
0 |  | 0 | NONE | 0 | NONE | 0 | DDD_NONE
1 |  | 1 | UNARY | 1 | A | 1 | DDD_UNKNOWN
2 |  | 2 | PICKUP | 2 | B | 2 | DDD_UPSTREAM_LOW
3 |  | 3 | DROPOUT | 3 | C | 3 | DDD_UPSTREAM_MEDIUM
4 |  | 4 | COMPRESSED_PICKUP | 4 | AB | 4 | DDD_UPSTREAM_HIGH
5 |  | 5 | COMPRESSED_DURATION | 5 | BC | 5 | DDD_DOWNSTREAM_LOW
6 |  | 6 | COMPRESSED_VALUE | 6 | CA | 6 | DDD_DOWNSTREAM_MEDIUM
7 |  | 7 | AGGREGATED_PICKUP | 7 | ABC | 7 | DDD_DOWNSTREAM_HIGH
8 |  | 8 | AGGREGATED_DURATION | 8 | N | 8
9 |  | 9 | AGGREGATED_VALUE | 9 | G | 9
A |  | A | P1 ACKNOWLEDGED | A | NG | A
B |  | B | DIGITAL_OUTPUT_ASSOCIATED | B |  | B
C |  | C | FILES_ASSOCIATED | C |  | C
D |  | D | WFC_ASSOCIATED | D |  | D
E |  | E |  | E |  | E
F | ALARM_EVENT | F |  | F |  | F