## Instructions
MFR82761 | 03/2019 | ATVxxx - Communication Parameters
/!\ WARNING
UNEXPECTED MOVEMENT
Drive systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this drive system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
/!\ WARNING
LOSS OF CONTROL
• The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code:
Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name:
Parameter designation
Logic address:
Addresses for Modbus, Profibus, Profinet and Ethernet TCP
Address for the messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index:
Addresses for CANopen, PowerLink and EtherCAT.
CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
DeviceNet path:
Address for DeviceNet and Ethernet IP.
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link:
- For WORD (listing), a dynamic link opens its description. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
- For WORD (bit register), in the Type column, a dynamic link opens its description.
Category:
Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access:
Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units:
Physical unit and multiplier.
Factory setting:
Value of the parameter set at the factory.
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range:
Possible values.
Display:
Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order:
Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 |  | Control parameters | R/W | WORD (BitString16) | -
CMD | Command register | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 |  | Control parameters | R/W | WORD (BitString16) | - |  |  | [Cmd Register] (CMD) | [Communication map] (CMM)
RPR | Time counter reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] NO |  | [Time Counter Reset] (RPR) | [Counter Management] (ELT) [V0_SubmenuCounterManagement] (COMA) [Maintenance] (CSMA)
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 |  | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | -32767 rpm ... 32767 rpm
LFR | Reference frequency | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 |  | Setpoint parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -300.0 Hz ... 300.0 Hz | [Ref Frequency] (LFR) | [Drive parameters] (MPI)
PISP | PIDSet Point | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000
AIV1 | AIV1 Image input | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -8192 ... 8192 | [AIV1 Image input] (AIV1) | [Drive parameters] (MPI)
MFR | Multiplying coefficient | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFR) | [Drive parameters] (MPI) [Settings] (SET)
ETA | CIA402 State Register | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 |  | Status parameters | R | WORD (BitString16) | - |  |  | [CIA402 State Reg] (ETA) | [Communication map] (CMM)
HMIS | Drive state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | - |  |  | [Drive State] (HMIS) | [System] (DST)
ETI | Internal State Register | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 |  | Status parameters | R | WORD (BitString16) | -
CRC | Channel for reference frequency | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 |  | Status parameters | R | WORD (BitString16) | -
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 |  | Status parameters | R | WORD (BitString16) | -
CNFS | Active configuration | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  |  | [Config. active] (CNFS) | [Drive parameters] (MPI)
STUN | Tune selection | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Tune selection] (STUN) | [Simply start] (SIM) [Motor tune] (MTU)
STUR | Autotuning flux status | 16#2669 = 9833 | 16#2044/22 | 16#92/01/22 = 146/01/34 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Autotuning Flux Status] (STUR) | [Autotuning flux] (TUNR)
TUNV | Autotuning flux verification value | 16#266B = 9835 | 16#2044/24 | 16#92/01/24 = 146/01/36 |  | Status parameters | R/W | UINT (Unsigned16) | 1 % | 65535 % | 0 % ... 65535 % | [Autotuning flux verif] (TUNV) | [Autotuning flux] (TUNR)
SMOT | Status of motor tune in term of saliency | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  |  | [Saliency mot. state] (SMOT) | [Motor tune] (MTU)
ECSS | EtherCAT slave status | 16#1A22 = 6690 | 16#2024/5B | 16#82/01/5B = 130/01/91 | ETST | Status parameters | R/W | WORD (Enumeration) | - |  |  | [EthCat slave status] (ECSS) | [EtherCAT Module] (ETC)
ECAA | EtherCAT address | 16#1A24 = 6692 | 16#2024/5D | 16#82/01/5D = 130/01/93 |  | Status parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat addr] (ECAA) | [EtherCAT Module] (ETC)
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 |  | Actual values parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
RFR | Motor frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor Frequency] (RFR) | [M/S Local Display] (MSO) [Drive parameters] (MPI)
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (OTR) | [Motor parameters] (MMO)
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Current] (LCR) | [System] (DST) [Motor parameters] (MMO)
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [Motor parameters] (MMO)
OPR | Motor power | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Power] (OPR) | [Motor parameters] (MMO)
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FRH | Reference frequency before ramp | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -300.0 Hz ... 300.0 Hz | [Pre-Ramp Ref Freq] (FRH) | [System] (DST) [Drive parameters] (MPI) [Communication map] (CMM)
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
RPC | PID reference | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 |  | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [PID reference] (RPC) | [PID display] (PIC)
RPF | PID feedback | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 |  | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [PID feedback] (RPF) | [PID display] (PIC) [PID Feedback] (FDB) [PID Feedback] (FDB)
RPE | PID Error | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 |  | Reference parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [PID Error] (RPE) | [PID display] (PIC)
RPO | PID Output | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (RPO) | [PID display] (PIC)
ULN | Mains voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN) | [Drive parameters] (MPI)
THD | Drive thermal state | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drive Therm State] (THD) | [Drive parameters] (MPI)
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor Therm State] (THR) | [System] (DST) [Motor parameters] (MMO)
RTH | Motor run time | 16#0CAC = 3244 | 16#2002/2D | 16#71/01/2D = 113/01/45 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Motor Run Time] (RTH) | [Variable Speed Pump] (MPP) [Counter Management] (ELT) [Diag. data] (DDT)
PTH | Power-on time | 16#0CAE = 3246 | 16#2002/2F | 16#71/01/2F = 113/01/47 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Power-on time] (PTH) | [Counter Management] (ELT)
QFP0 | Number of QF1 starts | 16#0CD2 = 3282 | 16#2002/53 | 16#71/01/53 = 113/01/83 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [QF1 Nb Of Starts] (QFP0) | [Counter Management] (ELT) [V0_SubmenuCounterManagement] (COMA)
QFP3 | Number of QF3 starts | 16#0CD4 = 3284 | 16#2002/55 | 16#71/01/55 = 113/01/85 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [QF3 Nb Of Starts] (QFP3) | [Counter Management] (ELT) [V0_SubmenuCounterManagement] (COMA)
QFP4 | Number of QF91 starts | 16#0CD6 = 3286 | 16#2002/57 | 16#71/01/57 = 113/01/87 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [QF91 Nb Of Starts] (QFP4) | [Counter Management] (ELT) [V0_SubmenuCounterManagement] (COMA)
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 |  | I/O parameters | R | WORD (BitString16) | -
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 |  | I/O parameters | R/W | WORD (BitString16) | -
AI1C | Physical value AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2C | Physical value AI2 | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3C | Physical value AI3 | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1C | AQ1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
FQS | Pulse input measured frequency | 16#390B = 14603 | 16#2074/4 | 16#AA/01/04 = 170/01/04 |  | I/O parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 30000 Hz | [Measured Freq] (FQS) | [Drive parameters] (MPI)
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 |  | Fault parameters | R | WORD (BitString16) | -
LFT | Last Error occurred | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | - |  |  | [Last Error] (LFT) | [Diag. data] (DDT)
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 |  | Fault parameters | R/WS | WORD (BitString16) | -
CNF | Fieldbus module Communication interruption | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Fieldbus Com Interrupt] (CNF) | [DEVICENET DIAG] (DVN) [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN) [EtherCAT Module Diag] (ETD)
CNF3 | 3rd slot external communication error | 16#1BEF = 7151 | 16#2029/34 | 16#84/01/98 = 132/01/152 |  | Fault parameters | R/W | WORD (BitString16) | - |  |  | [3rd Slot Ext Comm Error] (CNF3) | [PLC Inside Data] (PLCI)
EPF3 | 3rd slot external error | 16#1BF0 = 7152 | 16#2029/35 | 16#84/01/99 = 132/01/153 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [3rd Slot External Error] (EPF3) | [PLC Inside Data] (PLCI)
ILF1 | Internal communication interruption 1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [InternCom Error1] (ILF1) | [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN) [EtherCAT Module Diag] (ETD)
ILF3 | 3rd slot internal communication error | 16#1BF2 = 7154 | 16#2029/37 | 16#84/01/9B = 132/01/155 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [3rd Slot Int Comm Error] (ILF3) | [PLC Inside Data] (PLCI)
INFO | Internal compatibility error | 16#1BF1 = 7153 | 16#2029/36 | 16#84/01/9A = 132/01/154 |  | Fault parameters | R | WORD (BitString16) | - |  |  | [Internal Compatibility] (INFO) | [PLC Inside Data] (PLCI) [HMI Panel Status] (HMIP)
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
ULP0 | DC bus voltage | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
RFP0 | Output frequency | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
THP0 | Motor thermal state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
EP0 | State word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 |  | History parameters | R | WORD (BitString16) | -
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 |  | History parameters | R | WORD (BitString16) | -
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 |  | History parameters | R | WORD (BitString16) | -
DCC0 | Command channel | 16#FB2C = 64300 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
DRC0 | Channel for reference frequency | 16#FB36 = 64310 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 |  | History parameters | R | WORD (BitString16) | -
RTP0 | Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
OTP0 | Motor torque | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
CS10 | Cabinet status 1 | 16#1EB4 = 7860 | 16#2030/3D | 16#88/01/3D = 136/01/61 |  | History parameters | R | WORD (BitString16) | -
CS20 | Cabinet status 2 | 16#1EC8 = 7880 | 16#2030/51 | 16#88/01/51 = 136/01/81 |  | History parameters | R | WORD (BitString16) | -
TTS0 | Thermal transformer | 16#1EDC = 7900 | 16#2031/1 | 16#88/01/65 = 136/01/101 |  | History parameters | R | INT (Signed16) | 1 °C |  | -50 °C ... 255 °C
FRP0 | Reference frequency | 16#1EF0 = 7920 | 16#2031/15 | 16#88/01/79 = 136/01/121 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
ULN0 | Mains voltage | 16#9B78 = 39800 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535
ILN0 | Mains current | 16#9BB4 = 39860 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
ULP1 | DC bus voltage | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP1) | [None] (DP1)
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP1) | [None] (DP1)
RFP1 | Output frequency | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP1) | [None] (DP1)
THP1 | Motor thermal state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP1) | [None] (DP1)
EP1 | Status of last error 1 | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP1) | [None] (DP1)
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP1) | [None] (DP1)
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP1) | [None] (DP1)
DCC1 | Command channel | 16#FB2D = 64301 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC1) | [None] (DP1)
DRC1 | Channel for reference frequency | 16#FB37 = 64311 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC1) | [None] (DP1)
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 |  | History parameters | R | WORD (BitString16) | -
RTP1 | Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP1) | [None] (DP1)
OTP1 | Motor torque | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP1) | [None] (DP1)
CS11 | Cabinet status 1 | 16#1EB5 = 7861 | 16#2030/3E | 16#88/01/3E = 136/01/62 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS11) | [None] (DP1)
CS21 | Cabinet status 2 | 16#1EC9 = 7881 | 16#2030/52 | 16#88/01/52 = 136/01/82 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS21) | [None] (DP1)
TTS1 | Thermal transformer | 16#1EDD = 7901 | 16#2031/2 | 16#88/01/66 = 136/01/102 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS1) | [None] (DP1)
FRP1 | Reference frequency | 16#1EF1 = 7921 | 16#2031/16 | 16#88/01/7A = 136/01/122 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP1) | [None] (DP1)
ULN1 | Mains voltage | 16#9B79 = 39801 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN1) | [None] (DP1)
ILN1 | Mains current | 16#9BB5 = 39861 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN1) | [None] (DP1)
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
ULP2 | DC bus voltage | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP2) | [None] (DP2)
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP2) | [None] (DP2)
RFP2 | Output frequency | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP2) | [None] (DP2)
THP2 | Motor thermal state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP2) | [None] (DP2)
EP2 | Status of last error 2 | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EP2) | [None] (DP2)
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP2) | [None] (DP2)
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP2) | [None] (DP2)
DCC2 | Command channel | 16#FB2E = 64302 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC2) | [None] (DP2)
DRC2 | Channel for reference frequency | 16#FB38 = 64312 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC2) | [None] (DP2)
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 |  | History parameters | R | WORD (BitString16) | -
RTP2 | Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP2) | [None] (DP2)
OTP2 | Motor torque | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP2) | [None] (DP2)
CS12 | Cabinet status 1 | 16#1EB6 = 7862 | 16#2030/3F | 16#88/01/3F = 136/01/63 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS12) | [None] (DP2)
CS22 | Cabinet status 2 | 16#1ECA = 7882 | 16#2030/53 | 16#88/01/53 = 136/01/83 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS22) | [None] (DP2)
TTS2 | Thermal transformer | 16#1EDE = 7902 | 16#2031/3 | 16#88/01/67 = 136/01/103 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS2) | [None] (DP2)
FRP2 | Reference frequency | 16#1EF2 = 7922 | 16#2031/17 | 16#88/01/7B = 136/01/123 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP2) | [None] (DP2)
ULN2 | Mains voltage | 16#9B7A = 39802 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN2) | [None] (DP2)
ILN2 | Mains current | 16#9BB6 = 39862 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN2) | [None] (DP2)
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
ULP3 | DC bus voltage | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP3) | [None] (DP3)
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP3) | [None] (DP3)
RFP3 | Output frequency | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP3) | [None] (DP3)
THP3 | Motor thermal state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP3) | [None] (DP3)
EP3 | Status of last error 3 | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EP3) | [None] (DP3)
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP3) | [None] (DP3)
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP3) | [None] (DP3)
DCC3 | Command channel | 16#FB2F = 64303 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC3) | [None] (DP3)
DRC3 | Channel for reference frequency | 16#FB39 = 64313 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC3) | [None] (DP3)
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 |  | History parameters | R | WORD (BitString16) | -
RTP3 | Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP3) | [None] (DP3)
OTP3 | Motor torque | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP3) | [None] (DP3)
CS13 | Cabinet status 1 | 16#1EB7 = 7863 | 16#2030/40 | 16#88/01/40 = 136/01/64 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS13) | [None] (DP3)
CS23 | Cabinet status 2 | 16#1ECB = 7883 | 16#2030/54 | 16#88/01/54 = 136/01/84 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS23) | [None] (DP3)
TTS3 | Thermal transformer | 16#1EDF = 7903 | 16#2031/4 | 16#88/01/68 = 136/01/104 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS3) | [None] (DP3)
FRP3 | Reference frequency | 16#1EF3 = 7923 | 16#2031/18 | 16#88/01/7C = 136/01/124 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP3) | [None] (DP3)
ULN3 | Mains voltage | 16#9B7B = 39803 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN3) | [None] (DP3)
ILN3 | Mains current | 16#9BB7 = 39863 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN3) | [None] (DP3)
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
ULP4 | DC bus voltage | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP4) | [None] (DP4)
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP4) | [None] (DP4)
RFP4 | Output frequency | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP4) | [None] (DP4)
THP4 | Motor thermal state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP4) | [None] (DP4)
EP4 | Status of last error 4 | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EP4) | [None] (DP4)
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP4) | [None] (DP4)
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP4) | [None] (DP4)
DCC4 | Command channel | 16#FB30 = 64304 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC4) | [None] (DP4)
DRC4 | Channel for reference frequency | 16#FB3A = 64314 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC4) | [None] (DP4)
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 |  | History parameters | R | WORD (BitString16) | -
RTP4 | Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP4) | [None] (DP4)
OTP4 | Motor torque | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP4) | [None] (DP4)
CS14 | Cabinet status 1 | 16#1EB8 = 7864 | 16#2030/41 | 16#88/01/41 = 136/01/65 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS14) | [None] (DP4)
CS24 | Cabinet status 2 | 16#1ECC = 7884 | 16#2030/55 | 16#88/01/55 = 136/01/85 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS24) | [None] (DP4)
TTS4 | Thermal transformer | 16#1EE0 = 7904 | 16#2031/5 | 16#88/01/69 = 136/01/105 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS4) | [None] (DP4)
FRP4 | Reference frequency | 16#1EF4 = 7924 | 16#2031/19 | 16#88/01/7D = 136/01/125 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP4) | [None] (DP4)
ULN4 | Mains voltage | 16#9B7C = 39804 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN4) | [None] (DP4)
ILN4 | Mains current | 16#9BB8 = 39864 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN4) | [None] (DP4)
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
ULP5 | DC bus voltage | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP5) | [None] (DP5)
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP5) | [None] (DP5)
RFP5 | Output frequency | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP5) | [None] (DP5)
THP5 | Motor thermal state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP5) | [None] (DP5)
EP5 | State word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP5) | [None] (DP5)
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP5) | [None] (DP5)
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP5) | [None] (DP5)
DCC5 | Command channel | 16#FB31 = 64305 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC5) | [None] (DP5)
DRC5 | Channel for reference frequency | 16#FB3B = 64315 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC5) | [None] (DP5)
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 |  | History parameters | R | WORD (BitString16) | -
RTP5 | Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP5) | [None] (DP5)
OTP5 | Motor torque | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP5) | [None] (DP5)
CS15 | Cabinet status 1 | 16#1EB9 = 7865 | 16#2030/42 | 16#88/01/42 = 136/01/66 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS15) | [None] (DP5)
CS25 | Cabinet status 2 | 16#1ECD = 7885 | 16#2030/56 | 16#88/01/56 = 136/01/86 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS25) | [None] (DP5)
TTS5 | Thermal transformer | 16#1EE1 = 7905 | 16#2031/6 | 16#88/01/6A = 136/01/106 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS5) | [None] (DP5)
FRP5 | Reference frequency | 16#1EF5 = 7925 | 16#2031/1A | 16#88/01/7E = 136/01/126 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP5) | [None] (DP5)
ULN5 | Mains voltage | 16#9B7D = 39805 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN5) | [None] (DP5)
ILN5 | Mains current | 16#9BB9 = 39865 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN5) | [None] (DP5)
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | -
ULP6 | DC bus voltage | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP6) | [None] (DP6)
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP6) | [None] (DP6)
RFP6 | Output frequency | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP6) | [None] (DP6)
THP6 | Motor thermal state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP6) | [None] (DP6)
EP6 | State word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP6) | [None] (DP6)
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP6) | [None] (DP6)
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP6) | [None] (DP6)
DCC6 | Command channel | 16#FB32 = 64306 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC6) | [None] (DP6)
DRC6 | Channel for reference frequency | 16#FB3C = 64316 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC6) | [None] (DP6)
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 |  | History parameters | R | WORD (BitString16) | -
RTP6 | Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP6) | [None] (DP6)
OTP6 | Motor torque | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP6) | [None] (DP6)
CS16 | Cabinet status 1 | 16#1EBA = 7866 | 16#2030/43 | 16#88/01/43 = 136/01/67 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS16) | [None] (DP6)
CS26 | Cabinet status 2 | 16#1ECE = 7886 | 16#2030/57 | 16#88/01/57 = 136/01/87 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS26) | [None] (DP6)
TTS6 | Thermal transformer | 16#1EE2 = 7906 | 16#2031/7 | 16#88/01/6B = 136/01/107 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS6) | [None] (DP6)
FRP6 | Reference frequency | 16#1EF6 = 7926 | 16#2031/1B | 16#88/01/7F = 136/01/127 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP6) | [None] (DP6)
ULN6 | Mains voltage | 16#9B7E = 39806 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN6) | [None] (DP6)
ILN6 | Mains current | 16#9BBA = 39866 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN6) | [None] (DP6)
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | -
ULP7 | DC bus voltage | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP7) | [None] (DP7)
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP7) | [None] (DP7)
RFP7 | Output frequency | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP7) | [None] (DP7)
THP7 | Motor thermal state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP7) | [None] (DP7)
EP7 | State word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP7) | [None] (DP7)
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP7) | [None] (DP7)
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP7) | [None] (DP7)
DCC7 | Command channel | 16#FB33 = 64307 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC7) | [None] (DP7)
DRC7 | Channel for reference frequency | 16#FB3D = 64317 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC7) | [None] (DP7)
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 |  | History parameters | R | WORD (BitString16) | -
RTP7 | Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP7) | [None] (DP7)
OTP7 | Motor torque | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP7) | [None] (DP7)
CS17 | Cabinet status 1 | 16#1EBB = 7867 | 16#2030/44 | 16#88/01/44 = 136/01/68 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS17) | [None] (DP7)
CS27 | Cabinet status 2 | 16#1ECF = 7887 | 16#2030/58 | 16#88/01/58 = 136/01/88 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS27) | [None] (DP7)
TTS7 | Thermal transformer | 16#1EE3 = 7907 | 16#2031/8 | 16#88/01/6C = 136/01/108 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS7) | [None] (DP7)
FRP7 | Reference frequency | 16#1EF7 = 7927 | 16#2031/1C | 16#88/01/80 = 136/01/128 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP7) | [None] (DP7)
ULN7 | Mains voltage | 16#9B7F = 39807 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN7) | [None] (DP7)
ILN7 | Mains current | 16#9BBB = 39867 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN7) | [None] (DP7)
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | -
ULP8 | DC bus voltage | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (ULP8) | [None] (DP8)
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP8) | [None] (DP8)
RFP8 | Output frequency | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP8) | [None] (DP8)
THP8 | Motor thermal state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP8) | [None] (DP8)
EP8 | State word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP8) | [None] (DP8)
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP8) | [None] (DP8)
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP8) | [None] (DP8)
DCC8 | Command channel | 16#FB34 = 64308 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC8) | [None] (DP8)
DRC8 | Channel for reference frequency | 16#FB3E = 64318 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC8) | [None] (DP8)
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 |  | History parameters | R | WORD (BitString16) | -
RTP8 | Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP8) | [None] (DP8)
OTP8 | Motor torque | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP8) | [None] (DP8)
CS18 | Cabinet status 1 | 16#1EBC = 7868 | 16#2030/45 | 16#88/01/45 = 136/01/69 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS18) | [None] (DP8)
CS28 | Cabinet status 2 | 16#1ED0 = 7888 | 16#2030/59 | 16#88/01/59 = 136/01/89 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS28) | [None] (DP8)
TTS8 | Thermal transformer | 16#1EE4 = 7908 | 16#2031/9 | 16#88/01/6D = 136/01/109 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS8) | [None] (DP8)
FRP8 | Reference frequency | 16#1EF8 = 7928 | 16#2031/1D | 16#88/01/81 = 136/01/129 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP8) | [None] (DP8)
ULN8 | Mains voltage | 16#9B80 = 39808 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN8) | [None] (DP8)
ILN8 | Mains current | 16#9BBC = 39868 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN8) | [None] (DP8)
NCV | Drive nominal rating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] NO
VCAL | Drive output voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [Unkown voltage] NO
INV | Nominal Drive Current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 |  | Identification parameters | R | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535
VDP | Drive software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NC1 | Com scan output 1 value | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (NC1) | [Com scan output map] (OSA)
NC2 | Com scan output 2 value | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (NC2) | [Com scan output map] (OSA)
NC3 | Com scan output 3 value | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (NC3) | [Com scan output map] (OSA)
NC4 | Com scan output 4 value | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (NC4) | [Com scan output map] (OSA)
NC5 | Com scan output 5 value | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (NC5) | [Com scan output map] (OSA)
NC6 | Com scan output 6 value | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (NC6) | [Com scan output map] (OSA)
NC7 | Com scan output 7 value | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (NC7) | [Com scan output map] (OSA)
NC8 | Com scan output 8 value | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (NC8) | [Com scan output map] (OSA)
NM1 | Com scan input 1 value | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (NM1) | [Com. scanner input map] (ISA)
NM2 | Com scan input 2 value | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (NM2) | [Com. scanner input map] (ISA)
NM3 | Com scan input 3 value | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (NM3) | [Com. scanner input map] (ISA)
NM4 | Com scan input 4 value | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (NM4) | [Com. scanner input map] (ISA)
NM5 | Com scan input 5 value | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (NM5) | [Com. scanner input map] (ISA)
NM6 | Com scan input 6 value | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (NM6) | [Com. scanner input map] (ISA)
NM7 | Com scan input 7 value | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (NM7) | [Com. scanner input map] (ISA)
NM8 | Com scan input 8 value | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (NM8) | [Com. scanner input map] (ISA)
SMAL | Velocity min amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 0 rpm ... 65535 rpm
SMIL | Velocity max amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 0 rpm ... 65535 rpm
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 1 rpm ... 4294967295 rpm
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 1 rpm ... 4294967295 rpm
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 |  | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 |  | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767
DOTD | Type of SwitchOn Disable Stop | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [SwitchOnDisable Stp] (DOTD) | [Stop configuration] (STT)
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Fast stop then disable voltage] FST2
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 |  | Configuration management | R/WS | WORD (BitString16) | - | BIT1
CHA1 | Parameter set sel 1 | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Parameter sets] (CHA1) | [Parameters switching] (MLP)
CHA2 | Parameter set sel 2 | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Parameter sets] (CHA2) | [Parameters switching] (MLP)
CFPS | Used parameter set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  |  | [Used param. set] (CFPS) | [Drive parameters] (MPI)
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S101) | [Set 1] (PS1)
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S102) | [Set 1] (PS1)
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S103) | [Set 1] (PS1)
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S104) | [Set 1] (PS1)
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S105) | [Set 1] (PS1)
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S106) | [Set 1] (PS1)
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S107) | [Set 1] (PS1)
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S108) | [Set 1] (PS1)
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S109) | [Set 1] (PS1)
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S110) | [Set 1] (PS1)
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S111) | [Set 1] (PS1)
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S112) | [Set 1] (PS1)
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S113) | [Set 1] (PS1)
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S114) | [Set 1] (PS1)
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S115) | [Set 1] (PS1)
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S201) | [Set 2] (PS2)
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S202) | [Set 2] (PS2)
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S203) | [Set 2] (PS2)
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S204) | [Set 2] (PS2)
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S205) | [Set 2] (PS2)
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S206) | [Set 2] (PS2)
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S207) | [Set 2] (PS2)
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S208) | [Set 2] (PS2)
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S209) | [Set 2] (PS2)
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S210) | [Set 2] (PS2)
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S211) | [Set 2] (PS2)
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S212) | [Set 2] (PS2)
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S213) | [Set 2] (PS2)
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S214) | [Set 2] (PS2)
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S215) | [Set 2] (PS2)
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S301) | [Set 3] (PS3)
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S302) | [Set 3] (PS3)
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S303) | [Set 3] (PS3)
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S304) | [Set 3] (PS3)
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S305) | [Set 3] (PS3)
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S306) | [Set 3] (PS3)
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S307) | [Set 3] (PS3)
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S308) | [Set 3] (PS3)
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S309) | [Set 3] (PS3)
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S310) | [Set 3] (PS3)
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S311) | [Set 3] (PS3)
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S312) | [Set 3] (PS3)
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S313) | [Set 3] (PS3)
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S314) | [Set 3] (PS3)
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S315) | [Set 3] (PS3)
LSP | Low Speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [Low Speed] (LSP) | [Simply start] (SIM) [Pump start stop] (PST) [Speed Limits] (SLM) [Settings] (SET)
HSP | High Speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [High Speed] (HSP) | [Simply start] (SIM) [Pump start stop] (PST) [Speed Limits] (SLM) [Settings] (SET)
ITH | Motor Thermal Current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Motor Th Current] (ITH) | [Simply start] (SIM) [Motor monitoring] (MOP) [Settings] (SET) [Motor thermal monit] (THT)
SPGU | Inertia factor | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Inertia Factor] (SPGU) | [Motor control] (DRC) [Settings] (SET)
SPG | Speed proportional gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [Spd Loop Optimization] (MCL) [Settings] (SET)
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | Refer to programming manual | 1 ms ... 65535 ms | [Speed time integral] (SIT) | [Spd Loop Optimization] (MCL) [Settings] (SET)
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 100 | [K speed loop filter] (SFC) | [Spd Loop Optimization] (MCL) [Settings] (SET)
JACO | Inertia Coefficient of the application | 16#2398 = 9112 | 16#203D/D | 16#8E/01/71 = 142/01/113 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | 1.00 | 0.10 ... 100.00 | [App. Inertia Coef.] (JACO) | [Spd Loop Optimization] (MCL)
SSL | Speed loop type | 16#2392 = 9106 | 16#203D/7 | 16#8E/01/6B = 142/01/107 | SSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [High performance] HPF |  | [Speed loop type] (SSL) | [Spd Loop Optimization] (MCL)
JEST | Estimated application inertia | 16#2393 = 9107 | 16#203D/8 | 16#8E/01/6C = 142/01/108 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Estim. app. inertia] (JEST) | [Spd Loop Optimization] (MCL)
JAPL | Application Inertia | 16#2394 = 9108 | 16#203D/9 | 16#8E/01/6D = 142/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Application Inertia] (JAPL) | [Spd Loop Optimization] (MCL)
JMU2 | Inertia Multiplying Coefficient | 16#239F = 9119 | 16#203D/14 | 16#8E/01/78 = 142/01/120 | JMUL | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Inertia Mult. Coef.] (JMU2) | [Spd Loop Optimization] (MCL)
FFP | Feed forward value | 16#2396 = 9110 | 16#203D/B | 16#8E/01/6F = 142/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 200 % | [Feed forward] (FFP) | [Spd Loop Optimization] (MCL)
FFV | Feed forward bandwidth | 16#2397 = 9111 | 16#203D/C | 16#8E/01/70 = 142/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 20 % ... 500 % | [FeedFwd Bandwidth] (FFV) | [Spd Loop Optimization] (MCL)
FFH | Filter time of the estimated speed | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | Refer to programming manual | 0.0 ms ... 100.0 ms | [Spd est. filter time] (FFH) | [Spd Loop Optimization] (MCL)
CRTF | Filter time of the current | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 0.0 ms | 0.0 ms ... 100.0 ms | [Current Filter Time] (CRTF) | [data] (MTD)
NFA | Notch Filter Activation | 16#23A0 = 9120 | 16#203D/15 | 16#8E/01/79 = 142/01/121 | NFL | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Notch Filter Activation] (NFA) | [Spd Loop Optimization] (MCL)
NFF1 | Notch Filter 1 - Frequency | 16#23A1 = 9121 | 16#203D/16 | 16#8E/01/7A = 142/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 10.0 Hz ... 150.0 Hz | [Notch Filter Freq 1] (NFF1) | [Spd Loop Optimization] (MCL)
NFB1 | Notch Filter 1 - Bandwidth | 16#23A2 = 9122 | 16#203D/17 | 16#8E/01/7B = 142/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 10 % ... 400 % | [Notch Filter Bdw 1] (NFB1) | [Spd Loop Optimization] (MCL)
NFD1 | Notch Filter 1 - Depth | 16#23A3 = 9123 | 16#203D/18 | 16#8E/01/7C = 142/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 99 % | [Notch Filter Depth 1] (NFD1) | [Spd Loop Optimization] (MCL)
NFF2 | Notch Filter 2 - Frequency | 16#23A4 = 9124 | 16#203D/19 | 16#8E/01/7D = 142/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 85.0 Hz | 10.0 Hz ... 150.0 Hz | [Notch Filter Freq 2] (NFF2) | [Spd Loop Optimization] (MCL)
NFB2 | Notch Filter 2 - Bandwidth | 16#23A5 = 9125 | 16#203D/1A | 16#8E/01/7E = 142/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 10 % ... 400 % | [Notch Filter Bdw 2] (NFB2) | [Spd Loop Optimization] (MCL)
NFD2 | Notch Filter 2 - Depth | 16#23A6 = 9126 | 16#203D/1B | 16#8E/01/7F = 142/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 25 % | 0 % ... 99 % | [Notch Filter Depth 2] (NFD2) | [Spd Loop Optimization] (MCL)
CTD | High current threshold | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [High Current Thd] (CTD) | [Threshold reached] (THRE) [Settings] (SET)
TTH | High torque threshold | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (TTH) | [Threshold reached] (THRE) [Settings] (SET)
TTL | Low torque threshold | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (TTL) | [Threshold reached] (THRE) [Settings] (SET)
FQL | Pulse warning threshold | 16#3911 = 14609 | 16#2074/A | 16#AA/01/0A = 170/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 30000 Hz | [Pulse warning thd.] (FQL) | [Frequency meter] (FQF)
FTD | Motor frequency threshold | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [Motor Freq Thd] (FTD) | [Threshold reached] (THRE) [Settings] (SET)
F2D | Frequency threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [Freq. threshold 2] (F2D) | [Threshold reached] (THRE) [Settings] (SET)
JF2 | Skip frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Skip Frequency 2] (JF2) | [Jump frequency] (JUF) [Settings] (SET)
JPF | Skip frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Skip Frequency] (JPF) | [Jump frequency] (JUF) [Settings] (SET)
JFH | Skip Freq. Hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip Freq.Hysteresis] (JFH) | [Jump frequency] (JUF) [Settings] (SET)
JF3 | 3rd Skip Frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [3rd Skip Frequency] (JF3) | [Jump frequency] (JUF) [Settings] (SET)
BFR | Motor Standard | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | [50Hz Motor frequency] 50Hz |  | [Motor Standard] (BFR) | [Simply start] (SIM) [data] (MTD)
NPR | Nominal motor power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nominal Motor Power] (NPR) | [Simply start] (SIM) [data] (MTD)
COS | Motor 1 Cosinus Phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Refer to programming manual | 0.50 ... 1.00 | [Motor 1 Cosinus Phi] (COS) | [Simply start] (SIM) [data] (MTD)
UNS | Nominal motor voltage | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 20000 V | [Nom Motor Voltage] (UNS) | [Simply start] (SIM) [data] (MTD)
NCR | Nominal motor current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nom Motor Current] (NCR) | [Simply start] (SIM) [data] (MTD)
FRS | Nominal Motor Frequency | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 300.0 Hz | [Nominal Motor Freq] (FRS) | [Simply start] (SIM) [data] (MTD)
NSP | Nominal motor speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nominal Motor Speed] (NSP) | [Simply start] (SIM) [data] (MTD)
TFR | Max frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 300.0 Hz | [Max Frequency] (TFR) | [Simply start] (SIM)
TUN | Autotuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] NO |  | [Autotuning] (TUN) | [Simply start] (SIM) [Motor tune] (MTU)
TUNR | Autotuning flux enable | 16#2668 = 9832 | 16#2044/21 | 16#92/01/21 = 146/01/33 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] NO |  | [Autotuning flux enable] (TUNR) | [Autotuning flux] (TUNR)
ENPT | Start standstill tune | 16#2666 = 9830 | 16#2044/1F | 16#92/01/1F = 146/01/31 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Start Standstill Tune] (ENPT) | [Autotuning flux] (TUNR)
IDL1 | First Id min current level in rotation | 16#266C = 9836 | 16#2044/25 | 16#92/01/25 = 146/01/37 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 65535 % | [1st Id min current] (IDL1) | [Autotuning flux] (TUNR)
IDH1 | First Id max current level in rotation | 16#266D = 9837 | 16#2044/26 | 16#92/01/26 = 146/01/38 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 65535 % | [1st Id max current] (IDH1) | [Autotuning flux] (TUNR)
IDL2 | Second Id min current level in rotation | 16#266E = 9838 | 16#2044/27 | 16#92/01/27 = 146/01/39 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 65535 % | [2nd Id min current] (IDL2) | [Autotuning flux] (TUNR)
IDH2 | Second Id max current level in rotation | 16#266F = 9839 | 16#2044/28 | 16#92/01/28 = 146/01/40 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 65535 % | [2nd Id max current] (IDH2) | [Autotuning flux] (TUNR)
EFAP | Expert flux setting | 16#2670 = 9840 | 16#2044/29 | 16#92/01/29 = 146/01/41 | EFAP | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear flux 1] LINF1 |  | [Expert Flux Setting] (EFAP) | [Autotuning flux] (TUNR)
TNBR | Max autotuning sequences | 16#2667 = 9831 | 16#2044/20 | 16#92/01/20 = 146/01/32 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3 | 1 ... 3 | [Max Autotuning] (TNBR) | [Autotuning flux] (TUNR)
L0A | Tangential main inductance | 16#2671 = 9841 | 16#2044/2A | 16#92/01/2A = 146/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Tangential Main Inductance] (L0A) | [data] (MTD) [Autotuning flux] (TUNR)
ALFA | Flux saturation curve numerator coefficient A | 16#2672 = 9842 | 16#2044/2B | 16#92/01/2B = 146/01/43 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 % | 0.00 % | -327.67 % ... 327.67 % | [Flux curve coeff A] (ALFA) | [data] (MTD) [Autotuning flux] (TUNR)
BET0 | Flux saturation curve denominator coefficient B | 16#2673 = 9843 | 16#2044/2C | 16#92/01/2C = 146/01/44 |  | Configuration and settings | R/WS | INT (Signed16) | 0.01 % | 0.00 % | -327.67 % ... 327.67 % | [Flux curve coeff B] (BET0) | [data] (MTD) [Autotuning flux] (TUNR)
PHIA | Rotor nominal flux | 16#2674 = 9844 | 16#2044/2D | 16#92/01/2D = 146/01/45 |  | Actual values parameters | R | UINT (Unsigned16) | 0.01 Wb |  | 0.00 Wb ... 655.35 Wb | [Rotor Nominal Flux] (PHIA) | [data] (MTD) [Autotuning flux] (TUNR)
LA | Main inductance | 16#2675 = 9845 | 16#2044/2E | 16#92/01/2E = 146/01/46 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Main Inductance] (LA) | [data] (MTD) [Autotuning flux] (TUNR)
TNF | Tune error status | 16#2676 = 9846 | 16#2044/2F | 16#92/01/2F = 146/01/47 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Tune Error Status] (TNF) | [data] (MTD) [Autotuning flux] (TUNR)
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Automatic autotune] (AUT) | [Motor tune] (MTU)
TUS | Autotuning status | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] TAB |  | [Autotuning Status] (TUS) | [Simply start] (SIM) [Motor tune] (MTU) [Autotuning flux] (TUNR)
TURS | Autotuning flux status | 16#266A = 9834 | 16#2044/23 | 16#92/01/23 = 146/01/35 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] TAB |  | [Autotuning flux status] (TURS) | [Autotuning flux] (TUNR)
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | [U/F VC Standard motor law] STD |  | [Motor control type] (CTT) | [Motor parameters] (MPA)
U1 | Volt point 1 on 5pt V/F | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 65535 V | [U1] (U1) | [Motor control] (DRC)
F1 | Freq point 1on 5pt V/F | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [F1] (F1) | [Motor control] (DRC)
U2 | Volt point 2 on 5pt V/F | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 65535 V | [U2] (U2) | [Motor control] (DRC)
F2 | Freq point 2 on 5pt V/F | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [F2] (F2) | [Motor control] (DRC)
U3 | Volt point 3 on 5pt V/F | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 65535 V | [U3] (U3) | [Motor control] (DRC)
F3 | Freq point 3 on 5pt V/F | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [F3] (F3) | [Motor control] (DRC)
U4 | Volt point 4 on 5pt V/F | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 65535 V | [U4] (U4) | [Motor control] (DRC)
F4 | Freq point 4 on 5pt V/F | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [F4] (F4) | [Motor control] (DRC)
U5 | Volt point 5 on 5pt V/F | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 65535 V | [U5] (U5) | [Motor control] (DRC)
F5 | Freq point 5 on 5pt V/F | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [F5] (F5) | [Motor control] (DRC)
NCRS | Sync motor nominal current | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Sync Nominal I ] (NCRS) | [data] (MTD)
NSPS | Nominal synchronous motor speed | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nom SyncMotor Speed] (NSPS) | [data] (MTD)
PPNS | Pole pairs number (sync) | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 50 | [Pole pairs] (PPNS) | [data] (MTD)
TQS | Nominal motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 1 ... 65535 | [Nom Motor torque] (TQS) | [data] (MTD)
PHS | Sync. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [data] (MTD)
LDS | Sync motor d inductance | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Autotune L d-axis] (LDS) | [data] (MTD)
LQS | Sync motor q inductance | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Autotune L q-axis] (LQS) | [data] (MTD)
RSAS | Calculated SyncMotor Stator R | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [SyncMotor Stator R] (RSAS) | [data] (MTD)
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFR) | [Motor control] (DRC) [Settings] (SET)
SLP | Slip Compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [Motor control] (DRC) [Settings] (SET)
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 |  | Configuration and settings | R | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 100
FLG | Frequency loop gain | 16#2594 = 9620 | 16#2042/15 | 16#91/01/15 = 145/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [FreqLoopGain] (FLG) | [Spd Loop Optimization] (MCL)
STA | Frequency loop stability | 16#2595 = 9621 | 16#2042/16 | 16#91/01/16 = 145/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [FreqLoop Stab] (STA) | [Spd Loop Optimization] (MCL)
RSA | AsyncMotor Stator resistance | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [AsyncMotor R Stator] (RSA) | [data] (MTD)
IDA | Magnetizing Current | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Magnetizing Current] (IDA) | [data] (MTD)
LFA | AsyncMotor Leakage inductance | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [AsyncMotor Lf Induct] (LFA) | [data] (MTD)
TRA | Rotor time constant | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Rotor Time Const] (TRA) | [data] (MTD)
FRSS | Synchronous motor nominal freq | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 300.0 Hz | [Sync Nominal Freq] (FRSS) | [data] (MTD)
CLI | Current limitation | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Current Limitation] (CLI) | [Motor monitoring] (MOP) [Settings] (SET) [2nd current limit.] (CLI)
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Boost activation] (BOA) | [Motor control] (DRC)
LBA | Load sharing | 16#37DD = 14301 | 16#2071/2 | 16#A8/01/66 = 168/01/102 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Load sharing] (LBA) | [Load Sharing] (LDS) [Load Sharing] (LDS) [Load Sharing M/S] (MSB)
LBC | Load correction | 16#37DE = 14302 | 16#2071/3 | 16#A8/01/67 = 168/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 1000.0 Hz | [Load correction] (LBC) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS) [Settings] (SET)
LBC1 | Correction min speed | 16#37DF = 14303 | 16#2071/4 | 16#A8/01/68 = 168/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 999.9 Hz | [Correction min spd] (LBC1) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
LBC2 | Correction max speed | 16#37E0 = 14304 | 16#2071/5 | 16#A8/01/69 = 168/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 1000.0 Hz | [Correction max spd] (LBC2) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
LBC3 | Torque offset | 16#37E1 = 14305 | 16#2071/6 | 16#A8/01/6A = 168/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Torque offset] (LBC3) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
LBF | Sharing filter | 16#37E2 = 14306 | 16#2071/7 | 16#A8/01/6B = 168/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 100 ms | 100 ms ... 20000 ms | [Sharing filter] (LBF) | [Load Sharing M/S] (MSB) [Load Sharing] (LDS) [Load Sharing] (LDS)
FMOH | Fan max operation time | 16#9EB8 = 40632 |  |  |  | Configuration and setting | R/WS | UINT (Unsigned16) | 1 h | 30000 h | 0 h ... 65535 h | [Fan Max Oper Time] (FMOH) | [Settings] (SET) [Fan management] (FAMA)
TCC | 2/3-wire control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2-wire control] 2C |  | [2/3-Wire Control] (TCC) | [Simply start] (SIM) [Command and Reference] (CRP)
TCT | Type of 2-wire control | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Transition] TRN |  | [2-wire type] (TCT) | [Command and Reference] (CRP)
RRS | Reverse assignment | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Reverse Assign] (RRS) | [Command and Reference] (CRP)
BSP | Reference frequency template selection | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard ref template] BSD |  | [Ref Freq template] (BSP) | [Pump start stop] (PST) [Speed Limits] (SLM) [Input/Output] (IO)
AI1T | Configuration of AI1 | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI1 Type] (AI1T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
UIL1 | AI1 voltage scaling parameter of 0% | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 Min. Value] (UIL1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
UIH1 | AI1 voltage scaling parameter of 100% | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 Max Value] (UIH1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1] (AI1C) [AI1 configuration] (AI1)
AI1E | AI1 intermediate point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point X] (AI1E) | [AI1 configuration] (AI1)
AI1S | AI1 intermediate point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 configuration] (AI1)
AI2T | Configuration of AI2 | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [AI bipolar volts selected] N10U |  | [AI2 Type] (AI2T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI2 Config.] (MSR2) [Torque Ref AI2 Config.] (MTR2) [AI2 configuration] (AI2)
UIL2 | AI2 voltage scaling parameter of 0% | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 Min. Value] (UIL2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [Speed Ref AI2 Config.] (MSR2) [Torque Ref AI2 Config.] (MTR2) [AI2 configuration] (AI2)
UIH2 | AI2 voltage scaling parameter of 100% | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 Max value] (UIH2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [Speed Ref AI2 Config.] (MSR2) [Torque Ref AI2 Config.] (MTR2) [AI2 configuration] (AI2)
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2] (AI2C) [AI2 configuration] (AI2)
AI2E | AI2 intermediate point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point X] (AI2E) | [AI2 configuration] (AI2)
AI2S | AI2 intermediate point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 configuration] (AI2)
AI3T | Configuration of AI3 | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI3 Type] (AI3T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
CRL3 | AI3 current scaling parameter of 0% | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 Min. Value] (CRL3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
CRH3 | AI3 current scaling parameter of 100% | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 Max Value] (CRH3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3] (AI3C) [AI3 configuration] (AI3)
AI3E | AI3 intermediate point X | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 X Interm. point] (AI3E) | [AI3 configuration] (AI3)
AI3S | AI3 intermediate point Y | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Y Interm. point] (AI3S) | [AI3 configuration] (AI3)
AO1 | AQ1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor frequency] OFR |  | [AQ1 assignment] (AO1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1T | AQ1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AQ1 Type] (AO1T) | [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
AOL1 | AQ1 min output value | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ1 min output] (AOL1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
AOH1 | AQ1 max output value | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ1 max output] (AOH1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
UOL1 | AQ1 minimum output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ1 min Output] (UOL1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
UOH1 | AQ1 maximum output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ1 max Output] (UOH1) | [AQ1] (AO1C) [Speed Ref AQ1 Config.] (MSM1) [Torque Ref AQ1 Config.] (MTM1) [AQ1 configuration] (AO1)
ASL1 | Scaling AQ1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 min] (ASL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
ASH1 | Scaling AQ1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 max] (ASH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1F | AQ1 filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ1 Filter] (AO1F) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
FR1 | Configuration reference frequency 1 | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 1 Config] (FR1) | [Command and Reference] (CRP) [PID Reference] (RF) [PID Reference] (RF)
RIN | Reverse direction disable | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Reverse Disable] (RIN) | [Command and Reference] (CRP) [Reverse disable] (REIN)
PST | Stop key enable | 16#FA02 = 64002 |  |  | PST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop key priority] YES |  | [Stop Key Enable] (PST) | [Command and Reference] (CRP)
CHCF | Control mode configuration | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Combined channel mode] SIM |  | [Control Mode] (CHCF) | [Command and Reference] (CRP)
CCS | Command switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Command channel 1] CD1 |  | [Command Switching] (CCS) | [Command and Reference] (CRP)
CD1 | Command channel 1 assign | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminal block] TER |  | [Cmd channel 1] (CD1) | [Command and Reference] (CRP)
CD2 | Command channel 2 assign | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus communication] MDB |  | [Cmd channel 2] (CD2) | [Command and Reference] (CRP)
RFC | Freq Switching Assignment | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Freq Switch Assign] (RFC) | [Command and Reference] (CRP)
FR2 | Configuration reference frequency 2 | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 2 Config] (FR2) | [Command and Reference] (CRP)
COP | Copy Ch.1-Ch.2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No copy] NO |  | [Copy Ch1-Ch2] (COP) | [Command and Reference] (CRP)
BMP | HMI command | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] DIS |  | [HMI cmd.] (BMP) | [Command and Reference] (CRP)
RCB | Select switching (1 to 1B) | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Reference frequency channel 1] FR1 |  | [Ref 1B switching] (RCB) | [Command and Reference] (CRP)
FR1B | Configuration ref. 1B | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref.1B channel] (FR1B) | [Command and Reference] (CRP)
SA2 | Summing input 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Summing Input 2] (SA2) | [Ref. operations] (OAI)
SA3 | Summing input 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Summing Input 3] (SA3) | [Ref. operations] (OAI)
DA2 | Subtract reference frequency 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 2] (DA2) | [Ref. operations] (OAI)
DA3 | Subtract reference frequency 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 3] (DA3) | [Ref. operations] (OAI)
MA2 | Reference frequency 2 multiply | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 2 Multiply] (MA2) | [Ref. operations] (OAI)
MA3 | Reference frequency 3 multiply | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 3 Multiply] (MA3) | [Ref. operations] (OAI)
RPT | Type of Ramp | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear ramp] LIN |  | [Ramp Type] (RPT) | [Ramp] (RAMP)
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [Tenths of seconds] 01 |  | [Ramp increment] (INR) | [Ramp] (RAMP) [Settings] (SET)
ACC | Acceleration ramp time | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 0 ... 9999 | [Acceleration] (ACC) | [Simply start] (SIM) [Pump start stop] (PST) [Ramp] (RAMP) [Settings] (SET)
DEC | Deceleration ramp time | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 0 ... 9999 | [Deceleration] (DEC) | [Simply start] (SIM) [Pump start stop] (PST) [Ramp] (RAMP) [Settings] (SET)
TA1 | Start ACC ramp rounding | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Acc round] (TA1) | [Ramp] (RAMP) [Settings] (SET)
TA2 | End ACC ramp rounding | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Acc round] (TA2) | [Ramp] (RAMP) [Settings] (SET)
TA3 | Start DEC ramp rounding | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Dec round] (TA3) | [Ramp] (RAMP) [Settings] (SET)
TA4 | End DEC ramp rounding | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Dec round] (TA4) | [Ramp] (RAMP) [Settings] (SET)
FRT | Ramp 2 frequency threshold | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Ramp 2 Thd] (FRT) | [Ramp switching] (RPT)
RPS | Ramp switching Assignment | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ramp Switch Assign] (RPS) | [Ramp switching] (RPT)
AC2 | Acceleration 2 ramp time | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 1 ... 9999 | [Acceleration 2] (AC2) | [Ramp switching] (RPT) [Settings] (SET) [+/- speed around ref] (SRE)
DE2 | Deceleration 2 | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 1 ... 9999 | [Deceleration 2] (DE2) | [Ramp switching] (RPT) [Settings] (SET) [+/- speed around ref] (SRE)
AC3 | Acceleration 3 ramp time | 16#2336 = 9014 | 16#203C/F | 16#8E/01/0F = 142/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 1 ... 9999 | [Acceleration 3] (AC3) | [Ramp switching] (RPT) [Settings] (SET)
DE3 | Deceleration 3 ramp time | 16#2337 = 9015 | 16#203C/10 | 16#8E/01/10 = 142/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 1 ... 9999 | [Deceleration 3] (DE3) | [Ramp switching] (RPT) [Settings] (SET)
FT3 | Ramp 3 frequency threshold | 16#2338 = 9016 | 16#203C/11 | 16#8E/01/11 = 142/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Ramp 3 Thd] (FT3) | [Ramp switching] (RPT)
BRA | Decel ramp adaptation | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Dec.Ramp Adapt] (BRA) | [Ramp] (RAMP)
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [On ramp] RMP |  | [Type of stop] (STT) | [Stop configuration] (STT)
FFT | Freewheel stop threshold | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.2 Hz ... 300.0 Hz | [Freewheel stop Thd] (FFT) | [Stop configuration] (STT) [Settings] (SET)
NST | Freewheel stop | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Freewheel Stop] (NST) | [Stop configuration] (STT)
ADC | Automatic DC Injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | [No DC injection] NO |  | [Auto DC Injection] (ADC) | [Auto DC injection] (ADC)
SDC1 | Auto DC injection level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Auto DC inj Level 1] (SDC1) | [Auto DC injection] (ADC) [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
TDC1 | Auto DC injection time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC Inj Time 1] (TDC1) | [Auto DC injection] (ADC) [Settings] (SET)
SDC2 | Auto DC injection level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Auto DC inj Level 2] (SDC2) | [Auto DC injection] (ADC) [Settings] (SET)
TDC2 | Auto DC injection time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC Inj Time 2] (TDC2) | [Auto DC injection] (ADC) [Settings] (SET)
JOG | Jog assignment | 16#2B66 = 11110 | 16#2051/B | 16#98/01/6F = 152/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Jog Assign] (JOG) | [Jog] (JOG)
JGF | Jog frequency | 16#2B67 = 11111 | 16#2051/C | 16#98/01/70 = 152/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 10.0 Hz | [Jog Frequency] (JGF) | [Jog] (JOG) [Settings] (SET)
JGT | Jog delay | 16#2B68 = 11112 | 16#2051/D | 16#98/01/71 = 152/01/113 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 2.0 s | [Jog Delay] (JGT) | [Jog] (JOG) [Settings] (SET)
PS2 | 2 Preset Freq assignment | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 Preset Freq] (PS2) | [Preset speeds] (PSS)
PS4 | 4 Preset Freq assignment | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 Preset Freq] (PS4) | [Preset speeds] (PSS)
PS8 | 8 Preset Freq assignment | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [8 Preset Freq] (PS8) | [Preset speeds] (PSS)
PS16 | 16 Preset Freq assignment | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [16 Preset Freq] (PS16) | [Preset speeds] (PSS)
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 2] (SP2) | [Preset speeds] (PSS) [Settings] (SET)
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 3] (SP3) | [Preset speeds] (PSS) [Settings] (SET)
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 4] (SP4) | [Preset speeds] (PSS) [Settings] (SET)
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 5] (SP5) | [Preset speeds] (PSS) [Settings] (SET)
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 6] (SP6) | [Preset speeds] (PSS) [Settings] (SET)
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 7] (SP7) | [Preset speeds] (PSS) [Settings] (SET)
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 8] (SP8) | [Preset speeds] (PSS) [Settings] (SET)
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 9] (SP9) | [Preset speeds] (PSS) [Settings] (SET)
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 10] (SP10) | [Preset speeds] (PSS) [Settings] (SET)
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 11] (SP11) | [Preset speeds] (PSS) [Settings] (SET)
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 12] (SP12) | [Preset speeds] (PSS) [Settings] (SET)
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 13] (SP13) | [Preset speeds] (PSS) [Settings] (SET)
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 14] (SP14) | [Preset speeds] (PSS) [Settings] (SET)
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 15] (SP15) | [Preset speeds] (PSS) [Settings] (SET)
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 300.0 Hz | [Preset speed 16] (SP16) | [Preset speeds] (PSS) [Settings] (SET)
USP | + speed assignment | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USP) | [+/- speed] (UPD)
DSP | - speed assignment | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSP) | [+/- speed] (UPD)
STR | Reference frequency save | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No save] NO |  | [Ref Frequency Save] (STR) | [+/- speed] (UPD)
USI | + speed assignment | 16#2D00 = 11520 | 16#2055/15 | 16#9A/01/79 = 154/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USI) | [+/- speed around ref] (SRE)
DSI | - speed assignment | 16#2D01 = 11521 | 16#2055/16 | 16#9A/01/7A = 154/01/122 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSI) | [+/- speed around ref] (SRE)
SRP | +/- Speed limitation | 16#2CF1 = 11505 | 16#2055/6 | 16#9A/01/6A = 154/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 50 % | [+/- Speed limitation] (SRP) | [+/- speed around ref] (SRE) [Settings] (SET)
SPM | Reference frequency memory assignment | 16#212B = 8491 | 16#2036/5C | 16#8B/01/5C = 139/01/92 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref Freq Memo assign] (SPM) | [Memo reference frequency] (SPM)
FLU | Motor fluxing configure | 16#364E = 13902 | 16#206D/3 | 16#A6/01/67 = 166/01/103 | FLU | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Motor fluxing] (FLU) | [Fluxing by DI] (FLI) [Settings] (SET)
FLI | Fluxing input assignment | 16#364D = 13901 | 16#206D/2 | 16#A6/01/66 = 166/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fluxing assignment] (FLI) | [Fluxing by DI] (FLI)
FCR | Motor fluxing level | 16#364F = 13903 | 16#206D/4 | 16#A6/01/68 = 166/01/104 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | 0 % ... 150 % | [Motor Fluxing Level] (FCR) | [Fluxing by DI] (FLI)
AST | Auto angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Rotational Current Injection] RCI |  | [Angle setting type] (AST) | [data] (MTD) [Angle test setting] (ASA) [Motor tune] (MTU) [Fluxing by DI] (FLI)
ASA | Angle auto-test | 16#3661 = 13921 | 16#206D/16 | 16#A6/01/7A = 166/01/122 | ASA | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Angle auto-test] (ASA) | [Angle test setting] (ASA)
ASL | Angle Test assignment | 16#3663 = 13923 | 16#206D/18 | 16#A6/01/7C = 166/01/124 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Angle Test Assign] (ASL) | [Angle test setting] (ASA)
ATA | Angle setting activation mode | 16#3664 = 13924 | 16#206D/19 | 16#A6/01/7D = 166/01/125 | ATA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Run command] AUTO |  | [Angle setting Mode] (ATA) | [Angle test setting] (ASA)
ASTS | Auto angle setting status | 16#3666 = 13926 | 16#206D/1B | 16#A6/01/7F = 166/01/127 | ASTS | Status parameters | R | WORD (Enumeration) | - | [Not done] TAB |  | [Angle setting status] (ASTS) | [Angle test setting] (ASA)
SPB | Bandwidth of the HF PLL | 16#3CF3 = 15603 | 16#207E/4 | 16#AF/01/04 = 175/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 400 % | [HF pll bandwidth] (SPB) | [Motor control] (DRC)
ILR | Current level of the HF alignment | 16#3CF5 = 15605 | 16#207E/6 | 16#AF/01/06 = 175/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 50 % | 0 % ... 200 % | [Current Level Align] (ILR) | [Motor control] (DRC)
SIR | Boost level for IPMA alignment | 16#3CF6 = 15606 | 16#207E/7 | 16#AF/01/07 = 175/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [Boost level align.] (SIR) | [Motor control] (DRC)
MCR | Maximum current of PSI alignment | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [PSI Align Curr Max] (MCR) | [data] (MTD) [Motor tune] (MTU)
BLC | Brake assignment | 16#2711 = 10001 | 16#2046/2 | 16#93/01/02 = 147/01/02 | BLC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Brake assignment] (BLC) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BST | Motion type selection | 16#2718 = 10008 | 16#2046/9 | 16#93/01/09 = 147/01/09 | BST | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Movement type] (BST) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BCI | Brake contact input | 16#2719 = 10009 | 16#2046/A | 16#93/01/0A = 147/01/10 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Brake Contact] (BCI) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BIP | Brake release pulse | 16#2717 = 10007 | 16#2046/8 | 16#93/01/08 = 147/01/08 | BIP | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [Brake Release Pulse] (BIP) | [Brake logic control] (BLC) [Brake logic control] (BLC)
IBR | Brake Release current | 16#2716 = 10006 | 16#2046/7 | 16#93/01/07 = 147/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Brk Release Current] (IBR) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
IRD | Rev. brake release curr. | 16#271B = 10011 | 16#2046/C | 16#93/01/0C = 147/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Brake release I Rev] (IRD) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BRT | Brake release time | 16#2714 = 10004 | 16#2046/5 | 16#93/01/05 = 147/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | Refer to programming manual | 0.00 s ... 5.00 s | [Brake Release time] (BRT) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BIR | Brake release frequency | 16#271C = 10012 | 16#2046/D | 16#93/01/0D = 147/01/13 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Brake release freq] (BIR) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BEN | Brake engage frequency | 16#2713 = 10003 | 16#2046/4 | 16#93/01/04 = 147/01/04 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Brake engage freq] (BEN) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
TBE | Brake engage delay | 16#271A = 10010 | 16#2046/B | 16#93/01/0B = 147/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Brake engage delay] (TBE) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BET | Brake engage time | 16#2715 = 10005 | 16#2046/6 | 16#93/01/06 = 147/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | Refer to programming manual | 0.00 s ... 5.00 s | [Brake engage time] (BET) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BED | Brake engage at reversal | 16#2724 = 10020 | 16#2046/15 | 16#93/01/15 = 147/01/21 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Engage at reversal] (BED) | [Brake logic control] (BLC) [Brake logic control] (BLC)
JDC | Jump at reversal | 16#271D = 10013 | 16#2046/E | 16#93/01/0E = 147/01/14 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | -0.1 Hz ... 10.0 Hz | [Jump at reversal] (JDC) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
BECD | Brake engage at 0 speed | 16#271E = 10014 | 16#2046/F | 16#93/01/0F = 147/01/15 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 s | -0.1 s | -0.1 s ... 30.0 s | [Brake engage at 0] (BECD) | [Brake logic control] (BLC) [Brake logic control] (BLC)
TTR | Time to restart | 16#2726 = 10022 | 16#2046/17 | 16#93/01/17 = 147/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 15.00 s | [Time to restart] (TTR) | [Settings] (SET) [Brake logic control] (BLC) [Brake logic control] (BLC)
FBCI | Brake feedback filter | 16#2729 = 10025 | 16#2046/1A | 16#93/01/1A = 147/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [Brake Fdbk Filter] (FBCI) | [Brake logic control] (BLC) [Brake logic control] (BLC)
BRH | Brake hidden | 16#2742 = 10050 | 16#2046/33 | 16#93/01/33 = 147/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
BRR | Current ramp time | 16#271F = 10015 | 16#2046/10 | 16#93/01/10 = 147/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 5.00 s | [Current ramp time] (BRR) | [Brake logic control] (BLC) [Brake logic control] (BLC)
PIF | PID controller feedback | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID feedback Assign] (PIF) | [PID Feedback] (FDB) [PID Feedback] (FDB)
PIF1 | Minimum PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 32767 | [Min PID feedback] (PIF1) | [PID Feedback] (FDB) [PID Feedback] (FDB)
PIF2 | Maximum PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 1000 | 0 ... 32767 | [Max PID feedback] (PIF2) | [PID Feedback] (FDB) [PID Feedback] (FDB)
PIP1 | Minimum PID process | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 150 | 0 ... 32767 | [Min PID Process] (PIP1) | [PID Reference] (RF) [PID Reference] (RF)
PIP2 | Maximum PID process | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 900 | 0 ... 32767 | [Max PID Process] (PIP2) | [PID Reference] (RF) [PID Reference] (RF)
PII | Internal PID reference | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Intern PID Ref] (PII) | [PID Reference] (RF) [PID Reference] (RF)
RPI | Internal PID reference | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 150 | 0 ... 32767 | [Internal PID ref] (RPI) | [PID display] (PIC) [PID Reference] (RF) [PID Reference] (RF)
RPG | PID Proportional gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Prop.Gain] (RPG) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
RIG | PID controller integral gain | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Intgl.Gain] (RIG) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (RDG) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PRP) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PIC | PID inversion | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Inversion] (PIC) | [Settings] (ST) [Settings] (ST)
POL | PID controller min. output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -300.0 Hz ... 300.0 Hz | [PID Min Output] (POL) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
POH | PID controller max. output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 300.0 Hz | [PID Max Output] (POH) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PAL | Minimum feedback level Warning | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 65535 | [Min fbk Warning] (PAL) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Settings] (SET)
PAH | Maximum feedback level Warning | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 1000 | 0 ... 65535 | [Max fbk Warning] (PAH) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Settings] (SET)
PER | PID error Warning | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 65535 | [PID error Warning] (PER) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
PIS | PID integral disabled | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID Integral OFF] (PIS) | [Settings] (ST) [Settings] (ST)
FPI | Predictive speed reference | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Predictive Speed Ref] (FPI) | [PID Reference] (RF) [PID Reference] (RF)
PSR | PID speed input % ref | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSR) | [PID Reference] (RF) [PID Reference] (RF) [Settings] (SET)
PAU | Auto/Manual select input | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Auto/Manual assign.] (PAU) | [PID Reference] (RF) [PID Reference] (RF)
PIM | Manual PID reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Manual PID reference] (PIM) | [PID Reference] (RF) [PID Reference] (RF)
TLS | Low speed timeout | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low Speed Timeout] (TLS) | [Settings] (SET) [Stop after speed timeout] (PRSP)
PR2 | 2 PID Preset assignment | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 PID Preset Assign] (PR2) | [PID preset references] (PRI) [PID preset references] (PRI)
PR4 | 4 PID Preset assignment | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 PID Preset Assign] (PR4) | [PID preset references] (PRI) [PID preset references] (PRI)
RP2 | 2nd PID preset reference | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 300 | 0 ... 32767 | [Ref PID Preset 2] (RP2) | [Settings] (SET) [PID preset references] (PRI) [PID preset references] (PRI)
RP3 | 3rd PID preset reference | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 0 ... 32767 | [Ref PID Preset 3] (RP3) | [Settings] (SET) [PID preset references] (PRI) [PID preset references] (PRI)
RP4 | 4th PID preset reference | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 900 | 0 ... 32767 | [Ref PID Preset 4] (RP4) | [PID preset references] (PRI) [PID preset references] (PRI) [Settings] (SET)
TLA | Torque limit. activation | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque limit activ.] (TLA) | [Torque limitation] (TOL)
INTP | Torque increment | 16#23FF = 9215 | 16#203E/10 | 16#8F/01/10 = 143/01/16 | INCPER | Configuration and settings | R/WS | WORD (Enumeration) | - | [1%] 1 |  | [Torque increment] (INTP) | [Torque limitation] (TOL)
TLIM | Motoring torque limit | 16#23FB = 9211 | 16#203E/C | 16#8F/01/0C = 143/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 3000 | [Motor torque limit] (TLIM) | [Torque limitation] (TOL) [Settings] (SET)
TLIG | Generator torque limit | 16#23FC = 9212 | 16#203E/D | 16#8F/01/0D = 143/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 3000 | [Gen. torque limit] (TLIG) | [Torque limitation] (TOL) [Settings] (SET)
TAA | Reference torque assignment | 16#23FE = 9214 | 16#203E/F | 16#8F/01/0F = 143/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Torque Assign] (TAA) | [Torque limitation] (TOL)
TLC | Torque analog limit. activ | 16#23FD = 9213 | 16#203E/E | 16#8F/01/0E = 143/01/14 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Analog limit activ.] (TLC) | [Torque limitation] (TOL)
TSS | Torque/Speed switching control mode | 16#2404 = 9220 | 16#203E/15 | 16#8F/01/15 = 143/01/21 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Trq/spd switching] (TSS) | [Torque control] (TOR)
TR1 | Channel for torque reference | 16#2405 = 9221 | 16#203E/16 | 16#8F/01/16 = 143/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque ref. channel] (TR1) | [Torque control] (TOR)
TSD | Torque reference sign switching | 16#2406 = 9222 | 16#203E/17 | 16#8F/01/17 = 143/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Torque ref. sign] (TSD) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
DBN | Torque regulation negative deadband | 16#2407 = 9223 | 16#203E/18 | 16#8F/01/18 = 143/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 2000.0 Hz | [Negative deadband] (DBN) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
DBP | Torque regulation positive deadband | 16#2408 = 9224 | 16#203E/19 | 16#8F/01/19 = 143/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 2000.0 Hz | [Positive deadband] (DBP) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TRT | Torque ratio | 16#2409 = 9225 | 16#203E/1A | 16#8F/01/1A = 143/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 1000.0 % | [Torque ratio] (TRT) | [Torque control] (TOR) [Settings] (SET) [M/S Torque Control] (MSQ)
TRP | Torque ramp time | 16#240A = 9226 | 16#203E/1B | 16#8F/01/1B = 143/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 3.00 s | 0.00 s ... 99.99 s | [Torque ramp time] (TRP) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TST | Torque control stop type | 16#240B = 9227 | 16#203E/1C | 16#8F/01/1C = 143/01/28 | TST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] NST |  | [Torque control stop] (TST) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TOB | Response to torque control error | 16#240C = 9228 | 16#203E/1D | 16#8F/01/1D = 143/01/29 | TOB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Warning] ALRM |  | [Torque Ctrl ErrorResp] (TOB) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
RTO | Torque control time out | 16#240D = 9229 | 16#203E/1E | 16#8F/01/1E = 143/01/30 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 999.9 s | [Torque ctrl time out] (RTO) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
SPT | Spin time | 16#240E = 9230 | 16#203E/1F | 16#8F/01/1F = 143/01/31 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 0.0 s ... 3600.0 s | [Spin time] (SPT) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TQR | Torque ratio assignment | 16#2411 = 9233 | 16#203E/22 | 16#8F/01/22 = 143/01/34 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Torque Ratio Assign] (TQR) | [Torque control] (TOR)
TQO | Torque offset assignment | 16#2413 = 9235 | 16#203E/24 | 16#8F/01/24 = 143/01/36 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Torque Offset Assign] (TQO) | [Torque control] (TOR)
TRI | Torque reference assignment | 16#2416 = 9238 | 16#203E/27 | 16#8F/01/27 = 143/01/39 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Torque reference channel] TR1 |  | [Torque Ref Assign] (TRI) | [Torque control] (TOR)
TR2 | Torque reference 2 channel | 16#2417 = 9239 | 16#203E/28 | 16#8F/01/28 = 143/01/40 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque Ref 2 Channel] (TR2) | [Torque control] (TOR)
LC2 | Current Limitation 2 | 16#23F2 = 9202 | 16#203E/3 | 16#8F/01/03 = 143/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Current Limitation2] (LC2) | [2nd current limit.] (CLI)
CL2 | Current limitation 2 value | 16#23F3 = 9203 | 16#203E/4 | 16#8F/01/04 = 143/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Current Limit2 Value] (CL2) | [2nd current limit.] (CLI) [Settings] (SET)
LC2F | Current Limitation 2 threshold | 16#23F5 = 9205 | 16#203E/6 | 16#8F/01/06 = 143/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Current Limitation2 Thd] (LC2F) | [2nd current limit.] (CLI)
TASU | Reference torque switch assignment | 16#23F8 = 9208 | 16#203E/9 | 16#8F/01/09 = 143/01/09 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ref Torque Switch Assign] (TASU) | [Torque limitation] (TOL)
TAA2 | Reference torque 2 assignment | 16#23F9 = 9209 | 16#203E/A | 16#8F/01/0A = 143/01/10 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Torque 2 Assign] (TAA2) | [Torque limitation] (TOL)
CHM | Multimotors selection | 16#1F59 = 8025 | 16#2032/1A | 16#89/01/1A = 137/01/26 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Multimotors] (CHM) | [Multimotors config] (MMC)
CNF1 | 2 configurations assignt. | 16#1F55 = 8021 | 16#2032/16 | 16#89/01/16 = 137/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Configurations] (CNF1) | [Multimotors config] (MMC)
CNF2 | 3 configurations assignt. | 16#1F56 = 8022 | 16#2032/17 | 16#89/01/17 = 137/01/23 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Configurations] (CNF2) | [Multimotors config] (MMC)
TUL | Autotuning input assignment | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Autotuning Assign] (TUL) | [Motor tune] (MTU)
RSF | Fault reset input assignment | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Fault Reset Assign] (RSF) | [Fault reset] (RST)
RP | Product restart | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Product restart] (RP) | [Fault reset] (RST)
RPA | Product restart assignment | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Prod Restart Assign] (RPA) | [Fault reset] (RST)
TAR | Fault Reset Time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] 5 |  | [Fault Reset Time] (TAR) | [Auto Fault Reset] (ATR)
ATR | Automatic Fault reset | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Auto Fault Reset] (ATR) | [Auto Fault Reset] (ATR)
HRFC | Extended fault reset activation | 16#1BEE = 7150 | 16#2029/33 | 16#84/01/97 = 132/01/151 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Extended Fault Reset] (HRFC) | [Fault reset] (RST)
FLR | Catch on fly | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | FLR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Catch On Fly] (FLR) | [Catch on the fly] (FLR)
THT | Motor thermal monitoring mode | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Motor Thermal Mode] (THT) | [Motor monitoring] (MOP) [Motor thermal monit] (THT)
TTD | Motor thermal threshold | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor Therm Thd] (TTD) | [Motor monitoring] (MOP) [Threshold reached] (THRE) [Settings] (SET)
TTD2 | Motor 2 thermal threshold | 16#2AFE = 11006 | 16#2050/7 | 16#98/01/07 = 152/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor2 Therm Thd] (TTD2) | [Motor monitoring] (MOP) [Threshold reached] (THRE)
TTD3 | Motor 3 thermal threshold | 16#2AFF = 11007 | 16#2050/8 | 16#98/01/08 = 152/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor3 Therm Thd] (TTD3) | [Motor monitoring] (MOP) [Threshold reached] (THRE)
TTD4 | Motor 4 thermal threshold | 16#2B00 = 11008 | 16#2050/9 | 16#98/01/09 = 152/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor4 therm. level] (TTD4) | [Motor monitoring] (MOP) [Threshold reached] (THRE)
OLL | Motor overtemp error response | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [MotorTemp ErrorResp] (OLL) | [Motor monitoring] (MOP)
OPL | Output Phase Loss assignment | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [OutPhaseLoss Assign] (OPL) | [Output phase loss] (OPL)
ODT | Output Phase Loss delay | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPhaseLoss Delay] (ODT) | [Output phase loss] (OPL)
IPL | Input Phase Loss assignment | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [InPhaseLoss Assign] (IPL) | [Input phase loss] (IPL)
OHL | Drive overtemp error response | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [DriveTemp ErrorResp] (OHL) | [Drive overload monit] (OBR)
THA | Drive thermal state Warning | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Drv Thermal Warning] (THA) | [Drive overload monit] (OBR)
ETF | External error assignment | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ext Error assign] (ETF) | [External error] (ETF)
EPL | Drive response to external error | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Ext Error Resp] (EPL) | [External error] (ETF)
EPL3 | Response to 3rd slot error | 16#1B6F = 7023 | 16#2028/18 | 16#84/01/18 = 132/01/24 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [3rd Slot Error Resp] (EPL3) | [External error] (ETF)
CMVI | Voltage rise injection | 16#3636 = 13878 | 16#206C/4F | 16#A6/01/4F = 166/01/79 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Voltage Rise Injection] (CMVI) | [Motor control] (DRC)
USB | Response to undervoltage | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error triggered] 0 |  | [Undervoltage Resp] (USB) | [Undervoltage handling] (USB)
UST | Undervoltage timeout | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [UnderVolt timeout] (UST) | [Undervoltage handling] (USB)
STP | Stop type on power loss | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [Stop Type PLoss] (STP) | [Undervoltage handling] (USB)
SDD | Load slip detection | 16#1B5D = 7005 | 16#2028/6 | 16#84/01/06 = 132/01/06 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Load slip detection] (SDD) | [Encoder monitoring] (SDD)
DCT | DC Bus charge opt. time | 16#3612 = 13842 | 16#206C/2B | 16#A6/01/2B = 166/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 60.00 s
STRT | Output short circuit test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Output Short Circuit Test] (STRT) | [Motor monitoring] (MOP)
COFM | Catch on fly mode | 16#0C29 = 3113 | 16#2001/E | 16#70/01/72 = 112/01/114 | COFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Measured] HWCOF |  | [Catch On Fly Mode] (COFM) | [Catch on the fly] (FLR)
LFL3 | Response to 4-20mA loss on AI3 | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI3 4-20mA loss] (LFL3) | [4-20 mA loss] (LFL)
INH | Disable Error Detection | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [ErrorDetect Disable] (INH) | [Error detection disable] (INH)
INHS | Forced Run | 16#1BD6 = 7126 | 16#2029/1B | 16#84/01/7F = 132/01/127 | INHS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] NO |  | [Forced Run] (INHS) | [Error detection disable] (INH)
INHR | Forced Run Reference Frequency | 16#1BD7 = 7127 | 16#2029/1C | 16#84/01/80 = 132/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 6553.5 Hz | [Forced Run Ref] (INHR) | [Error detection disable] (INH)
CLL | Response to Fieldbus module communication interruption | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Fieldbus Interrupt Resp] (CLL) | [Communication Module] (COMO)
COL | Response to CANopen error | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CANopen Error Resp] (COL) | [Communication Module] (COMO)
SLL | Response to Modbus interruption | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Modbus Error Resp] (SLL) | [Fieldbus monitoring] (CLL)
SSB | Stop type - Torque/I limit | 16#2418 = 9240 | 16#203E/29 | 16#8F/01/29 = 143/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [Trq/I limit. stop] (SSB) | [Torque limitation] (TOL) [Torque or I limit detect] (TID)
TNL | Response to Autotuning error | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Tuning Error Resp] (TNL) | [Motor tune] (MTU)
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [Pairing password] (PPI) | [My preferences] (MYP)
LFF | Fall back speed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [FallbackSpeed] (LFF) | [4-20 mA loss] (LFL) [External error] (ETF) [Communication Module] (COMO) [Fieldbus monitoring] (CLL) [Fallback speed] (LFF) [Embedded modbus TCP] (EMTC) [Pumpcycle monitoring] (CSP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [M/S System Architecture] (MSA)
FQF | Frequency meter | 16#3909 = 14601 | 16#2074/2 | 16#AA/01/02 = 170/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Frequency meter] (FQF) | [Frequency meter] (FQF)
FQC | Pulse scaling divisor | 16#390A = 14602 | 16#2074/3 | 16#AA/01/03 = 170/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 | 1.0 | 1.0 ... 100.0 | [Pulse scal. divider] (FQC) | [Frequency meter] (FQF)
FQA | Overspd. pulse threshold | 16#390C = 14604 | 16#2074/5 | 16#AA/01/05 = 170/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 30000 Hz | [Overspd. pulse thd.] (FQA) | [Frequency meter] (FQF)
TDS | Pulse Overspeed delay | 16#390D = 14605 | 16#2074/6 | 16#AA/01/06 = 170/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse overspd delay] (TDS) | [Frequency meter] (FQF)
FDT | Level freq. pulse ctrl | 16#390E = 14606 | 16#2074/7 | 16#AA/01/07 = 170/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Level fr. pulse ctrl] (FDT) | [Frequency meter] (FQF)
FQT | Pulse threshold wo Run | 16#390F = 14607 | 16#2074/8 | 16#AA/01/08 = 170/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 0 Hz | 0 Hz ... 1000 Hz | [Pulse thd. wo Run] (FQT) | [Frequency meter] (FQF)
NCA1 | Scan output 1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
NCA2 | Scan output 2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
NCA3 | Scan output 3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA4 | Scan output 4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA5 | Scan output 5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA6 | Scan output 6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA7 | Scan output 7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA8 | Scan output 8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA1 | Scan input 1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
NMA2 | Scan input 2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
NMA3 | Scan input 3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA4 | Scan input 4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA5 | Scan input 5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA6 | Scan input 6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA7 | Scan input 7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA8 | Scan input 8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA1 | Scan input 1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 | [Scan. IN1 address] (OMA1) | [DeviceNet] (DNC)
OMA2 | Scan input 2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 | [Scan. IN2 address] (OMA2) | [DeviceNet] (DNC)
OMA3 | Scan input 3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan. IN3 address] (OMA3) | [DeviceNet] (DNC)
OMA4 | Scan input 4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan. IN4 address] (OMA4) | [DeviceNet] (DNC)
OMA5 | Scan input 5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA6 | Scan input 6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA1 | Scan output 1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 | [Scan.Out1 address] (OCA1) | [DeviceNet] (DNC)
OCA2 | Scan output 2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 | [Scan.Out2 address] (OCA2) | [DeviceNet] (DNC)
OCA3 | Scan output 3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan.Out3 address] (OCA3) | [DeviceNet] (DNC)
OCA4 | Scan output 4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan.Out4 address] (OCA4) | [DeviceNet] (DNC)
OCA5 | Scan output 5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA6 | Scan output 6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ADD | Drive Modbus Address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus Address] (ADD) | [Modbus Fieldbus] (MD1)
AMOC | Mdb add comm. Module | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus add Com.C.] (AMOC) | [Modbus Fieldbus] (MD1)
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus baud rate] (TBR) | [Modbus Fieldbus] (MD1)
TFO | Modbus format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus Format] (TFO) | [Modbus Fieldbus] (MD1)
TTO | Modbus timeout | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [ModbusTimeout] (TTO) | [Modbus Fieldbus] (MD1)
ADCO | Drive CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 127 | [CANopen Address ] (ADCO) | [CANopen ] (CNO)
BDCO | CANopen baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Baud rate 250kbps] 250K |  | [CANopen Baudrate] (BDCO) | [CANopen ] (CNO)
ERCO | CANopen error | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [CANopen Error] (ERCO) | [CANopen map] (CNM) [CANopen ] (CNO)
FLO | Forced local assignment | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forced Local Assign] (FLO) | [Command and Reference] (CRP)
FLOC | Forced Local frequency assignment | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Forced Local Freq] (FLOC) | [Command and Reference] (CRP)
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOT) | [Command and Reference] (CRP)
ADRC | Drive address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (ADRC) | [DeviceNet] (DNC) [Profibus] (PBC)
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [PPO profile used] (PRFL) | [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN)
DPMA | DP Master Active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R/W | WORD (Enumeration) | - | [Master 1] 1 |  | [DP Master Active] (DPMA) | [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN)
ECSA | EtherCAT second address | 16#1A23 = 6691 | 16#2024/5C | 16#82/01/5C = 130/01/92 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [EthCat 2nd addr] (ECSA) | [EtherCAT Module] (ETC)
CIOA | Configured Assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIOA) | [DeviceNet] (DNC)
BDR | Comm. option baud rate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [Automatic] AUTO |  | [Bit rate] (BDR) | [DeviceNet] (DNC)
MRJ | Communication port 1 assignment | 16#179F = 6047 | 16#201E/30 | 16#7F/01/30 = 127/01/48 | MRJ | Configuration and settings | R | WORD (Enumeration) | - | [Modbus 1] MDB |  | [Comm Port 1 Assign] (MRJ) | [Modbus Fieldbus] (MD1)
MRJ2 | Communication port 2 assignment | 16#179E = 6046 | 16#201E/2F | 16#7F/01/2F = 127/01/47 | MRJ | Configuration and settings | R | WORD (Enumeration) | - | [Modbus 1] MDB |  | [Comm Port 2 Assign] (MRJ2) | [Modbus HMI] (MD2)
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R/W | WORD (Enumeration) | - | [Automatic] AUTO |  | [Data rate used] (BDRU) | [DEVICENET DIAG] (DVN) [PROFIBUS DIAG] (PRB)
RDS | Rate and duplex setting | 16#FAFB = 64251 |  |  | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto detected] AUTO |  | [Rate setting] (RDS) | [Eth Module Config] (ETO)
EWE | Enable web and/or email | 16#FB08 = 64264 |  |  |  | Configuration and settings | R/W | WORD (BitString16) | - | 1
ARD | Actual rate and duplex | 16#FB0A = 64266 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Actual rate] (ARD) | [Ethernet Module Diag] (MTE) [Eth Module Config] (ETO)
L1D | DI1 Delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI1 Delay] (L1D) | [DI1 Configuration] (DI1)
R1 | R1 Assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in operating state "Fault"] FLT |  | [R1 Assignment] (R1) | [R1 configuration] (R1)
R2 | R2 Assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [R2 Assignment] (R2) | [R2 configuration] (R2)
L2D | DI2 Delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI2 Delay] (L2D) | [DI2 Configuration] (DI2)
R1D | R1 Delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (R1D) | [R1 configuration] (R1)
R2D | R2 Delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (R2D) | [R2 configuration] (R2)
L3D | DI3 Delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI3 Delay] (L3D) | [DI3 Configuration] (DI3)
R1S | R1 Active level | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R1 Active at] (R1S) | [R1 configuration] (R1)
R2S | R2 Active level | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R2 Active at] (R2S) | [R2 configuration] (R2)
L4D | DI4 Delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI4 Delay] (L4D) | [DI4 Configuration] (DI4)
R1H | R1 Holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R1 Holding time] (R1H) | [R1 configuration] (R1)
R2H | R2 Holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R2 Holding time] (R2H) | [R2 configuration] (R2)
L5D | DI5 Delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI5 Delay] (L5D) | [DI5 Configuration] (DI5)
L6D | DI6 Delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI6 Delay] (L6D) | [DI6 Configuration] (DI6)
L7D | DI7 Delay | 16#0FA7 = 4007 | 16#200A/8 | 16#75/01/08 = 117/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI7 Delay] (L7D) | [DI7 Configuration] (DI7)
L8D | DI8 Delay | 16#0FA8 = 4008 | 16#200A/9 | 16#75/01/09 = 117/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI8 Delay] (L8D) | [DI8 Configuration] (DI8)
DO1 | DQ1 Assignment | 16#13A7 = 5031 | 16#2014/20 | 16#7A/01/20 = 122/01/32 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ1 Assignment] (DO1) | [DQ1 configuration] (DO1)
DO1D | DQ1 Delay time | 16#10B9 = 4281 | 16#200C/52 | 16#76/01/52 = 118/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ1 Delay time] (DO1D) | [DQ1 configuration] (DO1)
DO1H | DQ1 Holding time | 16#10AF = 4271 | 16#200C/48 | 16#76/01/48 = 118/01/72 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ1 Holding time] (DO1H) | [DQ1 configuration] (DO1)
DO1S | DQ1 Active level | 16#10A5 = 4261 | 16#200C/3E | 16#76/01/3E = 118/01/62 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [DQ1 Active at] (DO1S) | [DQ1 configuration] (DO1)
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
MMF | Measured output freq. | 16#0C93 = 3219 | 16#2002/14 | 16#71/01/14 = 113/01/20 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Measured output fr.] (MMF) | [Drive parameters] (MPI)
SOTR | OTR without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 |  | Configuration and settings | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 |  | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 %
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
PGI | Number of pulses | 16#15E4 = 5604 | 16#201A/5 | 16#7D/01/05 = 125/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1024 | 100 ... 10000 | [Number of pulses] (PGI) | [Encoder configuration] (IEN)
ENS | AB Encoder type configuration | 16#15E8 = 5608 | 16#201A/9 | 16#7D/01/09 = 125/01/09 | ENS | Configuration and settings | R/WS | WORD (Enumeration) | - | [For signals A/A-/B/B-] AABB |  | [AB Encoder type] (ENS) | [Encoder configuration] (IEN)
ENU | Encoder usage | 16#15E6 = 5606 | 16#201A/7 | 16#7D/01/07 = 125/01/07 | ENU | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Encoder usage] (ENU) | [Encoder configuration] (IEN)
ENC | Encoder check | 16#15E5 = 5605 | 16#201A/6 | 16#7D/01/06 = 125/01/06 | ENC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Encoder check not done] NO |  | [Encoder check] (ENC) | [Encoder configuration] (IEN)
ECC | Encoder coupling monitoring | 16#15E7 = 5607 | 16#201A/8 | 16#7D/01/08 = 125/01/08 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Encoder Coupling Monit] (ECC) | [Encoder monitoring] (SDD)
ECT | Encoder check time | 16#15E9 = 5609 | 16#201A/A | 16#7D/01/0A = 125/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 2.0 s | 2.0 s ... 10.0 s | [Encoder check time] (ECT) | [Encoder monitoring] (SDD)
RPPN | Resolver poles nbr | 16#15ED = 5613 | 16#201A/E | 16#7D/01/0E = 125/01/14 | RPPN | Configuration and settings | R/WS | WORD (Enumeration) | - | [2 poles] 2P |  | [Resolver poles nbr] (RPPN) | [Encoder configuration] (IEN)
UECP | Encoder type | 16#15EF = 5615 | 16#201A/10 | 16#7D/01/10 = 125/01/16 | UECP | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Encoder Type] (UECP) | [Encoder configuration] (IEN)
UECV | Encoder supply voltage | 16#15F0 = 5616 | 16#201A/11 | 16#7D/01/11 = 125/01/17 | UECV | Configuration and settings | R/WS | WORD (Enumeration) | - | [Undefined] UND |  | [Encoder supply volt.] (UECV) | [Encoder configuration] (IEN)
ENRI | Inversion of encoder rotation direction | 16#15F2 = 5618 | 16#201A/13 | 16#7D/01/13 = 125/01/19 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Encoder rotation inv.] (ENRI) | [Encoder configuration] (IEN)
FFA | Encoder feeback filter activation | 16#15FE = 5630 | 16#201A/1F | 16#7D/01/1F = 125/01/31 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Encoder filter activ.] (FFA) | [Spd Loop Optimization] (MCL) [Encoder configuration] (IEN)
FFR | Encoder feedback filter value | 16#15FF = 5631 | 16#201A/20 | 16#7D/01/20 = 125/01/32 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 ms | Refer to programming manual | 0.0 ms ... 40.0 ms | [Encoder filter value] (FFR) | [Spd Loop Optimization] (MCL) [Encoder configuration] (IEN)
ULT | Underld T. Delay Detect. | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld T. Del. Detect] (ULT) | [Process underload] (ULD)
SRB | Hysteresis Frequency | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 300.0 Hz | [Hysteresis Freq] (SRB) | [Settings] (SET) [Process underload] (ULD) [Process overload] (OLD)
UDL | Underload Management | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Underload Mangmt.] (UDL) | [Process underload] (ULD)
RMUD | Unld. Freq.Thr. Detection | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Unld. FreqThr. Det.] (RMUD) | [Settings] (SET) [Process underload] (ULD)
LUL | Unld.Thr. at O speed | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [Settings] (SET) [Process underload] (ULD)
LUN | Unld.Thr. at Nom. speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUN) | [Settings] (SET) [Process underload] (ULD)
TOL | Overload Time Detect. | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Time Detect.] (TOL) | [Process overload] (OLD)
ODL | Ovld.Proces Management | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Ovld.Proces.Mngmt] (ODL) | [Process overload] (OLD)
ACCP | PID acceleration time | 16#2ED1 = 11985 | 16#2059/56 | 16#9C/01/BA = 156/01/186 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [PID acceleration time] (ACCP) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
ACCS | Acceleration on Start | 16#2350 = 9040 | 16#203C/29 | 16#8E/01/29 = 142/01/41 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 9999 | [Start Accel Ramp] (ACCS) | [Pump start stop] (PST) [Settings] (SET)
AI1I | AI1 input physical image (MAX = 8192) | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2I | AI2 input physical image (MAX = 8192) | 16#1467 = 5223 | 16#2016/18 | 16#7B/01/18 = 123/01/24 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3I | AI3 input physical image (MAX = 8192) | 16#1468 = 5224 | 16#2016/19 | 16#7B/01/19 = 123/01/25 |  | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AI4C | Physical value AI4 | 16#147D = 5245 | 16#2016/2E | 16#7B/01/2E = 123/01/46 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI4E | AI4 intermediate point X | 16#1171 = 4465 | 16#200E/42 | 16#77/01/42 = 119/01/66 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 X Interm. point] (AI4E) | [AI4 configuration] (AI4)
AI4F | AI4 filter | 16#1167 = 4455 | 16#200E/38 | 16#77/01/38 = 119/01/56 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI4 filter] (AI4F) | [AI4] (AI4C) [AI4 configuration] (AI4)
AI4I | AI4 input physical image (MAX = 8192) | 16#1469 = 5225 | 16#2016/1A | 16#7B/01/1A = 123/01/26 |  | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AI4R | AI4 real application image (MAX = 8192) | 16#1473 = 5235 | 16#2016/24 | 16#7B/01/24 = 123/01/36 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI4S | AI4 intermediate point Y | 16#117B = 4475 | 16#200E/4C | 16#77/01/4C = 119/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 Y Interm.point] (AI4S) | [AI4 configuration] (AI4)
AI4T | Configuration of AI4 | 16#1135 = 4405 | 16#200E/6 | 16#77/01/06 = 119/01/06 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI4 Type] (AI4T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
AI5C | AI5 customer image (1mV, 0.001mA) | 16#147E = 5246 | 16#2016/2F | 16#7B/01/2F = 123/01/47 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI5E | AI5 delinearization input level | 16#1172 = 4466 | 16#200E/43 | 16#77/01/43 = 119/01/67 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 X Interm. point] (AI5E) | [AI5 configuration] (AI5)
AI5F | AI5 cutoff time of the low-filter | 16#1168 = 4456 | 16#200E/39 | 16#77/01/39 = 119/01/57 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI5 filter] (AI5F) | [AI5] (AI5C) [AI5 configuration] (AI5)
AI5I | AI5 input physical image (MAX = 8192) | 16#146A = 5226 | 16#2016/1B | 16#7B/01/1B = 123/01/27 |  | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AI5R | AI5 real application image (MAX = 8192) | 16#1474 = 5236 | 16#2016/25 | 16#7B/01/25 = 123/01/37 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI5S | AI5 delinearization output level | 16#117C = 4476 | 16#200E/4D | 16#77/01/4D = 119/01/77 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 Y Interm.point] (AI5S) | [AI5 configuration] (AI5)
AI5T | AI5 type | 16#1136 = 4406 | 16#200E/7 | 16#77/01/07 = 119/01/07 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI5 Type] (AI5T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
AIC1 | Channel assignment for virtual Analog Input AIV1 | 16#14A2 = 5282 | 16#2016/53 | 16#7B/01/53 = 123/01/83 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AIV1 Channel Assign] (AIC1) | [Virtual AI1] (AV1)
AO1I | AO1 output physical image (MAX = 8192) | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO2 | AQ2 assignment | 16#139E = 5022 | 16#2014/17 | 16#7A/01/17 = 122/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor current] OCR |  | [AQ2 assignment] (AO2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AO2C | AQ2 physical value | 16#1498 = 5272 | 16#2016/49 | 16#7B/01/49 = 123/01/73 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AO2F | AQ2 filter | 16#1204 = 4612 | 16#2010/D | 16#78/01/0D = 120/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ2 Filter] (AO2F) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AO2I | AO2 output physical image (MAX = 8192) | 16#1484 = 5252 | 16#2016/35 | 16#7B/01/35 = 123/01/53 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO2R | AO2 real application image (MAX = 8192) | 16#148E = 5262 | 16#2016/3F | 16#7B/01/3F = 123/01/63 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AO2T | Configuration of AQ2 | 16#11FA = 4602 | 16#2010/3 | 16#78/01/03 = 120/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AQ2 Type] (AO2T) | [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
AOH2 | AQ2 max output value | 16#122C = 4652 | 16#2010/35 | 16#78/01/35 = 120/01/53 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ2 max output] (AOH2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
AOL2 | AQ2 min output value | 16#1222 = 4642 | 16#2010/2B | 16#78/01/2B = 120/01/43 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ2 min output] (AOL2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
APPS | Application state | 16#3E6C = 15980 | 16#2081/51 | 16#B0/01/B5 = 176/01/181 | APPS | Status parameters | R | WORD (Enumeration) | - |  |  | [Application state] (APPS) | [Application Parameters] (APR)
ASH2 | Scaling AQ2 max | 16#1240 = 4672 | 16#2010/49 | 16#78/01/49 = 120/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 max] (ASH2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
ASL2 | Scaling AQ2 min | 16#1236 = 4662 | 16#2010/3F | 16#78/01/3F = 120/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 min] (ASL2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
CAR | Customer Warning clearing | 16#3F98 = 16280 | 16#2084/51 | 16#B2/01/51 = 178/01/81 | CAR | Configuration and settings | R/W | WORD (Enumeration) | - | [No Warning clearing] NO |  | [Warning Clearing] (CAR) | [Customer events] (CUEV)
CASH | Money saved | 16#2A36 = 10806 | 16#204E/7 | 16#97/01/07 = 151/01/07 |  | Actual values parameters | R | UINT (Unsigned32) | Refer to programming manual |  | 0 ... 4294967295 | [Money Saved] (CASH) | [Energy Saving] (ESA)
CC1 | Time Counter 1 | 16#3F84 = 16260 | 16#2084/3D | 16#B2/01/3D = 178/01/61 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 1] (CC1) | [Customer event 1] (CE1)
CC2 | Time Counter 2 | 16#3F86 = 16262 | 16#2084/3F | 16#B2/01/3F = 178/01/63 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 2] (CC2) | [Customer event 2] (CE2)
CC3 | Time Counter 3 | 16#3F88 = 16264 | 16#2084/41 | 16#B2/01/41 = 178/01/65 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 3] (CC3) | [Customer event 3] (CE3)
CC4 | Time Counter 4 | 16#3F8A = 16266 | 16#2084/43 | 16#B2/01/43 = 178/01/67 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 4] (CC4) | [Customer event 4] (CE4)
CC5 | Time Counter 5 | 16#3F8C = 16268 | 16#2084/45 | 16#B2/01/45 = 178/01/69 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 5] (CC5) | [Customer event 5] (CE5)
CCA1 | Configuration of customer Warning 1 | 16#3F48 = 16200 | 16#2084/1 | 16#B2/01/01 = 178/01/01 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 1] (CCA1) | [Customer event 1] (CE1)
CCA2 | Configuration of customer Warning 2 | 16#3F49 = 16201 | 16#2084/2 | 16#B2/01/02 = 178/01/02 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 2] (CCA2) | [Customer event 2] (CE2)
CCA3 | Configuration of customer Warning 3 | 16#3F4A = 16202 | 16#2084/3 | 16#B2/01/03 = 178/01/03 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 3] (CCA3) | [Customer event 3] (CE3)
CCA4 | Configuration of customer Warning 4 | 16#3F4B = 16203 | 16#2084/4 | 16#B2/01/04 = 178/01/04 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 4] (CCA4) | [Customer event 4] (CE4)
CCA5 | Configuration of customer Warning 5 | 16#3F4C = 16204 | 16#2084/5 | 16#B2/01/05 = 178/01/05 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 5] (CCA5) | [Customer event 5] (CE5)
CCL1 | Configuration Counter Limit 1 | 16#3F70 = 16240 | 16#2084/29 | 16#B2/01/29 = 178/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 1] (CCL1) | [Customer event 1] (CE1)
CCL2 | Configuration Counter Limit 2 | 16#3F72 = 16242 | 16#2084/2B | 16#B2/01/2B = 178/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 2] (CCL2) | [Customer event 2] (CE2)
CCL3 | Configuration Counter Limit 3 | 16#3F74 = 16244 | 16#2084/2D | 16#B2/01/2D = 178/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 3] (CCL3) | [Customer event 3] (CE3)
CCL4 | Configuration Counter Limit 4 | 16#3F76 = 16246 | 16#2084/2F | 16#B2/01/2F = 178/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 4] (CCL4) | [Customer event 4] (CE4)
CCL5 | Configuration Counter Limit 5 | 16#3F78 = 16248 | 16#2084/31 | 16#B2/01/31 = 178/01/49 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 5] (CCL5) | [Customer event 5] (CE5)
CCS1 | Configuration Counter Source 1 | 16#3F52 = 16210 | 16#2084/B | 16#B2/01/0B = 178/01/11 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 1] (CCS1) | [Customer event 1] (CE1)
CCS2 | Configuration Counter Source 2 | 16#3F53 = 16211 | 16#2084/C | 16#B2/01/0C = 178/01/12 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 2] (CCS2) | [Customer event 2] (CE2)
CCS3 | Configuration Counter Source 3 | 16#3F54 = 16212 | 16#2084/D | 16#B2/01/0D = 178/01/13 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 3] (CCS3) | [Customer event 3] (CE3)
CCS4 | Configuration Counter Source 4 | 16#3F55 = 16213 | 16#2084/E | 16#B2/01/0E = 178/01/14 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 4] (CCS4) | [Customer event 4] (CE4)
CCS5 | Configuration Counter Source 5 | 16#3F56 = 16214 | 16#2084/F | 16#B2/01/0F = 178/01/15 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 5] (CCS5) | [Customer event 5] (CE5)
CDT1 | Date Time Warning 1 | 16#3F5C = 16220 | 16#2084/15 | 16#B2/01/15 = 178/01/21 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT2 | Date Time Warning 2 | 16#3F5E = 16222 | 16#2084/17 | 16#B2/01/17 = 178/01/23 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT3 | Date Time Warning 3 | 16#3F60 = 16224 | 16#2084/19 | 16#B2/01/19 = 178/01/25 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT4 | Date Time Warning 4 | 16#3F62 = 16226 | 16#2084/1B | 16#B2/01/1B = 178/01/27 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT5 | Date Time Warning 5 | 16#3F64 = 16228 | 16#2084/1D | 16#B2/01/1D = 178/01/29 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CMP9 | Cmd word | 16#1C47 = 7239 | 16#202A/28 | 16#85/01/28 = 133/01/40 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP9) | [None] (DP9)
CMPA | Cmd word | 16#1DCE = 7630 | 16#202E/1F | 16#87/01/1F = 135/01/31 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPA) | [None] (DPA)
CMPB | Cmd word | 16#1DCF = 7631 | 16#202E/20 | 16#87/01/20 = 135/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPB) | [None] (DPB)
CMPC | CMD command word | 16#1DD0 = 7632 | 16#202E/21 | 16#87/01/21 = 135/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPC) | [None] (DPC)
CMPD | CMD command word | 16#1DD1 = 7633 | 16#202E/22 | 16#87/01/22 = 135/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPD) | [None] (DPD)
CMPE | CMD command word | 16#1DD2 = 7634 | 16#202E/23 | 16#87/01/23 = 135/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPE) | [None] (DPE)
CMPF | CMD command word | 16#1DD3 = 7635 | 16#202E/24 | 16#87/01/24 = 135/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPF) | [None] (DPF)
CO2S | Co2 Saved | 16#2A38 = 10808 | 16#204E/9 | 16#97/01/09 = 151/01/09 |  | Actual values parameters | R | UINT (Unsigned32) | 0.1 t |  | 0.0 t ... 429496729.5 t | [Co2 Saved] (CO2S) | [Energy Saving] (ESA)
CRH1 | AI1 current scaling parameter of 100% | 16#115A = 4442 | 16#200E/2B | 16#77/01/2B = 119/01/43 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI1 Max Value] (CRH1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
CRH4 | AI4 current scaling parameter of 100% | 16#115D = 4445 | 16#200E/2E | 16#77/01/2E = 119/01/46 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI4 Max Value] (CRH4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
CRH5 | AI5 current scaling parameter of 100% | 16#115E = 4446 | 16#200E/2F | 16#77/01/2F = 119/01/47 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI5 Max Value] (CRH5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
CRL1 | AI1 current scaling parameter of 0% | 16#1150 = 4432 | 16#200E/21 | 16#77/01/21 = 119/01/33 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI1 Min. Value] (CRL1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [Speed Ref AI1 Config.] (MSR1) [Torque Ref AI1 Config.] (MTR1) [AI1 configuration] (AI1)
CRL4 | AI4 current scaling parameter of 0% | 16#1153 = 4435 | 16#200E/24 | 16#77/01/24 = 119/01/36 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI4 Min. Value] (CRL4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
CRL5 | AI5 current scaling parameter of 0% | 16#1154 = 4436 | 16#200E/25 | 16#77/01/25 = 119/01/37 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI5 Min. Value] (CRL5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
CRP9 | Cmd & ref channel | 16#1C83 = 7299 | 16#202A/64 | 16#85/01/64 = 133/01/100 |  | History parameters | R | WORD (BitString16) | -
CRPA | Cmd & ref channel | 16#1E0A = 7690 | 16#202E/5B | 16#87/01/5B = 135/01/91 |  | History parameters | R | WORD (BitString16) | -
CRPB | Cmd & ref channel | 16#1E0B = 7691 | 16#202E/5C | 16#87/01/5C = 135/01/92 |  | History parameters | R | WORD (BitString16) | -
CRPC | Cmd & ref channel | 16#1E0C = 7692 | 16#202E/5D | 16#87/01/5D = 135/01/93 |  | History parameters | R | WORD (BitString16) | -
CRPD | Cmd & ref channel | 16#1E0D = 7693 | 16#202E/5E | 16#87/01/5E = 135/01/94 |  | History parameters | R | WORD (BitString16) | -
CRPE | Cmd & ref channel | 16#1E0E = 7694 | 16#202E/5F | 16#87/01/5F = 135/01/95 |  | History parameters | R | WORD (BitString16) | -
CRPF | Cmd & ref channel | 16#1E0F = 7695 | 16#202E/60 | 16#87/01/60 = 135/01/96 |  | History parameters | R | WORD (BitString16) | -
CTDL | Low Current Threshold | 16#2B02 = 11010 | 16#2050/B | 16#98/01/0B = 152/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Low I Threshold] (CTDL) | [Threshold reached] (THRE) [Settings] (SET)
CVHS | Speed level from which check-valve ramp is used | 16#2352 = 9042 | 16#203C/2B | 16#8E/01/2B = 142/01/43 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Valve Spd 2] (CVHS) | [Pump start stop] (PST) [Settings] (SET)
CVLS | Speed Level up to which check-valve ramp is used | 16#2353 = 9043 | 16#203C/2C | 16#8E/01/2C = 142/01/44 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Valve Spd 1] (CVLS) | [Pump start stop] (PST) [Settings] (SET)
D11D | DQ11 activation delay | 16#10BB = 4283 | 16#200C/54 | 16#76/01/54 = 118/01/84 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ11 actv delay] (D11D) | [DQ11 Configuration] (DO11)
D11H | DQ11 holding delay | 16#10B1 = 4273 | 16#200C/4A | 16#76/01/4A = 118/01/74 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ11 hold delay] (D11H) | [DQ11 Configuration] (DO11)
D11S | DQ11 status (output active level) | 16#10A7 = 4263 | 16#200C/40 | 16#76/01/40 = 118/01/64 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [DQ11 status] (D11S) | [DQ11 Configuration] (DO11)
D12D | DQ12 activation delay | 16#10BC = 4284 | 16#200C/55 | 16#76/01/55 = 118/01/85 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ12 actv delay] (D12D) | [DQ12 Configuration] (DO12)
D12H | DQ12 holding delay | 16#10B2 = 4274 | 16#200C/4B | 16#76/01/4B = 118/01/75 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ12 hold delay] (D12H) | [DQ12 Configuration] (DO12)
D12S | DQ12 status (output active level) | 16#10A8 = 4264 | 16#200C/41 | 16#76/01/41 = 118/01/65 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [DQ12 status] (D12S) | [DQ12 Configuration] (DO12)
DECS | Deceleration on Stop | 16#2354 = 9044 | 16#203C/2D | 16#8E/01/2D = 142/01/45 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 9999 | [Final Dec. Ramp] (DECS) | [Pump start stop] (PST) [Settings] (SET)
DECV | Deceleration while check valve is closing (Smooth) | 16#2351 = 9041 | 16#203C/2A | 16#8E/01/2A = 142/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 9999 | [Dec. Check Valve] (DECV) | [Pump start stop] (PST) [Settings] (SET)
DM0 | Hour and minute of actual fault | 16#1C8E = 7310 | 16#202B/B | 16#85/01/6F = 133/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM1 | Hour and minute of fault record x (1 is last) | 16#1C8F = 7311 | 16#202B/C | 16#85/01/70 = 133/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM2 | Hour and minute of fault record x (1 is last) | 16#1C90 = 7312 | 16#202B/D | 16#85/01/71 = 133/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM3 | Hour and minute of fault record x (1 is last) | 16#1C91 = 7313 | 16#202B/E | 16#85/01/72 = 133/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM4 | Hour and minute of fault record x (1 is last) | 16#1C92 = 7314 | 16#202B/F | 16#85/01/73 = 133/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM5 | Hour and minute of fault record x (1 is last) | 16#1C93 = 7315 | 16#202B/10 | 16#85/01/74 = 133/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM6 | Hour and minute of fault record x (1 is last) | 16#1C94 = 7316 | 16#202B/11 | 16#85/01/75 = 133/01/117 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM7 | Hour and minute of fault record x (1 is last) | 16#1C95 = 7317 | 16#202B/12 | 16#85/01/76 = 133/01/118 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM8 | Hour and minute of fault record x (1 is last) | 16#1C96 = 7318 | 16#202B/13 | 16#85/01/77 = 133/01/119 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM9 | Hour and minute of fault record x (1 is last) | 16#1C97 = 7319 | 16#202B/14 | 16#85/01/78 = 133/01/120 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMA | Hour and minute of fault record x (1 is last) | 16#1E1E = 7710 | 16#202F/B | 16#87/01/6F = 135/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMB | Hour and minute of fault record x (1 is last) | 16#1E1F = 7711 | 16#202F/C | 16#87/01/70 = 135/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMC | Hour and minute of fault record x (1 is last) | 16#1E20 = 7712 | 16#202F/D | 16#87/01/71 = 135/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMD | Hour and minute of fault record x (1 is last) | 16#1E21 = 7713 | 16#202F/E | 16#87/01/72 = 135/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DME | Hour and minute of fault record x (1 is last) | 16#1E22 = 7714 | 16#202F/F | 16#87/01/73 = 135/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMF | Hour and minute of fault record x (1 is last) | 16#1E23 = 7715 | 16#202F/10 | 16#87/01/74 = 135/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DO11 | DO11 assignment | 16#13A9 = 5033 | 16#2014/22 | 16#7A/01/22 = 122/01/34 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ11 assignment] (DO11) | [DQ11 Configuration] (DO11)
DO12 | DO12 assignment | 16#13AA = 5034 | 16#2014/23 | 16#7A/01/23 = 122/01/35 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ12 assignment] (DO12) | [DQ12 Configuration] (DO12)
DP9 | Fault record 9 (1 is last) | 16#1C29 = 7209 | 16#202A/A | 16#85/01/0A = 133/01/10 | LFT | History parameters | R | WORD (Enumeration) | -
DPA | Fault record 10 (1 is last) | 16#1DB0 = 7600 | 16#202E/1 | 16#87/01/01 = 135/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
DPB | Fault record 11 (1 is last) | 16#1DB1 = 7601 | 16#202E/2 | 16#87/01/02 = 135/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
DPC | Fault record 12 (1 is last) | 16#1DB2 = 7602 | 16#202E/3 | 16#87/01/03 = 135/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
DPD | Fault record 13 (1 is last) | 16#1DB3 = 7603 | 16#202E/4 | 16#87/01/04 = 135/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
DPE | Fault record 14 (1 is last) | 16#1DB4 = 7604 | 16#202E/5 | 16#87/01/05 = 135/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
DPF | Fault record 15 (1 is last) | 16#1DB5 = 7605 | 16#202E/6 | 16#87/01/06 = 135/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
DRYD | Dry Run error time delay | 16#3E50 = 15952 | 16#2081/35 | 16#B0/01/99 = 176/01/153 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 5 s | 0 s ... 3600 s | [DryRun Error Delay] (DRYD) | [Dry run Monit] (DYR) [Settings] (SET)
DRYM | Dry Run Mode | 16#3E4E = 15950 | 16#2081/33 | 16#B0/01/97 = 176/01/151 | DRYM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [DryRun Mode] (DRYM) | [Dry run Monit] (DYR)
DRYR | Dry Run restart time delay | 16#3E51 = 15953 | 16#2081/36 | 16#B0/01/9A = 176/01/154 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 60 s | 10 s ... 3600 s | [DryRun Restart Delay] (DRYR) | [Dry run Monit] (DYR) [Settings] (SET)
DRYW | Dry Run Switch Select | 16#3E4F = 15951 | 16#2081/34 | 16#B0/01/98 = 176/01/152 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Switch Select] (DRYW) | [Dry run Monit] (DYR)
DRYX | Dry Run Factor | 16#3E52 = 15954 | 16#2081/37 | 16#B0/01/9B = 176/01/155 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 90 % | 0 % ... 100 % | [Dry Run Factor] (DRYX) | [Dry run Monit] (DYR) [Settings] (SET)
ECI | Energy Consumption Indicator | 16#3EB5 = 16053 | 16#2082/36 | 16#B1/01/36 = 177/01/54 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | 0 ... 32767 | [Energy Cons. Ind.] (ECI) | [Variable Speed Pump] (MPP)
ECO2 | CO2 ratio | 16#2A32 = 10802 | 16#204E/3 | 16#97/01/03 = 151/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.001 kg/kWh | 0.000 kg/kWh | 0.000 kg/kWh ... 65.535 kg/kWh | [CO2 ratio] (ECO2) | [Energy Saving] (ESA)
ECST | kWh Cost | 16#2A31 = 10801 | 16#204E/2 | 16#97/01/02 = 151/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [kWh Cost] (ECST) | [Energy Saving] (ESA)
EFY | Efficiency | 16#3EB2 = 16050 | 16#2082/33 | 16#B1/01/33 = 177/01/51 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Efficiency] (EFY) | [Variable Speed Pump] (MPP)
EFYJ | Lowest Efficiency | 16#3EB4 = 16052 | 16#2082/35 | 16#B1/01/35 = 177/01/53 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Lowest Eff.] (EFYJ) | [Variable Speed Pump] (MPP)
EFYK | Highest Efficiency | 16#3EB3 = 16051 | 16#2082/34 | 16#B1/01/34 = 177/01/52 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Highest Eff.] (EFYK) | [Variable Speed Pump] (MPP)
EP9 | Status of last error 1 | 16#1C33 = 7219 | 16#202A/14 | 16#85/01/14 = 133/01/20 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP9) | [None] (DP9)
EPA | Status of last error 2 | 16#1DBA = 7610 | 16#202E/B | 16#87/01/0B = 135/01/11 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EPA) | [None] (DPA)
EPB | Status of last error 3 | 16#1DBB = 7611 | 16#202E/C | 16#87/01/0C = 135/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EPB) | [None] (DPB)
EPC | Status of last error 4 | 16#1DBC = 7612 | 16#202E/D | 16#87/01/0D = 135/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EPC) | [None] (DPC)
EPD | State word | 16#1DBD = 7613 | 16#202E/E | 16#87/01/0E = 135/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPD) | [None] (DPD)
EPE | State word | 16#1DBE = 7614 | 16#202E/F | 16#87/01/0F = 135/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPE) | [None] (DPE)
EPF | State word | 16#1DBF = 7615 | 16#202E/10 | 16#87/01/10 = 135/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPF) | [None] (DPF)
EPI | Energy Performance Indicator | 16#3EB6 = 16054 | 16#2082/37 | 16#B1/01/37 = 177/01/55 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | 0 ... 32767 | [Energy Perf. Ind] (EPI) | [Variable Speed Pump] (MPP)
EPRW | Active Electrical output power estimation | 16#0CDD = 3293 | 16#2002/5E | 16#71/01/5E = 113/01/94 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Acv Elc Out Pwr Estm] (EPRW) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO) [Variable Speed Pump] (MPP)
ERR | Ethernet Error Code | 16#FB0E = 64270 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Ethernet Error Code] (ERR) | [Ethernet Module Diag] (MTE)
ESAV | Energy Saved | 16#2A34 = 10804 | 16#204E/5 | 16#97/01/05 = 151/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Energy Saved] (ESAV) | [Energy Saving] (ESA)
ETAD | DRIVECOM : Status word | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 |  | Status parameters | R | WORD (BitString16) | -
ETHF | Ethernet embedded fault (ETHF) | 16#1BE0 = 7136 | 16#2029/25 | 16#84/01/89 = 132/01/137 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
ETHL | Ethernet error response | 16#1B6D = 7021 | 16#2028/16 | 16#84/01/16 = 132/01/22 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Eth Error Response] (ETHL) | [Embedded modbus TCP] (EMTC) [Communication Module] (COMO)
F2DL | 2 Frequency Threshold | 16#2B04 = 11012 | 16#2050/D | 16#98/01/0D = 152/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [2 Freq. Threshold] (F2DL) | [Threshold reached] (THRE) [Settings] (SET)
FPBT | Fan operation time | 16#0CC0 = 3264 | 16#2002/41 | 16#71/01/41 = 113/01/65 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [Fan Operation Time] (FPBT) | [Counter Management] (ELT) [V0_SubmenuCounterManagement] (COMA)
FEM | Flow Estimation Mode | 16#3E80 = 16000 | 16#2082/1 | 16#B1/01/01 = 177/01/01 | FEM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disable pump characteristics] NO |  | [Flow Estimation Mode] (FEM) | [Flow estimation] (SFE)
FS1C | Total Quantity | 16#3D65 = 15717 | 16#207F/12 | 16#AF/01/76 = 175/01/118 |  | Actual values parameters | R/WS | INT (Signed32) | Refer to programming manual |  | 0 ... 2147483647 | [Total Quantity] (FS1C) | [Application Parameters] (APR)
FS1J | LowestFlow | 16#3EB8 = 16056 | 16#2082/39 | 16#B1/01/39 = 177/01/57 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Lowest Flow] (FS1J) | [Application Parameters] (APR)
FS1K | Highest Flow | 16#3EB7 = 16055 | 16#2082/38 | 16#B1/01/38 = 177/01/56 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Highest Flow] (FS1K) | [Application Parameters] (APR)
FSPD | Fan speed | 16#0CBF = 3263 | 16#2002/40 | 16#71/01/40 = 113/01/64 |  | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
FTDL | Low Freq. Threshold | 16#2B03 = 11011 | 16#2050/C | 16#98/01/0C = 152/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Low Freq.Threshold] (FTDL) | [Threshold reached] (THRE) [Settings] (SET)
FTO | Ovld time Before Restart | 16#3857 = 14423 | 16#2072/18 | 16#A9/01/18 = 169/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Overload T.B.Rest.] (FTO) | [Settings] (SET) [Process overload] (OLD)
FTU | Unld Time Before Restart | 16#384D = 14413 | 16#2072/E | 16#A9/01/0E = 169/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Underload T.B.Rest.] (FTU) | [Settings] (SET) [Process underload] (ULD)
GRFL | Ground Fault activation | 16#1B76 = 7030 | 16#2028/1F | 16#84/01/1F = 132/01/31 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 % | -0.1 % | -0.2 % ... 100.0 % | [Ground Fault Activation] (GRFL) | [Ground Fault ] (GRFL)
GIVB | Response to input ground fault | 16#9CC3 = 40131 |  |  | GOVB | Configuration and settings | R/W | WORD (Enumeration) | - | [Ground warning] ALRM
GIVL | Input ground fault level | 16#9CBA = 40122 |  |  |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | -0.1 % | -0.1 % ... 200.0 %
GIVT | Input ground fault timeout | 16#9CBB = 40123 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.1 s | 0.1 s ... 6000.0 s
GOVB | Response to output ground fault | 16#9CC2 = 40130 |  |  | GOVB | Configuration and settings | R/W | WORD (Enumeration) | - | [Ground warning] ALRM
GOVL | Output ground fault level | 16#9CB8 = 40120 |  |  |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | -0.1 % | -0.1 % ... 200.0 %
GOVT | Output ground fault timeout | 16#9CB9 = 40121 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.1 s | 0.1 s ... 6000.0 s
HS9 | Drive state | 16#1CA1 = 7329 | 16#202B/1E | 16#85/01/82 = 133/01/130 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS9) | [None] (DP9)
HSA | Drive state | 16#1E28 = 7720 | 16#202F/15 | 16#87/01/79 = 135/01/121 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSA) | [None] (DPA)
HSB | Drive state | 16#1E29 = 7721 | 16#202F/16 | 16#87/01/7A = 135/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSB) | [None] (DPB)
HSC | Drive state | 16#1E2A = 7722 | 16#202F/17 | 16#87/01/7B = 135/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSC) | [None] (DPC)
HSD | Drive state | 16#1E2B = 7723 | 16#202F/18 | 16#87/01/7C = 135/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSD) | [None] (DPD)
HSE | Drive state | 16#1E2C = 7724 | 16#202F/19 | 16#87/01/7D = 135/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSE) | [None] (DPE)
HSF | Drive state | 16#1E2D = 7725 | 16#202F/1A | 16#87/01/7E = 135/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSF) | [None] (DPF)
IC0 | Input Energy (Wh) | 16#2982 = 10626 | 16#204C/1B | 16#96/01/1B = 150/01/27 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh
IC1 | Input Energy (kWh) | 16#2983 = 10627 | 16#204C/1C | 16#96/01/1C = 150/01/28 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh
IC2 | Input Energy (MWh) | 16#2984 = 10628 | 16#204C/1D | 16#96/01/1D = 150/01/29 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh
IC3 | Input Energy (GWh) | 16#2985 = 10629 | 16#204C/1E | 16#96/01/1E = 150/01/30 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh
IC4 | Input Energy (TWh) | 16#2986 = 10630 | 16#204C/1F | 16#96/01/1F = 150/01/31 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh
IE0 | Real Input Energy (Wh) | 16#298C = 10636 | 16#204C/25 | 16#96/01/25 = 150/01/37 |  | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Input Energy] (IE0) | [Elec Ener Input Counter] (ELI)
IE1 | Real Input Energy (kWh) | 16#298D = 10637 | 16#204C/26 | 16#96/01/26 = 150/01/38 |  | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Input Energy] (IE1) | [Elec Ener Input Counter] (ELI)
IE2 | Real Input Energy (MWh) | 16#298E = 10638 | 16#204C/27 | 16#96/01/27 = 150/01/39 |  | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Input Energy] (IE2) | [Elec Ener Input Counter] (ELI)
IE3 | Real Input Energy (GWh) | 16#298F = 10639 | 16#204C/28 | 16#96/01/28 = 150/01/40 |  | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Input Energy] (IE3) | [Elec Ener Input Counter] (ELI)
IE4 | Real Input Energy (TWh) | 16#2990 = 10640 | 16#204C/29 | 16#96/01/29 = 150/01/41 |  | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Input Energy] (IE4) | [Elec Ener Input Counter] (ELI)
IL1I | Logic inputs physical image (bit0 = LI1 ...) | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 |  | I/O parameters | R | WORD (BitString16) | -
INRC | NCR current scaling | 16#2649 = 9801 | 16#2044/2 | 16#92/01/02 = 146/01/02 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRL | LFA inductance scaling | 16#264C = 9804 | 16#2044/5 | 16#92/01/05 = 146/01/05 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRP | NPR power scaling | 16#264A = 9802 | 16#2044/3 | 16#92/01/03 = 146/01/03 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRR | RSA resistance scaling | 16#264B = 9803 | 16#2044/4 | 16#92/01/04 = 146/01/04 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRT | TQS torque scaling | 16#264D = 9805 | 16#2044/6 | 16#92/01/06 = 146/01/06 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INTI | TRA time scaling | 16#264E = 9806 | 16#2044/7 | 16#92/01/07 = 146/01/07 | CINR | Configuration and settings | R | WORD (Enumeration) | -
IP9 | ETI state word | 16#1C3D = 7229 | 16#202A/1E | 16#85/01/1E = 133/01/30 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP9) | [None] (DP9)
IPA | ETI state word | 16#1DC4 = 7620 | 16#202E/15 | 16#87/01/15 = 135/01/21 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPA) | [None] (DPA)
IPAD | iPar detected error code | 16#FB18 = 64280 |  |  |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Code] (IPAD) | [PROFINET DIAG] (PRN)
IPB | ETI state word | 16#1DC5 = 7621 | 16#202E/16 | 16#87/01/16 = 135/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPB) | [None] (DPB)
IPC | ETI state word | 16#1DC6 = 7622 | 16#202E/17 | 16#87/01/17 = 135/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPC) | [None] (DPC)
IPD | ETI state word | 16#1DC7 = 7623 | 16#202E/18 | 16#87/01/18 = 135/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPD) | [None] (DPD)
IPE | ETI state word | 16#1DC8 = 7624 | 16#202E/19 | 16#87/01/19 = 135/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPE) | [None] (DPE)
IPF | ETI state word | 16#1DC9 = 7625 | 16#202E/1A | 16#87/01/1A = 135/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPF) | [None] (DPF)
IPR | Active Electrical input power estimation (100% = drive power) | 16#0C92 = 3218 | 16#2002/13 | 16#71/01/13 = 113/01/19 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | 0 % ... 65535 %
IPRW | Instantaneous active input power | 16#0CDE = 3294 | 16#2002/5F | 16#71/01/5F = 113/01/95 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Active Input Power] (IPRW) | [Elec Ener Input Counter] (ELI)
L11D | DI11 Delay | 16#0FAB = 4011 | 16#200A/C | 16#75/01/0C = 117/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI11 Delay] (L11D) | [DI11 Configuration] (DI11)
L12D | DI12 Delay | 16#0FAC = 4012 | 16#200A/D | 16#75/01/0D = 117/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI12 Delay] (L12D) | [DI12 Configuration] (DI12)
L13D | DI13 Delay | 16#0FAD = 4013 | 16#200A/E | 16#75/01/0E = 117/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI13 Delay] (L13D) | [DI13 Configuration] (DI13)
L14D | DI14 Delay | 16#0FAE = 4014 | 16#200A/F | 16#75/01/0F = 117/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI14 Delay] (L14D) | [DI14 Configuration] (DI14)
L15D | DI15 delay | 16#0FAF = 4015 | 16#200A/10 | 16#75/01/10 = 117/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI15 Delay] (L15D) | [DI15 Configuration] (DI15)
L16D | DI16 delay | 16#0FB0 = 4016 | 16#200A/11 | 16#75/01/11 = 117/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI16 Delay] (L16D) | [DI16 Configuration] (DI16)
LALR | Last Warning | 16#325A = 12890 | 16#2062/5B | 16#A1/01/5B = 161/01/91 | ALR | Actual values parameters | R | WORD (Enumeration) | - |  |  | [Last Warning] (LALR) | [Diag. data] (DDT)
LCAC | LifeCycle Warning Configuration | 16#3598 = 13720 | 16#206B/15 | 16#A5/01/79 = 165/01/121 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [LifeCycle Warning] (LCAC) | [Drive warranty mgnt] (DWMA)
LCAD | Life Cycle Date | 16#3599 = 13721 | 16#206B/16 | 16#A5/01/7A = 165/01/122 |  | Actual values parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Warranty expired] (LCAD) | [Drive warranty mgnt] (DWMA)
LCP9 | Motor current | 16#1C51 = 7249 | 16#202A/32 | 16#85/01/32 = 133/01/50 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP9) | [None] (DP9)
LCPA | Motor current | 16#1DD8 = 7640 | 16#202E/29 | 16#87/01/29 = 135/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPA) | [None] (DPA)
LCPB | Motor current | 16#1DD9 = 7641 | 16#202E/2A | 16#87/01/2A = 135/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPB) | [None] (DPB)
LCPC | Motor current | 16#1DDA = 7642 | 16#202E/2B | 16#87/01/2B = 135/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPC) | [None] (DPC)
LCPD | Motor current | 16#1DDB = 7643 | 16#202E/2C | 16#87/01/2C = 135/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPD) | [None] (DPD)
LCPE | Motor current | 16#1DDC = 7644 | 16#202E/2D | 16#87/01/2D = 135/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPE) | [None] (DPE)
LCPF | Motor current | 16#1DDD = 7645 | 16#202E/2E | 16#87/01/2E = 135/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPF) | [None] (DPF)
LDD1 | Log Distribution Data 1 | 16#4010 = 16400 | 16#2086/1 | 16#B3/01/01 = 179/01/01 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 1] (LDD1) | [Log dstrb prm select] (LDP)
LDD2 | Log Distribution Data 2 | 16#4012 = 16402 | 16#2086/3 | 16#B3/01/03 = 179/01/03 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib.Data 2] (LDD2) | [Log dstrb prm select] (LDP)
LDD3 | Log Distribution Data 3 | 16#4014 = 16404 | 16#2086/5 | 16#B3/01/05 = 179/01/05 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 3] (LDD3) | [Log dstrb prm select] (LDP)
LDD4 | Log Distribution Data 4 | 16#4016 = 16406 | 16#2086/7 | 16#B3/01/07 = 179/01/07 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 4] (LDD4) | [Log dstrb prm select] (LDP)
LDEN | Logging Distribution State | 16#4019 = 16409 | 16#2086/A | 16#B3/01/0A = 179/01/10 | LDEN | Configuration and settings | R/W | WORD (Enumeration) | - | [Stop] STOP |  | [Log Distrib State] (LDEN) | [Distributed logging] (DLO)
LDM1 | Distribution data max value 1 | 16#4011 = 16401 | 16#2086/2 | 16#B3/01/02 = 179/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 1] (LDM1) | [Distributed logging] (DLO)
LDM2 | Distribution data max value 2 | 16#4013 = 16403 | 16#2086/4 | 16#B3/01/04 = 179/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 2] (LDM2) | [Distributed logging] (DLO)
LDM3 | Distribution data max value 3 | 16#4015 = 16405 | 16#2086/6 | 16#B3/01/06 = 179/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 3] (LDM3) | [Distributed logging] (DLO)
LDM4 | Distribution data max value 4 | 16#4017 = 16407 | 16#2086/8 | 16#B3/01/08 = 179/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 4] (LDM4) | [Distributed logging] (DLO)
LDST | Logging Distribution Sample Time | 16#4018 = 16408 | 16#2086/9 | 16#B3/01/09 = 179/01/09 | LDST | Configuration and settings | R/W | WORD (Enumeration) | - | [1 second] 1S |  | [Log Distrib Spl Time] (LDST) | [Distributed logging] (DLO)
LFL1 | Response to 4-20mA loss on AI1 | 16#1B69 = 7017 | 16#2028/12 | 16#84/01/12 = 132/01/18 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI1 4-20mA loss] (LFL1) | [4-20 mA loss] (LFL)
LFL4 | Response to 4-20mA loss on AI4 | 16#1B66 = 7014 | 16#2028/F | 16#84/01/0F = 132/01/15 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI4 4-20mA loss] (LFL4) | [4-20 mA loss] (LFL)
LFL5 | Response to 4-20mA loss on AI5 | 16#1B6B = 7019 | 16#2028/14 | 16#84/01/14 = 132/01/20 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI5 4-20mA loss] (LFL5) | [4-20 mA loss] (LFL)
LOC | Ovld Threshold Detection | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 70 % ... 150 % | [Ovld Detection Thr.] (LOC) | [Settings] (SET) [Process overload] (OLD)
MD0 | Year, month and day of actual fault | 16#1C84 = 7300 | 16#202B/1 | 16#85/01/65 = 133/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD1 | Year, month and day of fault record x (1 is last) | 16#1C85 = 7301 | 16#202B/2 | 16#85/01/66 = 133/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD2 | Year, month and day of fault record x (1 is last) | 16#1C86 = 7302 | 16#202B/3 | 16#85/01/67 = 133/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD3 | Year, month and day of fault record x (1 is last) | 16#1C87 = 7303 | 16#202B/4 | 16#85/01/68 = 133/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD4 | Year, month and day of fault record x (1 is last) | 16#1C88 = 7304 | 16#202B/5 | 16#85/01/69 = 133/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD5 | Year, month and day of fault record x (1 is last) | 16#1C89 = 7305 | 16#202B/6 | 16#85/01/6A = 133/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD6 | Year, month and day of fault record x (1 is last) | 16#1C8A = 7306 | 16#202B/7 | 16#85/01/6B = 133/01/107 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD7 | Year, month and day of fault record x (1 is last) | 16#1C8B = 7307 | 16#202B/8 | 16#85/01/6C = 133/01/108 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD8 | Year, month and day of fault record x (1 is last) | 16#1C8C = 7308 | 16#202B/9 | 16#85/01/6D = 133/01/109 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD9 | Year, month and day of fault record x (1 is last) | 16#1C8D = 7309 | 16#202B/A | 16#85/01/6E = 133/01/110 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDA | Year, month and day of fault record x (1 is last) | 16#1E14 = 7700 | 16#202F/1 | 16#87/01/65 = 135/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDB | Year, month and day of fault record x (1 is last) | 16#1E15 = 7701 | 16#202F/2 | 16#87/01/66 = 135/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDC | Year, month and day of fault record x (1 is last) | 16#1E16 = 7702 | 16#202F/3 | 16#87/01/67 = 135/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDD | Year, month and day of fault record x (1 is last) | 16#1E17 = 7703 | 16#202F/4 | 16#87/01/68 = 135/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDE | Year, month and day of fault record x (1 is last) | 16#1E18 = 7704 | 16#202F/5 | 16#87/01/69 = 135/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDF | Year, month and day of fault record x (1 is last) | 16#1E19 = 7705 | 16#202F/6 | 16#87/01/6A = 135/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
ME0 | Motor energy consumption (Wh) | 16#2969 = 10601 | 16#204C/2 | 16#96/01/02 = 150/01/02 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Motor Consumption] (ME0) | [Mechanical Energy] (MEC)
ME1 | Motor energy consumption (kWh) | 16#296A = 10602 | 16#204C/3 | 16#96/01/03 = 150/01/03 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Motor Consumption] (ME1) | [Mechanical Energy] (MEC)
ME2 | Motor energy consumption (MWh) | 16#296B = 10603 | 16#204C/4 | 16#96/01/04 = 150/01/04 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Motor Consumption] (ME2) | [Mechanical Energy] (MEC)
ME3 | Motor energy consumption (GWh) | 16#296C = 10604 | 16#204C/5 | 16#96/01/05 = 150/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Motor Consumption] (ME3) | [Mechanical Energy] (MEC)
ME4 | Motor energy consumption (TWh) | 16#296D = 10605 | 16#204C/6 | 16#96/01/06 = 150/01/06 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Motor Consumption] (ME4) | [Mechanical Energy] (MEC)
MOEP | Peak Output Power | 16#2991 = 10641 | 16#204C/2A | 16#96/01/2A = 150/01/42 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Peak Output Power ] (MOEP) | [Elec Ener Output Counter] (ELO)
NFHP | No Flow High Power | 16#3E5B = 15963 | 16#2081/40 | 16#B0/01/A4 = 176/01/164 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [High Power] (NFHP) | [Dry run Monit] (DYR)
NFHS | No Flow High Speed | 16#3E5A = 15962 | 16#2081/3F | 16#B0/01/A3 = 176/01/163 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [High Speed] (NFHS) | [Dry run Monit] (DYR)
NFLP | No Flow Low Power | 16#3E59 = 15961 | 16#2081/3E | 16#B0/01/A2 = 176/01/162 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Low Power] (NFLP) | [Dry run Monit] (DYR)
NFLS | No Flow Low Speed | 16#3E58 = 15960 | 16#2081/3D | 16#B0/01/A1 = 176/01/161 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Low Speed] (NFLS) | [Dry run Monit] (DYR)
NSM | Number of motor starts | 16#0CBC = 3260 | 16#2002/3D | 16#71/01/3D = 113/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Nb Of Starts] (NSM) | [Diag. data] (DDT) [Counter Management] (ELT) [Variable Speed Pump] (MPP)
OC0 | Electrical energy consumed by the motor (Wh) | 16#296E = 10606 | 16#204C/7 | 16#96/01/07 = 150/01/07 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Elc Energy Cons] (OC0) | [kWh Counters] (KWC)
OC1 | Electrical energy consumed by the motor (KWh) | 16#296F = 10607 | 16#204C/8 | 16#96/01/08 = 150/01/08 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Elc Energy Cons] (OC1) | [kWh Counters] (KWC)
OC2 | Electrical energy consumed by the motor (MWh) | 16#2970 = 10608 | 16#204C/9 | 16#96/01/09 = 150/01/09 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Elc Energy Cons] (OC2) | [kWh Counters] (KWC)
OC3 | Electrical energy consumed by the motor (GWh) | 16#2971 = 10609 | 16#204C/A | 16#96/01/0A = 150/01/10 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Elc Energy Cons] (OC3) | [kWh Counters] (KWC)
OC4 | Electrical energy consumed by the motor (TWh) | 16#2972 = 10610 | 16#204C/B | 16#96/01/0B = 150/01/11 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Elc Energy Cons] (OC4) | [kWh Counters] (KWC)
OCA7 | Scan output 7 address | 16#3C43 = 15427 | 16#207C/1C | 16#AE/01/1C = 174/01/28 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA8 | Scan output 8 address | 16#3C44 = 15428 | 16#207C/1D | 16#AE/01/1D = 174/01/29 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA9 | Scan output 9 address | 16#3C45 = 15429 | 16#207C/1E | 16#AE/01/1E = 174/01/30 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAA | Scan output 10 address | 16#3C46 = 15430 | 16#207C/1F | 16#AE/01/1F = 174/01/31 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAB | Scan output 11 address | 16#3C47 = 15431 | 16#207C/20 | 16#AE/01/20 = 174/01/32 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAC | Scan output 12 address | 16#3C48 = 15432 | 16#207C/21 | 16#AE/01/21 = 174/01/33 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAD | Scan output 13 address | 16#3C49 = 15433 | 16#207C/22 | 16#AE/01/22 = 174/01/34 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAE | Scan output 14 address | 16#3C4A = 15434 | 16#207C/23 | 16#AE/01/23 = 174/01/35 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAF | Scan output 15 address | 16#3C4B = 15435 | 16#207C/24 | 16#AE/01/24 = 174/01/36 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAG | Scan output 16 address | 16#3C4C = 15436 | 16#207C/25 | 16#AE/01/25 = 174/01/37 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCT | Electrical energy consumed TODAY by the motor (KWh) | 16#297E = 10622 | 16#204C/17 | 16#96/01/17 = 150/01/23 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Today] (OCT) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO)
OCY | Electrical energy consumed YESTERDAY by the motor (KWh) | 16#2980 = 10624 | 16#204C/19 | 16#96/01/19 = 150/01/25 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Yesterday] (OCY) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO)
OE0 | Real energy consumption (Wh) | 16#2978 = 10616 | 16#204C/11 | 16#96/01/11 = 150/01/17 |  | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Consumption] (OE0) | [Elec Ener Output Counter] (ELO)
OE1 | Real energy consumption (kWh) | 16#2979 = 10617 | 16#204C/12 | 16#96/01/12 = 150/01/18 |  | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Consumption] (OE1) | [Elec Ener Output Counter] (ELO)
OE2 | Real energy consumption (MWh) | 16#297A = 10618 | 16#204C/13 | 16#96/01/13 = 150/01/19 |  | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Consumption] (OE2) | [Elec Ener Output Counter] (ELO)
OE3 | Real energy consumption (GWh) | 16#297B = 10619 | 16#204C/14 | 16#96/01/14 = 150/01/20 |  | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Consumption] (OE3) | [Elec Ener Output Counter] (ELO)
OE4 | Real energy consumption (TWh) | 16#297C = 10620 | 16#204C/15 | 16#96/01/15 = 150/01/21 |  | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Consumption] (OE4) | [Elec Ener Output Counter] (ELO)
OMA7 | Scan input 7 address | 16#3C2F = 15407 | 16#207C/8 | 16#AE/01/08 = 174/01/08 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA8 | Scan input 8 address | 16#3C30 = 15408 | 16#207C/9 | 16#AE/01/09 = 174/01/09 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA9 | Scan input 9 address | 16#3C31 = 15409 | 16#207C/A | 16#AE/01/0A = 174/01/10 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAA | Scan input 10 address | 16#3C32 = 15410 | 16#207C/B | 16#AE/01/0B = 174/01/11 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAB | Scan input 11 address | 16#3C33 = 15411 | 16#207C/C | 16#AE/01/0C = 174/01/12 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAC | Scan input 12 address | 16#3C34 = 15412 | 16#207C/D | 16#AE/01/0D = 174/01/13 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAD | Scan input 13 address | 16#3C35 = 15413 | 16#207C/E | 16#AE/01/0E = 174/01/14 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAE | Scan input 14 address | 16#3C36 = 15414 | 16#207C/F | 16#AE/01/0F = 174/01/15 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAF | Scan input 15 address | 16#3C37 = 15415 | 16#207C/10 | 16#AE/01/10 = 174/01/16 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAG | Scan input 16 address | 16#3C38 = 15416 | 16#207C/11 | 16#AE/01/11 = 174/01/17 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OP0 | Electrical energy produced by the motor (Wh) | 16#2973 = 10611 | 16#204C/C | 16#96/01/0C = 150/01/12 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh
OP1 | Electrical energy produced by the motor (KWh) | 16#2974 = 10612 | 16#204C/D | 16#96/01/0D = 150/01/13 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh
OP2 | Electrical energy produced by the motor (MWh) | 16#2975 = 10613 | 16#204C/E | 16#96/01/0E = 150/01/14 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh
OP3 | Electrical energy produced by the motor (GWh) | 16#2976 = 10614 | 16#204C/F | 16#96/01/0F = 150/01/15 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh
OP4 | Electrical energy produced by the motor (TWh) | 16#2977 = 10615 | 16#204C/10 | 16#96/01/10 = 150/01/16 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh
OPRW | Motor mechanical power estimation | 16#0CDC = 3292 | 16#2002/5D | 16#71/01/5D = 113/01/93 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Power Estim Value] (OPRW) | [Mechanical Energy] (MEC) [Dry run Monit] (DYR)
OTP9 | Motor torque | 16#1CAB = 7339 | 16#202B/28 | 16#85/01/8C = 133/01/140 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP9) | [None] (DP9)
OTPA | Motor torque | 16#1E32 = 7730 | 16#202F/1F | 16#87/01/83 = 135/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPA) | [None] (DPA)
OTPB | Motor torque | 16#1E33 = 7731 | 16#202F/20 | 16#87/01/84 = 135/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPB) | [None] (DPB)
OTPC | Motor torque | 16#1E34 = 7732 | 16#202F/21 | 16#87/01/85 = 135/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPC) | [None] (DPC)
OTPD | Motor torque | 16#1E35 = 7733 | 16#202F/22 | 16#87/01/86 = 135/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPD) | [None] (DPD)
OTPE | Motor torque | 16#1E36 = 7734 | 16#202F/23 | 16#87/01/87 = 135/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPE) | [None] (DPE)
OTPF | Motor torque | 16#1E37 = 7735 | 16#202F/24 | 16#87/01/88 = 135/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPF) | [None] (DPF)
PCA | Pump Curve Activation | 16#3D9B = 15771 | 16#207F/48 | 16#AF/01/AC = 175/01/172 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Pump Curve Activate] (PCA) | [Pump characteristics] (PCR)
PCAH | Over-consumption threshold | 16#2A62 = 10850 | 16#204E/33 | 16#97/01/33 = 151/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 200.0 % | [Over-Consumption Thd] (PCAH) | [Elec Ener Output Counter] (ELO)
PCAL | Under-consumption threshold | 16#2A63 = 10851 | 16#204E/34 | 16#97/01/34 = 151/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Under-Consumption Thd] (PCAL) | [Elec Ener Output Counter] (ELO)
PCAT | Over/Under-consumption time delay | 16#2A64 = 10852 | 16#204E/35 | 16#97/01/35 = 151/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 1 min | 0 min ... 60 min | [Over/Under-Cons Delay] (PCAT) | [Elec Ener Output Counter] (ELO)
PCBH | BEP Head | 16#3D97 = 15767 | 16#207F/44 | 16#AF/01/A8 = 175/01/168 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head BEP] (PCBH) | [Pump characteristics] (PCR)
PCBP | BEP Power | 16#3D99 = 15769 | 16#207F/46 | 16#AF/01/AA = 175/01/170 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power BEP] (PCBP) | [Pump characteristics] (PCR)
PCBQ | Flow at BEP | 16#3D98 = 15768 | 16#207F/45 | 16#AF/01/A9 = 175/01/169 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow at BEP] (PCBQ) | [Pump characteristics] (PCR)
PCH1 | Head entered at y (for HQ curve) | 16#3D8D = 15757 | 16#207F/3A | 16#AF/01/9E = 175/01/158 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 1] (PCH1) | [Pump characteristics] (PCR)
PCH2 | Head entered at y (for HQ curve) | 16#3D8E = 15758 | 16#207F/3B | 16#AF/01/9F = 175/01/159 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 2] (PCH2) | [Pump characteristics] (PCR)
PCH3 | Head entered at y (for HQ curve) | 16#3D8F = 15759 | 16#207F/3C | 16#AF/01/A0 = 175/01/160 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 3] (PCH3) | [Pump characteristics] (PCR)
PCH4 | Head entered at y (for HQ curve) | 16#3D90 = 15760 | 16#207F/3D | 16#AF/01/A1 = 175/01/161 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 4] (PCH4) | [Pump characteristics] (PCR)
PCH5 | Head entered at y (for HQ curve) | 16#3D91 = 15761 | 16#207F/3E | 16#AF/01/A2 = 175/01/162 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 5] (PCH5) | [Pump characteristics] (PCR)
PCM | Select which curve data are managed and will be entered on | 16#3D9A = 15770 | 16#207F/47 | 16#AF/01/AB = 175/01/171 | PCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disable pump characteristics] NO |  | [Mode] (PCM) | [Pump characteristics] (PCR)
PCP1 | Mechanical power entered at point y | 16#3D92 = 15762 | 16#207F/3F | 16#AF/01/A3 = 175/01/163 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 1] (PCP1) | [Pump characteristics] (PCR)
PCP2 | Mechanical power entered at point y | 16#3D93 = 15763 | 16#207F/40 | 16#AF/01/A4 = 175/01/164 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 2] (PCP2) | [Pump characteristics] (PCR)
PCP3 | Mechanical power entered at point y | 16#3D94 = 15764 | 16#207F/41 | 16#AF/01/A5 = 175/01/165 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 3] (PCP3) | [Pump characteristics] (PCR)
PCP4 | Mechanical power entered at point y | 16#3D95 = 15765 | 16#207F/42 | 16#AF/01/A6 = 175/01/166 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 4] (PCP4) | [Pump characteristics] (PCR)
PCP5 | Mechanical power entered at point y | 16#3D96 = 15766 | 16#207F/43 | 16#AF/01/A7 = 175/01/167 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 5] (PCP5) | [Pump characteristics] (PCR)
PCPB | Response to Pump cycle error | 16#3E1F = 15903 | 16#2081/4 | 16#B0/01/68 = 176/01/104 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [PumpCycleError Resp] (PCPB) | [Pumpcycle monitoring] (CSP)
PCPM | Pump cycle monitoring mode | 16#3E1C = 15900 | 16#2081/1 | 16#B0/01/65 = 176/01/101 | PCPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pump Cycle monitoring disabled] NO |  | [PumpCycle Monitor] (PCPM) | [Pumpcycle monitoring] (CSP)
PCPN | Pump cycle maximum allowed starts | 16#3E1D = 15901 | 16#2081/2 | 16#B0/01/66 = 176/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 6 | 1 ... 99 | [PumpCycle MaxStarts] (PCPN) | [Pumpcycle monitoring] (CSP)
PCPT | Pump cycle timeframe | 16#3E1E = 15902 | 16#2081/3 | 16#B0/01/67 = 176/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 60 min | 0 min ... 3600 min | [PumpCycle timeframe] (PCPT) | [Pumpcycle monitoring] (CSP)
PCQ1 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D88 = 15752 | 16#207F/35 | 16#AF/01/99 = 175/01/153 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 1] (PCQ1) | [Pump characteristics] (PCR)
PCQ2 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D89 = 15753 | 16#207F/36 | 16#AF/01/9A = 175/01/154 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 2] (PCQ2) | [Pump characteristics] (PCR)
PCQ3 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8A = 15754 | 16#207F/37 | 16#AF/01/9B = 175/01/155 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 3] (PCQ3) | [Pump characteristics] (PCR)
PCQ4 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8B = 15755 | 16#207F/38 | 16#AF/01/9C = 175/01/156 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 4] (PCQ4) | [Pump characteristics] (PCR)
PCQ5 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8C = 15756 | 16#207F/39 | 16#AF/01/9D = 175/01/157 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 5] (PCQ5) | [Pump characteristics] (PCR)
PCS | Pump Characteristics Status | 16#3D86 = 15750 | 16#207F/33 | 16#AF/01/97 = 175/01/151 | PCS | Status parameters | R | WORD (Enumeration) | - |  |  | [Status] (PCS) | [Pump characteristics] (PCR)
PCSP | Pump speed for which curves are entered | 16#3D87 = 15751 | 16#207F/34 | 16#AF/01/98 = 175/01/152 |  | Configuration and settings | R/WS | INT (Signed16) | 1 rpm | 0 rpm | 0 rpm ... 32767 rpm | [Pump Speed] (PCSP) | [Pump characteristics] (PCR)
PEG | Power Dynamic Gain | 16#3E85 = 16005 | 16#2082/6 | 16#B1/01/06 = 177/01/06 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Power Dynamic Gain] (PEG) | [Flow estimation] (SFE)
PEO | Power Static Offset | 16#3E86 = 16006 | 16#2082/7 | 16#B1/01/07 = 177/01/07 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Power Static Offset] (PEO) | [Flow estimation] (SFE)
PEV1 | TPDO1 Event mask | 16#17B6 = 6070 | 16#201E/47 | 16#7F/01/47 = 127/01/71 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV2 | TPDO2 Event mask | 16#17B7 = 6071 | 16#201E/48 | 16#7F/01/48 = 127/01/72 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV3 | TPDO3 Event mask | 16#17B8 = 6072 | 16#201E/49 | 16#7F/01/49 = 127/01/73 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV4 | TPDO4 Event mask | 16#17B9 = 6073 | 16#201E/4A | 16#7F/01/4A = 127/01/74 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PFC7 | DI7 Frequency measured | 16#343A = 13370 | 16#2067/47 | 16#A3/01/AB = 163/01/171 |  | Actual values parameters | R | UINT (Unsigned32) | 0.01 Hz |  | 0.00 Hz ... 42949672.95 Hz
PFC8 | DI8 Frequency measured | 16#344E = 13390 | 16#2067/5B | 16#A3/01/BF = 163/01/191 |  | Actual values parameters | R | UINT (Unsigned32) | 0.01 Hz |  | 0.00 Hz ... 42949672.95 Hz
PFI7 | DI7 Frequency filter | 16#3434 = 13364 | 16#2067/41 | 16#A3/01/A5 = 163/01/165 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI7 Frequency Filter] (PFI7) | [DI7 Frequency measured] (PFC7) [DI7 Pulse Config] (PAI7)
PFI8 | DI8 Frequency filter | 16#3448 = 13384 | 16#2067/55 | 16#A3/01/B9 = 163/01/185 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI8 Frequency Filter] (PFI8) | [DI8 Frequency measured] (PFC8) [DI8 Pulse Config] (PAI8)
PFL | U/F Profile | 16#2598 = 9624 | 16#2042/19 | 16#91/01/19 = 145/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 30 % | 0 % ... 100 % | [U/F Profile] (PFL) | [Motor control] (DRC)
PFMB | PID Feedback error response | 16#2E9D = 11933 | 16#2059/22 | 16#9C/01/86 = 156/01/134 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [PID Fdbk Error Resp] (PFMB) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM)
PFMD | PID Feedback error delay | 16#2E9C = 11932 | 16#2059/21 | 16#9C/01/85 = 156/01/133 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PID Fdbk Error Delay] (PFMD) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Settings] (SET)
PFMM | PID Feedback monitoring activation | 16#2E9A = 11930 | 16#2059/1F | 16#9C/01/83 = 156/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Fdbk Monitoring] (PFMM) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM)
PFMR | PID Feedback Range | 16#2E9B = 11931 | 16#2059/20 | 16#9C/01/84 = 156/01/132 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 3 % | 0 % ... 100 % | [PID Fdbk Range] (PFMR) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Settings] (SET)
PHR | Output phase rotation | 16#3459 = 13401 | 16#2068/2 | 16#A4/01/02 = 164/01/02 | PHR | Configuration and settings | R/WS | WORD (Enumeration) | - | [A - B - C phase rotation] ABC |  | [Output Ph Rotation] (PHR) | [Motor control] (DRC)
PIH7 | DI7 PulseInput High Frequency | 16#3432 = 13362 | 16#2067/3F | 16#A3/01/A3 = 163/01/163 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI7 PulseInput High Freq] (PIH7) | [DI7 Frequency measured] (PFC7) [DI7 Pulse Config] (PAI7)
PIH8 | DI8 PulseInput High Frequency | 16#3446 = 13382 | 16#2067/53 | 16#A3/01/B7 = 163/01/183 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI8 PulseInput High Freq] (PIH8) | [DI8 Frequency measured] (PFC8) [DI8 Pulse Config] (PAI8)
PIL7 | DI7 PulseInput Low Frequency | 16#3430 = 13360 | 16#2067/3D | 16#A3/01/A1 = 163/01/161 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.01 Hz | 0.00 Hz | 0.00 Hz ... 30000.00 Hz | [DI7 PulseInput Low Freq] (PIL7) | [DI7 Frequency measured] (PFC7) [DI7 Pulse Config] (PAI7)
PIL8 | DI8 PulseInput Low Frequency | 16#3444 = 13380 | 16#2067/51 | 16#A3/01/B5 = 163/01/181 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.01 Hz | 0.00 Hz | 0.00 Hz ... 30000.00 Hz | [DI8 PulseInput Low Freq] (PIL8) | [DI8 Frequency measured] (PFC8) [DI8 Pulse Config] (PAI8)
R3 | R3 Assignment | 16#138B = 5003 | 16#2014/4 | 16#7A/01/04 = 122/01/04 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R3 Assignment] (R3) | [R3 configuration] (R3)
R3D | R3 Delay time | 16#1093 = 4243 | 16#200C/2C | 16#76/01/2C = 118/01/44 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R3 Delay time] (R3D) | [R3 configuration] (R3)
R3H | R3 Holding time | 16#107F = 4223 | 16#200C/18 | 16#76/01/18 = 118/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R3 Holding time] (R3H) | [R3 configuration] (R3)
R3S | R3 Active level | 16#106B = 4203 | 16#200C/4 | 16#76/01/04 = 118/01/04 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R3 Active at] (R3S) | [R3 configuration] (R3)
R4 | R4 Assignment | 16#138C = 5004 | 16#2014/5 | 16#7A/01/05 = 122/01/05 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R4 Assignment] (R4) | [R4 configuration] (R4)
R4D | R4 Delay time | 16#1094 = 4244 | 16#200C/2D | 16#76/01/2D = 118/01/45 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R4 Delay time] (R4D) | [R4 configuration] (R4)
R4H | R4 Holding time | 16#1080 = 4224 | 16#200C/19 | 16#76/01/19 = 118/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R4 Holding time] (R4H) | [R4 configuration] (R4)
R4S | R4 Active level | 16#106C = 4204 | 16#200C/5 | 16#76/01/05 = 118/01/05 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R4 Active at] (R4S) | [R4 configuration] (R4)
R5 | R5 Assignment | 16#138D = 5005 | 16#2014/6 | 16#7A/01/06 = 122/01/06 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R5 Assignment] (R5) | [R5 configuration] (R5)
R5D | R5 Delay time | 16#1095 = 4245 | 16#200C/2E | 16#76/01/2E = 118/01/46 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R5 Delay time] (R5D) | [R5 configuration] (R5)
R5H | R5 Holding time | 16#1081 = 4225 | 16#200C/1A | 16#76/01/1A = 118/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R5 Holding time] (R5H) | [R5 configuration] (R5)
R5S | R5 Active at | 16#106D = 4205 | 16#200C/6 | 16#76/01/06 = 118/01/06 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R5 Active at ] (R5S) | [R5 configuration] (R5)
R6 | R6 assignment | 16#138E = 5006 | 16#2014/7 | 16#7A/01/07 = 122/01/07 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R6 Assignment] (R6) | [R6 configuration] (R6)
R6D | R6 activation delay time | 16#1096 = 4246 | 16#200C/2F | 16#76/01/2F = 118/01/47 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R6 activ delay time] (R6D) | [R6 configuration] (R6)
R6H | R6 holding delay time | 16#1082 = 4226 | 16#200C/1B | 16#76/01/1B = 118/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R6 hold delay time] (R6H) | [R6 configuration] (R6)
R6S | R6 status (output active level) | 16#106E = 4206 | 16#200C/7 | 16#76/01/07 = 118/01/07 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R6 status] (R6S) | [R6 configuration] (R6)
RFP9 | Motor frequency | 16#1C5B = 7259 | 16#202A/3C | 16#85/01/3C = 133/01/60 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFP9) | [None] (DP9)
RFPA | Motor frequency | 16#1DE2 = 7650 | 16#202E/33 | 16#87/01/33 = 135/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPA) | [None] (DPA)
RFPB | Motor frequency | 16#1DE3 = 7651 | 16#202E/34 | 16#87/01/34 = 135/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPB) | [None] (DPB)
RFPC | Motor frequency | 16#1DE4 = 7652 | 16#202E/35 | 16#87/01/35 = 135/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPC) | [None] (DPC)
RFPD | Motor frequency | 16#1DE5 = 7653 | 16#202E/36 | 16#87/01/36 = 135/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPD) | [None] (DPD)
RFPE | Motor frequency | 16#1DE6 = 7654 | 16#202E/37 | 16#87/01/37 = 135/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPE) | [None] (DPE)
RFPF | Motor frequency | 16#1DE7 = 7655 | 16#202E/38 | 16#87/01/38 = 135/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPF) | [None] (DPF)
RHO | Density | 16#3E82 = 16002 | 16#2082/3 | 16#B1/01/03 = 177/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 kg/m³ | 1000 kg/m³ | 100 kg/m³ ... 10000 kg/m³ | [Liquid Density] (RHO) | [Define system units] (SUC)
RTD | Reference high threshold | 16#2B05 = 11013 | 16#2050/E | 16#98/01/0E = 152/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Reference high Thd] (RTD) | [Threshold reached] (THRE) [Settings] (SET)
RTDL | Reference low threshold | 16#2B06 = 11014 | 16#2050/F | 16#98/01/0F = 152/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [Reference low Thd] (RTDL) | [Threshold reached] (THRE) [Settings] (SET)
RTP9 | Run Elapsed time | 16#1C65 = 7269 | 16#202A/46 | 16#85/01/46 = 133/01/70 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP9) | [None] (DP9)
RTPA | Run Elapsed time | 16#1DEC = 7660 | 16#202E/3D | 16#87/01/3D = 135/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPA) | [None] (DPA)
RTPB | Run Elapsed time | 16#1DED = 7661 | 16#202E/3E | 16#87/01/3E = 135/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPB) | [None] (DPB)
RTPC | Run Elapsed time | 16#1DEE = 7662 | 16#202E/3F | 16#87/01/3F = 135/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPC) | [None] (DPC)
RTPD | Run Elapsed time | 16#1DEF = 7663 | 16#202E/40 | 16#87/01/40 = 135/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPD) | [None] (DPD)
RTPE | Run Elapsed time | 16#1DF0 = 7664 | 16#202E/41 | 16#87/01/41 = 135/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPE) | [None] (DPE)
RTPF | Run Elapsed time | 16#1DF1 = 7665 | 16#202E/42 | 16#87/01/42 = 135/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPF) | [None] (DPF)
SAI4 | AI4 customer image (1mV, 0.001mA) without filter | 16#14AE = 5294 | 16#2016/5F | 16#7B/01/5F = 123/01/95 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI5 | AI5 customer image (1mV, 0.001mA) without filter | 16#14B2 = 5298 | 16#2016/63 | 16#7B/01/63 = 123/01/99 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO2 | AO2 customer image (1mV, 0.001mA) without filter | 16#14B0 = 5296 | 16#2016/61 | 16#7B/01/61 = 123/01/97 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SFS | PID start ref frequency | 16#2EB3 = 11955 | 16#2059/38 | 16#9C/01/9C = 156/01/156 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 300.0 Hz | [PID Start Ref Freq] (SFS) | [Settings] (ST) [Settings] (ST) [Settings] (SET)
SLBS | Sleep Boost Speed | 16#2DEC = 11756 | 16#2057/39 | 16#9B/01/9D = 155/01/157 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Boost Speed] (SLBS) | [Boost] (SBT) [Settings] (SET)
SLBT | Sleep Boost Time | 16#2DED = 11757 | 16#2057/3A | 16#9B/01/9E = 155/01/158 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [Sleep Boost Time] (SLBT) | [Boost] (SBT) [Settings] (SET)
SLE | Sleep Offset Threshold | 16#2DB6 = 11702 | 16#2057/3 | 16#9B/01/67 = 155/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 1.0 Hz ... 1000.0 Hz | [Sleep Offset Thres.] (SLE) | [Settings] (SET) [Stop after speed timeout] (PRSP)
SLFV | Estimated Pump flow value | 16#3E87 = 16007 | 16#2082/8 | 16#B1/01/08 = 177/01/08 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Est. Pump Flow] (SLFV) | [Variable Speed Pump] (MPP) [Flow estimation] (SFE)
SLHV | Estimated Pump head value | 16#3E8C = 16012 | 16#2082/D | 16#B1/01/0D = 177/01/13 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Est. Pump Head] (SLHV) | [Variable Speed Pump] (MPP)
SLPD | Sleep Delay | 16#2DEB = 11755 | 16#2057/38 | 16#9B/01/9C = 155/01/156 |  | Actual values parameters | R/W | INT (Signed16) | 1 s | 20 s | 0 s ... 3600 s | [Sleep Delay] (SLPD) | [Sleep menu] (SLP) [Settings] (SET)
SLPM | Sleep Detection Mode | 16#2DE6 = 11750 | 16#2057/33 | 16#9B/01/97 = 155/01/151 | SLPM | Actual values parameters | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sleep Detect Mode] (SLPM) | [Sleep menu] (SLP)
SLPR | Sleep Power Level | 16#2DEA = 11754 | 16#2057/37 | 16#9B/01/9B = 155/01/155 |  | Actual values parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Sleep Power Level] (SLPR) | [Sleep menu] (SLP) [Settings] (SET)
SLPW | Sleep Switch Assignment | 16#2DE7 = 11751 | 16#2057/34 | 16#9B/01/98 = 155/01/152 | PSLIN | Actual values parameters | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Sleep Switch Assign] (SLPW) | [Sleep menu] (SLP)
SLSL | Sleep Minimum Speed Level | 16#2DE9 = 11753 | 16#2057/36 | 16#9B/01/9A = 155/01/154 |  | Actual values parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Min Speed] (SLSL) | [Sleep menu] (SLP) [Settings] (SET)
SPD | Motor speed | 16#2EE4 = 12004 | 16#205A/5 | 16#9D/01/05 = 157/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Speed] (SPD) | [System] (DST) [Motor parameters] (MMO)
ST00 | Status registers 0 | 16#3EE4 = 16100 | 16#2083/1 | 16#B1/01/65 = 177/01/101 |  | Status parameters | R | WORD (BitString16) | -
ST02 | Status registers 2 | 16#3EE6 = 16102 | 16#2083/3 | 16#B1/01/67 = 177/01/103 |  | Status parameters | R | WORD (BitString16) | -
ST03 | Status registers 3 | 16#3EE7 = 16103 | 16#2083/4 | 16#B1/01/68 = 177/01/104 |  | Status parameters | R | WORD (BitString16) | -
ST04 | Status registers 4 | 16#3EE8 = 16104 | 16#2083/5 | 16#B1/01/69 = 177/01/105 |  | Status parameters | R | WORD (BitString16) | -
ST05 | Status registers 5 | 16#3EE9 = 16105 | 16#2083/6 | 16#B1/01/6A = 177/01/106 |  | Status parameters | R | WORD (BitString16) | -
ST06 | Status registers 6 | 16#3EEA = 16106 | 16#2083/7 | 16#B1/01/6B = 177/01/107 |  | Status parameters | R | WORD (BitString16) | -
ST07 | Status registers 7 | 16#3EEB = 16107 | 16#2083/8 | 16#B1/01/6C = 177/01/108 |  | Status parameters | R | WORD (BitString16) | -
ST08 | Status registers 8 | 16#3EEC = 16108 | 16#2083/9 | 16#B1/01/6D = 177/01/109 |  | Status parameters | R | WORD (BitString16) | -
ST09 | Status registers 9 | 16#3EED = 16109 | 16#2083/A | 16#B1/01/6E = 177/01/110 |  | Status parameters | R | WORD (BitString16) | -
ST11 | Status registers 11 | 16#3EEF = 16111 | 16#2083/C | 16#B1/01/70 = 177/01/112 |  | Status parameters | R | WORD (BitString16) | -
ST12 | Status registers 12 | 16#3EF0 = 16112 | 16#2083/D | 16#B1/01/71 = 177/01/113 |  | Status parameters | R | WORD (BitString16) | -
ST13 | Status registers 13 | 16#3EF1 = 16113 | 16#2083/E | 16#B1/01/72 = 177/01/114 |  | Status parameters | R | WORD (BitString16) | -
ST14 | Status registers 14 | 16#3EF2 = 16114 | 16#2083/F | 16#B1/01/73 = 177/01/115 |  | Status parameters | R | WORD (BitString16) | -
ST15 | Status registers 15 | 16#3EF3 = 16115 | 16#2083/10 | 16#B1/01/74 = 177/01/116 |  | Status parameters | R | WORD (BitString16) | -
ST16 | Status registers 16 | 16#3EF4 = 16116 | 16#2083/11 | 16#B1/01/75 = 177/01/117 |  | Status parameters | R | WORD (BitString16) | -
ST17 | Status registers 17 | 16#3EF5 = 16117 | 16#2083/12 | 16#B1/01/76 = 177/01/118 |  | Status parameters | R | WORD (BitString16) | -
ST18 | Status registers 18 | 16#3EF6 = 16118 | 16#2083/13 | 16#B1/01/77 = 177/01/119 |  | Status parameters | R | WORD (BitString16) | -
ST19 | Status registers 19 | 16#3EF7 = 16119 | 16#2083/14 | 16#B1/01/78 = 177/01/120 |  | Status parameters | R | WORD (BitString16) | -
ST20 | Status registers 20 | 16#3EF8 = 16120 | 16#2083/15 | 16#B1/01/79 = 177/01/121 |  | Status parameters | R | WORD (BitString16) | -
ST22 | Status registers 22 | 16#3EFA = 16122 | 16#2083/17 | 16#B1/01/7B = 177/01/123 |  | Status parameters | R | WORD (BitString16) | -
ST23 | Status registers 23 | 16#3EFB = 16123 | 16#2083/18 | 16#B1/01/7C = 177/01/124 |  | Status parameters | R | WORD (BitString16) | -
ST24 | Status registers 24 | 16#3EFC = 16124 | 16#2083/19 | 16#B1/01/7D = 177/01/125 |  | Status parameters | R | WORD (BitString16) | -
STP1 | Motor stall max time | 16#2437 = 9271 | 16#203E/48 | 16#8F/01/48 = 143/01/72 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 200.0 s | [Stall Max Time] (STP1) | [Settings] (SET) [Stall monitoring] (STPR)
STP2 | Stall monitoring current level | 16#2438 = 9272 | 16#203E/49 | 16#8F/01/49 = 143/01/73 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 150.0 % | 0.0 % ... 150.0 % | [Stall Current] (STP2) | [Settings] (SET) [Stall monitoring] (STPR)
STP3 | Stall monitoring frequency level | 16#2439 = 9273 | 16#203E/4A | 16#8F/01/4A = 143/01/74 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 2.0 Hz | 0.0 Hz ... 300.0 Hz | [Stall Frequency] (STP3) | [Settings] (SET) [Stall monitoring] (STPR)
STPC | Stall monitoring activation | 16#2436 = 9270 | 16#203E/47 | 16#8F/01/47 = 143/01/71 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Stall Monitoring] (STPC) | [Stall monitoring] (STPR)
SUCU | Application Currency Unit | 16#2EF9 = 12025 | 16#205A/1A | 16#9D/01/1A = 157/01/26 | SUCU | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Currency unit list] (SUCU) | [Define system units] (SUC)
SUFR | Application Flow Rate Unit (used as default) | 16#2EF6 = 12022 | 16#205A/17 | 16#9D/01/17 = 157/01/23 | SUFR | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Flow rate unit] (SUFR) | [Define system units] (SUC)
SUPR | Application Pressure Unit (used as default) | 16#2EF5 = 12021 | 16#205A/16 | 16#9D/01/16 = 157/01/22 | SUPR | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [P sensor unit] (SUPR) | [Define system units] (SUC)
SUTP | Application Temperature Unit (used as default) | 16#2EF8 = 12024 | 16#205A/19 | 16#9D/01/19 = 157/01/25 | SUTP | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Temperature unit] (SUTP) | [Define system units] (SUC)
TBR2 | HMI baud rate | 16#1787 = 6023 | 16#201E/18 | 16#7F/01/18 = 127/01/24 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [HMI baud rate] (TBR2) | [Modbus HMI] (MD2)
TFO2 | HMI format | 16#1788 = 6024 | 16#201E/19 | 16#7F/01/19 = 127/01/25 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [HMI format] (TFO2) | [Modbus HMI] (MD2)
TH1A | Thermal warning level for AI1 | 16#33A3 = 13219 | 16#2066/14 | 16#A3/01/14 = 163/01/20 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI1 Th Warn Level] (TH1A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH1B | Response to thermal error for AI1 | 16#33B7 = 13239 | 16#2066/28 | 16#A3/01/28 = 163/01/40 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI1 Th Error Resp] (TH1B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3A | Thermal warning level for AI3 | 16#33A5 = 13221 | 16#2066/16 | 16#A3/01/16 = 163/01/22 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI3 Th Warn Level] (TH3A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH1F | Thermal error level for AI1 | 16#33AD = 13229 | 16#2066/1E | 16#A3/01/1E = 163/01/30 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI1 Th Error Level] (TH1F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH3B | Response to thermal error for AI3 | 16#33B9 = 13241 | 16#2066/2A | 16#A3/01/2A = 163/01/42 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI3 Th Error Resp] (TH3B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH1S | Activation of the thermal monitoring on AI1 | 16#3399 = 13209 | 16#2066/A | 16#A3/01/0A = 163/01/10 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI1 Th Monitoring] (TH1S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3F | Thermal error level for AI3 | 16#33AF = 13231 | 16#2066/20 | 16#A3/01/20 = 163/01/32 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI3 Th Error Level] (TH3F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH1V | AI1 thermal value | 16#33C1 = 13249 | 16#2066/32 | 16#A3/01/32 = 163/01/50 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI1 Th Value] (TH1V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3S | Activation of the thermal monitoring on AI3 | 16#339B = 13211 | 16#2066/C | 16#A3/01/0C = 163/01/12 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI3 Th Monitoring] (TH3S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3V | AI3 thermal value | 16#33C3 = 13251 | 16#2066/34 | 16#A3/01/34 = 163/01/52 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI3 Th Value] (TH3V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4A | Thermal warning level for AI4 | 16#33A6 = 13222 | 16#2066/17 | 16#A3/01/17 = 163/01/23 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI4 Th Warn Level] (TH4A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH4B | Response to thermal error for AI4 | 16#33BA = 13242 | 16#2066/2B | 16#A3/01/2B = 163/01/43 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI4 Th Error Resp] (TH4B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4F | Thermal error level for AI4 | 16#33B0 = 13232 | 16#2066/21 | 16#A3/01/21 = 163/01/33 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI4 Th Error Level] (TH4F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH4S | Activation of the thermal monitoring on AI4 | 16#339C = 13212 | 16#2066/D | 16#A3/01/0D = 163/01/13 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI4 Th Monitoring] (TH4S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4V | AI4 thermal value | 16#33C4 = 13252 | 16#2066/35 | 16#A3/01/35 = 163/01/53 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI4 Th Value] (TH4V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5A | Thermal warning level for AI5 | 16#33A7 = 13223 | 16#2066/18 | 16#A3/01/18 = 163/01/24 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI5 Th Warn Level] (TH5A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH5B | Response to thermal error for AI5 | 16#33BB = 13243 | 16#2066/2C | 16#A3/01/2C = 163/01/44 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI5 Th Error Resp] (TH5B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5F | Thermal error level for AI5 | 16#33B1 = 13233 | 16#2066/22 | 16#A3/01/22 = 163/01/34 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI5 Th Error Level] (TH5F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH5S | Activation of the thermal monitoring on AI5 | 16#339D = 13213 | 16#2066/E | 16#A3/01/0E = 163/01/14 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI5 Th Monitoring] (TH5S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5V | AI5 thermal value | 16#33C5 = 13253 | 16#2066/36 | 16#A3/01/36 = 163/01/54 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI5 Th Value] (TH5V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THP9 | Motor thermal state | 16#1C79 = 7289 | 16#202A/5A | 16#85/01/5A = 133/01/90 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP9) | [None] (DP9)
THPA | Motor thermal state | 16#1E00 = 7680 | 16#202E/51 | 16#87/01/51 = 135/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPA) | [None] (DPA)
THPB | Motor thermal state | 16#1E01 = 7681 | 16#202E/52 | 16#87/01/52 = 135/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPB) | [None] (DPB)
THPC | Motor thermal state | 16#1E02 = 7682 | 16#202E/53 | 16#87/01/53 = 135/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPC) | [None] (DPC)
THPD | Motor thermal state | 16#1E03 = 7683 | 16#202E/54 | 16#87/01/54 = 135/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPD) | [None] (DPD)
THPE | Motor thermal state | 16#1E04 = 7684 | 16#202E/55 | 16#87/01/55 = 135/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPE) | [None] (DPE)
THPF | Motor thermal state | 16#1E05 = 7685 | 16#202E/56 | 16#87/01/56 = 135/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPF) | [None] (DPF)
TOCT | Type of control | 16#2E8F = 11919 | 16#2059/14 | 16#9C/01/78 = 156/01/120 | TOCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [NA] NA |  | [Type of control] (TOCT) | [PID Feedback] (FDB) [PID Feedback] (FDB)
TQB | Pulse without Run delay | 16#3910 = 14608 | 16#2074/9 | 16#AA/01/09 = 170/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 10.0 s | [Pulse wo Run delay] (TQB) | [Frequency meter] (FQF)
TTOB | Ethernet embedded : Time-out | 16#FB9F = 64415 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s
UIH3 | AI3 voltage scaling parameter of 100% | 16#1148 = 4424 | 16#200E/19 | 16#77/01/19 = 119/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI3 Max Value] (UIH3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
UIH4 | AI4 voltage scaling parameter of 100% | 16#1149 = 4425 | 16#200E/1A | 16#77/01/1A = 119/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI4 Max Value] (UIH4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
UIH5 | AI5 voltage scaling parameter of 100% | 16#114A = 4426 | 16#200E/1B | 16#77/01/1B = 119/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI5 Max Value] (UIH5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
UIL3 | AI3 voltage scaling parameter of 0% | 16#113E = 4414 | 16#200E/F | 16#77/01/0F = 119/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI3 Min. Value] (UIL3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [Speed Ref AI3 Config.] (MSR3) [Torque Ref AI3 Config.] (MTR3) [AI3 configuration] (AI3)
UIL4 | AI4 voltage scaling parameter of 0% | 16#113F = 4415 | 16#200E/10 | 16#77/01/10 = 119/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI4 Min. Value] (UIL4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [Speed Ref AI4 Config.] (MSR4) [Torque Ref AI4 Config.] (MTR4) [AI4 configuration] (AI4)
UIL5 | AI5 voltage scaling parameter of 0% | 16#1140 = 4416 | 16#200E/11 | 16#77/01/11 = 119/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI5 Min. Value] (UIL5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [Speed Ref AI5 Config.] (MSR5) [Torque Ref AI5 Config.] (MTR5) [AI5 configuration] (AI5)
ULP9 | Mains voltage | 16#1C6F = 7279 | 16#202A/50 | 16#85/01/50 = 133/01/80 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULP9) | [None] (DP9)
ULPA | Mains voltage | 16#1DF6 = 7670 | 16#202E/47 | 16#87/01/47 = 135/01/71 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULPA) | [None] (DPA)
ULPB | Mains voltage | 16#1DF7 = 7671 | 16#202E/48 | 16#87/01/48 = 135/01/72 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULPB) | [None] (DPB)
ULPC | Mains voltage | 16#1DF8 = 7672 | 16#202E/49 | 16#87/01/49 = 135/01/73 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULPC) | [None] (DPC)
ULPD | Mains voltage | 16#1DF9 = 7673 | 16#202E/4A | 16#87/01/4A = 135/01/74 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULPD) | [None] (DPD)
ULPE | Mains voltage | 16#1DFA = 7674 | 16#202E/4B | 16#87/01/4B = 135/01/75 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULPE) | [None] (DPE)
ULPF | Mains voltage | 16#1DFB = 7675 | 16#202E/4C | 16#87/01/4C = 135/01/76 |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains voltage] (ULPF) | [None] (DPF)
UOH2 | AQ2 maximum output | 16#1218 = 4632 | 16#2010/21 | 16#78/01/21 = 120/01/33 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ2 max Output] (UOH2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
UOL2 | AQ2 minimum output | 16#120E = 4622 | 16#2010/17 | 16#78/01/17 = 120/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ2 min Output] (UOL2) | [AQ2] (AO2C) [Speed Ref AQ2 Config.] (MSM2) [Torque Ref AQ2 Config.] (MTM2) [AQ2 configuration] (AO2)
VBUS | DC bus voltage | 16#0CAB = 3243 | 16#2002/2C | 16#71/01/2C = 113/01/44 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [DC bus voltage] (VBUS) | [Drive parameters] (MPI)
VCB | Catch on fly sensitivity | 16#0C27 = 3111 | 16#2001/C | 16#70/01/70 = 112/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 V | Refer to programming manual | 0.01 V ... 100.00 V | [Catch on Fly Sensitivity] (VCB) | [Catch on the fly] (FLR)
WUPE | Wake UP Process Error level | 16#2DF0 = 11760 | 16#2057/3D | 16#9B/01/A1 = 155/01/161 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Process Error] (WUPE) | [Wake up menu] (WKP) [Settings] (SET)
WUPF | Wake Up Process level | 16#2DEF = 11759 | 16#2057/3C | 16#9B/01/A0 = 155/01/160 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Process level] (WUPF) | [Wake up menu] (WKP) [Settings] (SET)
WUPM | Wake Up Mode | 16#2DEE = 11758 | 16#2057/3B | 16#9B/01/9F = 155/01/159 | WUPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Feedback] FBK |  | [Wake Up Mode] (WUPM) | [Wake up menu] (WKP)
PREF | Reference Power without drive | 16#2A30 = 10800 | 16#204E/1 | 16#97/01/01 = 151/01/01 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Reference Power] (PREF) | [Energy Saving] (ESA)
EPR | Active Electrical output power estimation | 16#0CE1 = 3297 | 16#2002/62 | 16#71/01/62 = 113/01/98 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -300 % ... 300 %
SPDM | Motor Mechanical speed | 16#2EEB = 12011 | 16#205A/C | 16#9D/01/0C = 157/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Mechanical speed] (SPDM) | [Variable Speed Pump] (MPP)
DRC9 | Channel for reference frequency | 16#FB3F = 64319 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC9) | [None] (DP9)
DRCA | Channel for reference frequency | 16#FB40 = 64320 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCA) | [None] (DPA)
DRCB | Channel for reference frequency | 16#FB41 = 64321 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCB) | [None] (DPB)
DRCC | Channel for reference frequency | 16#FB42 = 64322 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCC) | [None] (DPC)
DRCD | Channel for reference frequency | 16#FB43 = 64323 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCD) | [None] (DPD)
DRCE | Channel for reference frequency | 16#FB44 = 64324 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCE) | [None] (DPE)
DRCF | Channel for reference frequency | 16#FB45 = 64325 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCF) | [None] (DPF)
DCC9 | Command channel | 16#FB4A = 64330 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC9) | [None] (DP9)
DCCA | Command channel | 16#FB4B = 64331 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCA) | [None] (DPA)
DCCB | Command channel | 16#FB4C = 64332 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCB) | [None] (DPB)
DCCZ | Command channel | 16#FB4D = 64333 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCZ) | [None] (DPC)
DCCD | Command channel | 16#FB4E = 64334 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCD) | [None] (DPD)
DCCE | Command channel | 16#FB4F = 64335 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCE) | [None] (DPE)
DCCF | Command channel | 16#FB50 = 64336 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCF) | [None] (DPF)
ILCI | Cabinet Input physical state | 16#1453 = 5203 | 16#2016/4 | 16#7B/01/04 = 123/01/04 |  | I/O parameters | R | WORD (BitString16) | -
ILCR | Cabinet IO : Logic inputs real image (bit0 = DI50 ...) | 16#1454 = 5204 | 16#2016/5 | 16#7B/01/05 = 123/01/05 |  | I/O parameters | R | WORD (BitString16) | -
ILC2 | Cabinet fixed logic input state | 16#1455 = 5205 | 16#2016/6 | 16#7B/01/06 = 123/01/06 |  | I/O parameters | R | WORD (BitString16) | - |  |  | [Cab Fix Logic Input] (ILC2) | [I/O Map] (IOM) [Bypass Drive Data] (IOCP)
ILC3 | Drive Bypass Logic Input | 16#1456 = 5206 | 16#2016/7 | 16#7B/01/07 = 123/01/07 |  | I/O parameters | R | WORD (BitString16) | - |  |  | [Drive Bypass Logic Input] (ILC3) | [I/O Map] (IOM) [Bypass Drive Data] (IOCP)
OLCI | Cabinet Ouput physical state | 16#145D = 5213 | 16#2016/E | 16#7B/01/0E = 123/01/14 |  | I/O parameters | R | WORD (BitString16) | -
OLCR | Cabinet IO : Logic outputs real image (bit0 = R60 ...) | 16#145E = 5214 | 16#2016/F | 16#7B/01/0F = 123/01/15 |  | I/O parameters | R/W | WORD (BitString16) | -
OLC2 | Cabinet fixed logic output state | 16#145F = 5215 | 16#2016/10 | 16#7B/01/10 = 123/01/16 |  | I/O parameters | R | WORD (BitString16) | - |  |  | [Cab Fix Logic Output] (OLC2) | [I/O Map] (IOM) [Bypass Drive Data] (IOCP)
OLCP | Cabinet logic output state | 16#1460 = 5216 | 16#2016/11 | 16#7B/01/11 = 123/01/17 |  | I/O parameters | R | WORD (BitString16) | - |  |  | [Cab Logic Output] (OLCP) | [I/O Map] (IOM) [Bypass Drive Data] (IOCP)
PSS | Drive Systems pre-settings status | 16#1F7C = 8060 | 16#2032/3D | 16#89/01/3D = 137/01/61 | PSS | Configuration management | R | WORD (Enumeration) | -
HTQ | High torque | 16#241A = 9242 | 16#203E/2B | 16#8F/01/2B = 143/01/43 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 300.0 % | -300.0 % ... 300.0 % | [High Torque] (HTQ) | [Torque control] (TOR) [Settings] (SET) [M/S Torque Control] (MSQ)
LTQ | Low torque | 16#241B = 9243 | 16#203E/2C | 16#8F/01/2C = 143/01/44 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | -300.0 % | -300.0 % ... 300.0 % | [Low Torque] (LTQ) | [Torque control] (TOR) [Settings] (SET) [M/S Torque Control] (MSQ)
ILN | Mains current | 16#35D7 = 13783 | 16#206B/54 | 16#A5/01/B8 = 165/01/184 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Current] (ILN) | [Drive parameters] (MPI)
IL1 | Mains current L1 | 16#9A42 = 39490 |  |  |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Current L1] (IL1) | [Drive parameters] (MPI)
IL2 | Mains current L2 | 16#9A43 = 39491 |  |  |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Current L2] (IL2) | [Drive parameters] (MPI)
IL3 | Mains current L3 | 16#9A44 = 39492 |  |  |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Current L3] (IL3) | [Drive parameters] (MPI)
IQRW | Input reactive power | 16#0CE2 = 3298 | 16#2002/63 | 16#71/01/63 = 113/01/99 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Input Reactive Power] (IQRW) | [Elec Ener Input Counter] (ELI)
ISRW | Apparent input power | 16#0CE3 = 3299 | 16#2002/64 | 16#71/01/64 = 113/01/100 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Apparent Input Power] (ISRW) | [Elec Ener Input Counter] (ELI)
PWF | Input power factor | 16#35DA = 13786 | 16#206B/57 | 16#A5/01/BB = 165/01/187 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Input Power Factor] (PWF) | [Elec Ener Input Counter] (ELI)
FAC | Mains frequency | 16#35B6 = 13750 | 16#206B/33 | 16#A5/01/97 = 165/01/151 |  | Measurement parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Mains Frequency] (FAC) | [Drive parameters] (MPI)
OT4Q | 4 Quadrant Output torque value (100% = Cn motor) | 16#0CCE = 3278 | 16#2002/4F | 16#71/01/4F = 113/01/79 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
ST4Q | 4 Quadrant Output torque value (% of Cn motor in Q12) without filter | 16#0CCF = 3279 | 16#2002/50 | 16#71/01/50 = 113/01/80 |  | Actual values parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
PTOH | PTO maximum output frequency | 16#1251 = 4689 | 16#2010/5A | 16#78/01/5A = 120/01/90 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 kHz | Refer to programming manual | 1.00 kHz ... 30.00 kHz | [PTO Max Output Freq] (PTOH) | [PTO Frequency] (PTOC) [PTO configuration] (PTO) [PTO configuration] (PTO)
PTO | PTO assignment | 16#13BA = 5050 | 16#2014/33 | 16#7A/01/33 = 122/01/51 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [PTO Assign] (PTO) | [PTO Frequency] (PTOC) [PTO configuration] (PTO) [PTO configuration] (PTO)
PTOC | PTO frequency | 16#14A9 = 5289 | 16#2016/5A | 16#7B/01/5A = 123/01/90 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 kHz | 0.00 kHz | 0.00 kHz ... 655.35 kHz | [PTO Frequency] (PTOC) | [PTO configuration] (PTO) [PTO configuration] (PTO)
PUC | Encoder pulse count | 16#15EB = 5611 | 16#201A/C | 16#7D/01/0C = 125/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
SSCD | SSI code type | 16#15F4 = 5620 | 16#201A/15 | 16#7D/01/15 = 125/01/21 | SSCD | Configuration and settings | R/WS | WORD (Enumeration) | - | [Undefined] UND |  | [SSI code type] (SSCD) | [Encoder configuration] (IEN)
SSCP | SSI parity | 16#15F5 = 5621 | 16#201A/16 | 16#7D/01/16 = 125/01/22 | SSCP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Undefined] UND |  | [SSI parity] (SSCP) | [Encoder configuration] (IEN)
SSFS | SSI frame size | 16#15F6 = 5622 | 16#201A/17 | 16#7D/01/17 = 125/01/23 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | 0 ... 31 | [SSI frame size] (SSFS) | [Encoder configuration] (IEN)
ENMR | Number of revolutions | 16#15F7 = 5623 | 16#201A/18 | 16#7D/01/18 = 125/01/24 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | -1 | -1 ... 25 | [Nbr of revolutions] (ENMR) | [Encoder configuration] (IEN)
ENTR | Turn bit resolution | 16#15F8 = 5624 | 16#201A/19 | 16#7D/01/19 = 125/01/25 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | -1 | -1 ... 25 | [Turn bit resolution] (ENTR) | [Encoder configuration] (IEN)
REFQ | Resolver excitation frequency | 16#15FD = 5629 | 16#201A/1E | 16#7D/01/1E = 125/01/30 | REFQ | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 kHz] 8K |  | [Resolver Exct. Freq.] (REFQ) | [Encoder configuration] (IEN)
ENSP | Clock frequency | 16#15FB = 5627 | 16#201A/1C | 16#7D/01/1C = 125/01/28 | ENSP | Configuration and settings | R/WS | WORD (Enumeration) | - | [200 kHz] 200k |  | [Clock frequency] (ENSP) | [Encoder configuration] (IEN)
RPOS | Reset position assignment | 16#15FC = 5628 | 16#201A/1D | 16#7D/01/1D = 125/01/29 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Reset Position Assign] (RPOS) | [Encoder configuration] (IEN)
ABMF | AB encoder maximum frequency | 16#1600 = 5632 | 16#201A/21 | 16#7D/01/21 = 125/01/33 | ABMF | Configuration and settings | R/WS | WORD (Enumeration) | - | [300 kHz] 300K |  | [AB Encoder Max Freq] (ABMF) | [Encoder configuration] (IEN)
ENCR | Encoder resolution characteristic | 16#1642 = 5698 | 16#201A/63 | 16#7D/01/63 = 125/01/99 |  | Actual values parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
NSL | Nominal motor slip | 16#2585 = 9605 | 16#2042/6 | 16#91/01/06 = 145/01/06 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 Hz |  | 0.0 Hz ... 6553.5 Hz | [Nominal motor slip] (NSL) | [data] (MTD)
SPD1 | Signed mechanical speed | 16#2EEC = 12012 | 16#205A/D | 16#9D/01/0D = 157/01/13 |  | Actual values parameters | R | INT (Signed32) | Refer to programming manual |  | -100000 ... 100000 | [Signed Mech Speed] (SPD1) | [Motor parameters] (MMO)
BQM | Backlash mode | 16#41DC = 16860 | 16#208A/3D | 16#B5/01/3D = 181/01/61 | BQM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [BL Mode] (BQM) | [Backlash compensation] (BSQM)
BQFB | Response to backlash error | 16#41DD = 16861 | 16#208A/3E | 16#B5/01/3E = 181/01/62 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [BL ErrorResp] (BQFB) | [Backlash compensation] (BSQM)
BQSL | Backlash reference frequency | 16#41DF = 16863 | 16#208A/40 | 16#B5/01/40 = 181/01/64 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [BL Ref Freq] (BQSL) | [Backlash compensation] (BSQM)
BQA | Backlash acceleration | 16#41E0 = 16864 | 16#208A/41 | 16#B5/01/41 = 181/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 1 ... 9999 | [BL Acceleration] (BQA) | [Backlash compensation] (BSQM)
BQTL | Backlash torque limitation value | 16#41E1 = 16865 | 16#208A/42 | 16#B5/01/42 = 181/01/66 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 5.0 % | 0.0 % ... 100.0 % | [BL Trq Lim Value] (BQTL) | [Backlash compensation] (BSQM)
BQT | Backlash torque limitation monitoring delay | 16#41E2 = 16866 | 16#208A/43 | 16#B5/01/43 = 181/01/67 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 100.0 s | [BL Monit Delay] (BQT) | [Backlash compensation] (BSQM)
BQST | Backlash start delay | 16#41E3 = 16867 | 16#208A/44 | 16#B5/01/44 = 181/01/68 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 100.0 s | [BL Start Delay] (BQST) | [Backlash compensation] (BSQM)
BQFD | Backlash timeout | 16#41E4 = 16868 | 16#208A/45 | 16#B5/01/45 = 181/01/69 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | Refer to programming manual | 0.0 s ... 100.0 s | [BL Timeout] (BQFD) | [Backlash compensation] (BSQM)
BQMM | Backlash type | 16#41E6 = 16870 | 16#208A/47 | 16#B5/01/47 = 181/01/71 | BQMM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Sequential] SEQ |  | [BL Type] (BQMM) | [Backlash compensation] (BSQM)
BQMC | Backlash on slave(s) feedback | 16#41E7 = 16871 | 16#208A/48 | 16#B5/01/48 = 181/01/72 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [BL Slave Fdbck] (BQMC) | [Backlash compensation] (BSQM)
BQMT | Backlash time | 16#41E8 = 16872 | 16#208A/49 | 16#B5/01/49 = 181/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 100.0 s | [BL Time] (BQMT) | [Backlash compensation] (BSQM)
FDR0 | FDR error status | 16#FBB0 = 64432 |  |  | EFDR | Configuration management | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR0) | [Fast Device Replacement] (FDR)
FDS0 | FDR operating state | 16#FBB1 = 64433 |  |  | SFDR | Configuration management | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS0) | [Fast Device Replacement] (FDR)
FDA0 | FDR action | 16#FBB2 = 64434 |  |  | FDRA | Configuration management | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA0) | [Fast Device Replacement] (FDR)
FDV0 | Enable FDR function | 16#FBB3 = 64435 |  |  | N_Y | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV0) | [Fast Device Replacement] (FDR)
INF6 | Module identification error (INF6) | 16#1BE1 = 7137 | 16#2029/26 | 16#84/01/8A = 132/01/138 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Identification Error (INF6)] (INF6) | [Diag. data] (DDT)
INFJ | Internal Error 19 (Encoder) | 16#1BE6 = 7142 | 16#2029/2B | 16#84/01/8F = 132/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Internal Error 19] (INFJ) | [Diag. data] (DDT)
ENCE | Encoder feedback error number | 16#1643 = 5699 | 16#201A/64 | 16#7D/01/64 = 125/01/100 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Encoder Fdbck Error] (ENCE) | [Diag. data] (DDT)
HS1 | HMI status | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS1) | [None] (DP1)
HS2 | HMI status | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS2) | [None] (DP2)
HS3 | HMI status | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS3) | [None] (DP3)
HS4 | HMI status | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS4) | [None] (DP4)
HS5 | HMI status | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS5) | [None] (DP5)
HS6 | HMI status | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS6) | [None] (DP6)
HS7 | HMI status | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS7) | [None] (DP7)
HS8 | HMI status | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS8) | [None] (DP8)
MSS | M/S function status | 16#41C8 = 16840 | 16#208A/29 | 16#B5/01/29 = 181/01/41 | MSS | Status parameters | R | WORD (Enumeration) | - |  |  | [M/S Status] (MSS) | [M/S Local Display] (MSO)
MSMS | M/S Master speed reference | 16#41C9 = 16841 | 16#208A/2A | 16#B5/01/2A = 181/01/42 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -300.0 Hz ... 300.0 Hz | [M/S Master Speed Ref] (MSMS) | [M/S Local Display] (MSO)
MSMT | M/S Master torque reference | 16#41CA = 16842 | 16#208A/2B | 16#B5/01/2B = 181/01/43 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
MSSR | M/S Local speed reference | 16#41CB = 16843 | 16#208A/2C | 16#B5/01/2C = 181/01/44 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -300.0 Hz ... 300.0 Hz | [M/S Local Speed Ref] (MSSR) | [M/S Local Display] (MSO) [M/S System Display] (MSR)
MSTR | M/S Local torque reference | 16#41CC = 16844 | 16#208A/2D | 16#B5/01/2D = 181/01/45 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
OTQN | Motor Torque in Nm | 16#0CC4 = 3268 | 16#2002/45 | 16#71/01/45 = 113/01/69 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor Torque (Nm)] (OTQN) | [M/S Local Display] (MSO) [Motor parameters] (MMO)
MSDN | M/S device selection | 16#41CD = 16845 | 16#208A/2E | 16#B5/01/2E = 181/01/46 | MSID | Configuration and settings | R/W | WORD (Enumeration) | - | [Master] MSTER |  | [M/S Device Selection] (MSDN) | [M/S System Display] (MSR)
MSDS | M/S device status | 16#41CE = 16846 | 16#208A/2F | 16#B5/01/2F = 181/01/47 | MSS | Status parameters | R | WORD (Enumeration) | - |  |  | [M/S Device Status] (MSDS) | [M/S System Display] (MSR)
MSXS | M/S device speed reference | 16#41D0 = 16848 | 16#208A/31 | 16#B5/01/31 = 181/01/49 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -300.0 Hz ... 300.0 Hz | [M/S Device Speed Ref] (MSXS) | [M/S System Display] (MSR)
MSXT | M/S device torque reference | 16#41CF = 16847 | 16#208A/30 | 16#B5/01/30 = 181/01/48 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
TQN | Computed nominal motor torque | 16#25C5 = 9669 | 16#2042/46 | 16#91/01/46 = 145/01/70 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual | 499 | 1 ... 65535 | [Nom Motor torque] (TQN) | [Motor parameters] (MMO)
LTR | Torque reference | 16#2139 = 8505 | 16#2037/6 | 16#8B/01/6A = 139/01/106 |  | Setpoint parameters | R/W | INT (Signed16) | 0.1 % | 0.0 % | -300.0 % ... 300.0 % | [Torque ref.] (LTR) | [Drive parameters] (MPI)
TRR | Torque reference before ramp | 16#240F = 9231 | 16#203E/20 | 16#8F/01/20 = 143/01/32 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Torque reference] (TRR) | [Drive parameters] (MPI)
SFQ | Stator frequency | 16#0CC3 = 3267 | 16#2002/44 | 16#71/01/44 = 113/01/68 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.8 Hz ... 3276.7 Hz | [Stator Frequency] (SFQ) | [Drive parameters] (MPI)
RFQ | Rotor frequency | 16#0CC2 = 3266 | 16#2002/43 | 16#71/01/43 = 113/01/67 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.8 Hz ... 3276.7 Hz | [Rotor Frequency] (RFQ) | [Drive parameters] (MPI)
UL1 | Mains voltage phase 1-2 | 16#35B3 = 13747 | 16#206B/30 | 16#A5/01/94 = 165/01/148 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains voltage phase 1-2] (UL1) | [Drive parameters] (MPI)
UL2 | Mains voltage phase 2-3 | 16#35B4 = 13748 | 16#206B/31 | 16#A5/01/95 = 165/01/149 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains voltage phase 2-3] (UL2) | [Drive parameters] (MPI)
UL3 | Mains voltage phase 3-1 | 16#35B5 = 13749 | 16#206B/32 | 16#A5/01/96 = 165/01/150 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains voltage phase 3-1] (UL3) | [Drive parameters] (MPI)
THEV | Encoder thermal value | 16#161F = 5663 | 16#201A/40 | 16#7D/01/40 = 125/01/64 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Enc Th Value] (THEV) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THER | Encoder thermal resistor value | 16#161E = 5662 | 16#201A/3F | 16#7D/01/3F = 125/01/63 |  | Measurement parameters | R | INT (Signed16) | 1 Ohm |  | -32767 Ohm ... 32767 Ohm | [Enc Resistor Value] (THER) | [Analog inputs image] (AIA)
APPT | Application selection | 16#3D53 = 15699 | 16#207E/64 | 16#AF/01/64 = 175/01/100 | APPT | Configuration and settings | R/WS | WORD (Enumeration) | - | [All application functions available] ALL |  | [Application Selection] (APPT) | [Macro Configuration] (MCR)
MPC | Motor parameter choice | 16#258E = 9614 | 16#2042/F | 16#91/01/0F = 145/01/15 | MPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Nominal motor Power] NPR |  | [Motor param choice] (MPC) | [data] (MTD)
CRFA | Internal currents filter time | 16#239E = 9118 | 16#203D/13 | 16#8E/01/77 = 142/01/119 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 ms |  | 0.0 ms ... 6553.5 ms | [Currents Filter] (CRFA) | [data] (MTD)
RDAE | % error EMF sync | 16#25CC = 9676 | 16#2042/4D | 16#91/01/4D = 145/01/77 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | 0.0 % ... 6553.5 % | [% error EMF sync] (RDAE) | [data] (MTD)
TUNU | Autotuning usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Autotuning Usage] (TUNU) | [Motor tune] (MTU)
TCR | Level of current for autotuning | 16#259B = 9627 | 16#2042/1C | 16#91/01/1C = 145/01/28 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Autotuning Lvl Of Current] (TCR) | [Motor tune] (MTU)
RCL | Alignment Rotational Current Level | 16#3668 = 13928 | 16#206D/1D | 16#A6/01/81 = 166/01/129 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 75 % | 10 % ... 300 % | [Rotational Current Level] (RCL) | [Motor tune] (MTU)
RCIR | RCI alignment with transformer | 16#366A = 13930 | 16#206D/1F | 16#A6/01/83 = 166/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [RCI With Transformer] (RCIR) | [Motor tune] (MTU)
RCSP | RCI maximum output frequency | 16#366B = 13931 | 16#206D/20 | 16#A6/01/84 = 166/01/132 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | RCSP_AUTO | -0.1 Hz ... 300.0 Hz | [RCI Max Freq] (RCSP) | [Motor tune] (MTU)
THET | Encoder thermal sensor type | 16#161D = 5661 | 16#201A/3E | 16#7D/01/3E = 125/01/62 | THET | Configuration and settings | R/WS | WORD (Enumeration) | - | [None] NONE |  | [Enc Therm Sensor Type] (THET) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THEB | Response to thermal error for encoder | 16#1622 = 5666 | 16#201A/43 | 16#7D/01/43 = 125/01/67 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [Enc Th ErrorResp] (THEB) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THEF | Thermal error level for encoder | 16#1621 = 5665 | 16#201A/42 | 16#7D/01/42 = 125/01/66 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [Enc Th Error Level] (THEF) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THEA | Thermal warning level for encoder | 16#1620 = 5664 | 16#201A/41 | 16#7D/01/41 = 125/01/65 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [Enc Th Warn Level] (THEA) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
BOO | Boost | 16#3658 = 13912 | 16#206D/D | 16#A6/01/71 = 166/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | Refer to programming manual | -100 % ... 100 % | [Boost] (BOO) | [Motor control] (DRC)
FAB | Frequency Boost | 16#3657 = 13911 | 16#206D/C | 16#A6/01/70 = 166/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [Freq Boost] (FAB) | [Motor control] (DRC)
TEFF | External feed forward assignment | 16#23AA = 9130 | 16#203D/1F | 16#8E/01/83 = 142/01/131 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [External FeedFwd Assign] (TEFF) | [Spd Loop Optimization] (MCL)
FRI | Frequency of the HF injection signal | 16#3CF1 = 15601 | 16#207E/2 | 16#AF/01/02 = 175/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 Hz | 500 Hz | 250 Hz ... 1000 Hz | [HF injection freq.] (FRI) | [Motor control] (DRC)
MSCM | M/S communication mode | 16#41A0 = 16800 | 16#208A/1 | 16#B5/01/01 = 181/01/01 | MSCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [M/S Comm Mode] (MSCM) | [M/S System Architecture] (MSA)
MSID | Master or Slave ID selection | 16#41A1 = 16801 | 16#208A/2 | 16#B5/01/02 = 181/01/02 | MSID | Configuration and settings | R/WS | WORD (Enumeration) | - | [Master] MSTER |  | [M/S Device ID] (MSID) | [M/S System Architecture] (MSA)
MSDT | Master or Slave selection | 16#41A2 = 16802 | 16#208A/3 | 16#B5/01/03 = 181/01/03 | MSDT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Master] MSTER |  | [M/S Device Role] (MSDT) | [M/S System Architecture] (MSA)
MSSN | M/S number of slaves | 16#41A3 = 16803 | 16#208A/4 | 16#B5/01/04 = 181/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 10 | [M/S Number of Slaves] (MSSN) | [M/S System Architecture] (MSA)
MSSI | M/S Master speed reference input assignment | 16#41A4 = 16804 | 16#208A/5 | 16#B5/01/05 = 181/01/05 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [M/S Speed Ref In Assign] (MSSI) | [M/S System Architecture] (MSA)
MSTI | M/S Master torque reference input assignment | 16#41A6 = 16806 | 16#208A/7 | 16#B5/01/07 = 181/01/07 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [M/S Trq Ref In Assign] (MSTI) | [M/S System Architecture] (MSA)
MSSO | M/S speed reference output assignment | 16#41A5 = 16805 | 16#208A/6 | 16#B5/01/06 = 181/01/06 | CSA | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [M/S Speed Ref Out Assign] (MSSO) | [M/S System Architecture] (MSA)
MSTO | M/S torque reference output assignment | 16#41A7 = 16807 | 16#208A/8 | 16#B5/01/08 = 181/01/08 | CSA | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [M/S Trq Ref Out Assign] (MSTO) | [M/S System Architecture] (MSA)
MSDI | M/S local mode assignment | 16#41A8 = 16808 | 16#208A/9 | 16#B5/01/09 = 181/01/09 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [M/S Local Mode Assign] (MSDI) | [M/S System Architecture] (MSA)
MLTO | MultiDrive Link communication timeout | 16#17C5 = 6085 | 16#201E/56 | 16#7F/01/56 = 127/01/86 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.05 s | 0.01 s ... 10.00 s | [MDL Comm Timeout] (MLTO) | [M/S System Architecture] (MSA)
MSCB | M/S Response to communication error | 16#41A9 = 16809 | 16#208A/A | 16#B5/01/0A = 181/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [M/S Comm ErrorResp] (MSCB) | [M/S System Architecture] (MSA)
MSDB | M/S Response to device error | 16#41AA = 16810 | 16#208A/B | 16#B5/01/0B = 181/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [M/S Device ErrorResp] (MSDB) | [M/S System Architecture] (MSA)
MSDD | M/S device error delay | 16#41AB = 16811 | 16#208A/C | 16#B5/01/0C = 181/01/12 |  | Configuration and settings | R/WS | INT (Signed16) | 1 s | -1 s | -1 s ... 60 s | [M/S Device Error Delay] (MSDD) | [M/S System Architecture] (MSA)
MSMC | M/S mechanical coupling type | 16#41B4 = 16820 | 16#208A/15 | 16#B5/01/15 = 181/01/21 | MSMC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Rigid coupling] RIGID |  | [M/S Coupling Type] (MSMC) | [M/S Control] (MST)
MSCT | M/S control type | 16#41B5 = 16821 | 16#208A/16 | 16#B5/01/16 = 181/01/22 | MSCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Direct torque control ] TRQD |  | [M/S Control Type] (MSCT) | [M/S Control] (MST)
SSD | Speed reference direction | 16#41D1 = 16849 | 16#208A/32 | 16#B5/01/32 = 181/01/50 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Speed Ref Direction] (SSD) | [M/S Torque Control] (MSQ)
TQOP | Torque reference offset | 16#2412 = 9234 | 16#203E/23 | 16#8F/01/23 = 143/01/35 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -1000.0 % ... 1000.0 % | [Torque Ref Offset] (TQOP) | [Torque control] (TOR) [M/S Torque Control] (MSQ)
TRF | Torque filter activation | 16#2414 = 9236 | 16#203E/25 | 16#8F/01/25 = 143/01/37 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Torque Filter] (TRF) | [Torque control] (TOR) [M/S Control] (MST)
TRW | Torque filter bandwidth | 16#2415 = 9237 | 16#203E/26 | 16#8F/01/26 = 143/01/38 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 Hz | 20 Hz | 1 Hz ... 1000 Hz | [Torque Filter Bandwidth] (TRW) | [Torque control] (TOR) [M/S Control] (MST)
MSFE | M/S advanced filter activation | 16#41BE = 16830 | 16#208A/1F | 16#B5/01/1F = 181/01/31 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [M/S Advanced Filter] (MSFE) | [M/S Filters] (MSF)
MSFF | M/S advanced filter frequency | 16#41BF = 16831 | 16#208A/20 | 16#B5/01/20 = 181/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 10.0 Hz ... 150.0 Hz | [M/S Advanced Filter Freq] (MSFF) | [M/S Filters] (MSF)
MSFB | M/S advanced filter bandwidth | 16#41C0 = 16832 | 16#208A/21 | 16#B5/01/21 = 181/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 10 % ... 400 % | [M/S Advanced Filter Bdw] (MSFB) | [M/S Filters] (MSF)
MSFD | M/S advanced filter depth | 16#41C1 = 16833 | 16#208A/22 | 16#B5/01/22 = 181/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 99 % | [M/S Advanced Filter Depth] (MSFD) | [M/S Filters] (MSF)
MSFG | M/S advanced filter gain | 16#41C2 = 16834 | 16#208A/23 | 16#B5/01/23 = 181/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 1000 % | [M/S Advanced Filter Gain] (MSFG) | [M/S Filters] (MSF)
MSFC | M/S advanced filter coefficient | 16#41C3 = 16835 | 16#208A/24 | 16#B5/01/24 = 181/01/36 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 1000 % | [M/S Advanced Filter Coeff] (MSFC) | [M/S Filters] (MSF)
MSIB | M/S load balancing torque reference selection | 16#41BC = 16828 | 16#208A/1D | 16#B5/01/1D = 181/01/29 | MSTS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Before advanced filter] BFILT |  | [M/S Balance Trq Ref Sel] (MSIB) | [Load Sharing M/S] (MSB)
MSIT | M/S Master torque reference entry in control chain | 16#41BA = 16826 | 16#208A/1B | 16#B5/01/1B = 181/01/27 | MSTS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Before advanced filter] BFILT |  | [M/S Torque Ref Entry] (MSIT) | [M/S Control] (MST)
MSOT | M/S output torque reference selection | 16#41BB = 16827 | 16#208A/1C | 16#B5/01/1C = 181/01/28 | MSTS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Before advanced filter] BFILT |  | [M/S Out Torque Ref Select] (MSOT) | [M/S Control] (MST)
MSIS | M/S Master speed reference entry in control chain | 16#41B8 = 16824 | 16#208A/19 | 16#B5/01/19 = 181/01/25 | MSSS | Configuration and settings | R/WS | WORD (Enumeration) | - | [After Ramp] ARMP |  | [M/S Speed Ref Entry] (MSIS) | [M/S Control] (MST)
MSOS | M/S output speed reference selection | 16#41B9 = 16825 | 16#208A/1A | 16#B5/01/1A = 181/01/26 | MSSS | Configuration and settings | R/WS | WORD (Enumeration) | - | [After Ramp] ARMP |  | [M/S Out Speed Ref Select] (MSOS) | [M/S Control] (MST)
TPMM | Maximum power in motor mode | 16#2400 = 9216 | 16#203E/11 | 16#8F/01/11 = 143/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 0 % ... 300 % | [Pmax Motor] (TPMM) | [Torque limitation] (TOL) [Settings] (SET)
TPMG | Maximum power in generator mode | 16#2401 = 9217 | 16#203E/12 | 16#8F/01/12 = 143/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 0 % ... 300 % | [Pmax Generator] (TPMG) | [Torque limitation] (TOL) [Settings] (SET)
PTOL | PTO min output frequency | 16#1250 = 4688 | 16#2010/59 | 16#78/01/59 = 120/01/89 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 kHz | Refer to programming manual | 1.00 kHz ... 30.00 kHz | [PTO Min Output Freq] (PTOL) | [PTO configuration] (PTO) [PTO configuration] (PTO)
TRES | Resolver transformation ratio | 16#15F3 = 5619 | 16#201A/14 | 16#7D/01/14 = 125/01/20 | TRES | Configuration and settings | R/WS | WORD (Enumeration) | - | [0.5] 05 |  | [Transformation ratio] (TRES) | [Encoder configuration] (IEN)
UELC | Sincos lines count | 16#15F1 = 5617 | 16#201A/12 | 16#7D/01/12 = 125/01/18 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 10000 | [Sincos lines count] (UELC) | [Encoder configuration] (IEN)
TLOL | Drive overload monitoring activation | 16#1B77 = 7031 | 16#2028/20 | 16#84/01/20 = 132/01/32 | TLOL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Drive Overload Monit] (TLOL) | [Drive overload monit] (OBR)
TWO | Terminal Modbus: Word order | 16#1776 = 6006 | 16#201E/7 | 16#7F/01/07 = 127/01/07 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term word order] (TWO) | [Modbus Fieldbus] (MD1)
TWO2 | Terminal Modbus 2: Word order | 16#178A = 6026 | 16#201E/1B | 16#7F/01/1B = 127/01/27 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term 2 word order] (TWO2) | [Modbus HMI] (MD2)
FDR1 | FDR error status | 16#FBBA = 64442 |  |  | EFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR1) | [Fast Device Rep.] (FDRO)
FDS1 | FDR operating state | 16#FBBB = 64443 |  |  | SFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS1) | [Fast Device Rep.] (FDRO)
FDA1 | FDR action | 16#FBBC = 64444 |  |  | FDRA | Configuration and settings | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA1) | [Fast Device Rep.] (FDRO)
FDV1 | Enable FDR function | 16#FBBD = 64445 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV1) | [Fast Device Rep.] (FDRO)
CIC2 | Incorrect configuration 2 | 16#1C16 = 7190 | 16#2029/5B | 16#84/01/BF = 132/01/191 |  | Fault parameters | R/WS | WORD (BitString16) | -
CS19 | Cabinet status 1 | 16#1EBD = 7869 | 16#2030/46 | 16#88/01/46 = 136/01/70 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS19) | [None] (DP9)
CS29 | Cabinet status 2 | 16#1ED1 = 7889 | 16#2030/5A | 16#88/01/5A = 136/01/90 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS29) | [None] (DP9)
TTS9 | Thermal transformer | 16#1EE5 = 7909 | 16#2031/A | 16#88/01/6E = 136/01/110 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTS9) | [None] (DP9)
FRP9 | Reference frequency | 16#1EF9 = 7929 | 16#2031/1E | 16#88/01/82 = 136/01/130 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRP9) | [None] (DP9)
CS1A | Cabinet status 1 | 16#1EBE = 7870 | 16#2030/47 | 16#88/01/47 = 136/01/71 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS1A) | [None] (DPA)
CS2A | Cabinet status 2 | 16#1ED2 = 7890 | 16#2030/5B | 16#88/01/5B = 136/01/91 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS2A) | [None] (DPA)
TTSA | Thermal transformer | 16#1EE6 = 7910 | 16#2031/B | 16#88/01/6F = 136/01/111 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTSA) | [None] (DPA)
FRPA | Reference frequency | 16#1EFA = 7930 | 16#2031/1F | 16#88/01/83 = 136/01/131 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRPA) | [None] (DPA)
CS1B | Cabinet status 1 | 16#1EBF = 7871 | 16#2030/48 | 16#88/01/48 = 136/01/72 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS1B) | [None] (DPB)
CS2B | Cabinet status 2 | 16#1ED3 = 7891 | 16#2030/5C | 16#88/01/5C = 136/01/92 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS2B) | [None] (DPB)
TTSB | Thermal transformer | 16#1EE7 = 7911 | 16#2031/C | 16#88/01/70 = 136/01/112 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTSB) | [None] (DPB)
FRPB | Reference frequency | 16#1EFB = 7931 | 16#2031/20 | 16#88/01/84 = 136/01/132 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRPB) | [None] (DPB)
CS1C | Cabinet status 1 | 16#1EC0 = 7872 | 16#2030/49 | 16#88/01/49 = 136/01/73 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS1C) | [None] (DPC)
CS2C | Cabinet status 2 | 16#1ED4 = 7892 | 16#2030/5D | 16#88/01/5D = 136/01/93 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS2C) | [None] (DPC)
TTSC | Thermal transformer | 16#1EE8 = 7912 | 16#2031/D | 16#88/01/71 = 136/01/113 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTSC) | [None] (DPC)
FRPC | Reference frequency | 16#1EFC = 7932 | 16#2031/21 | 16#88/01/85 = 136/01/133 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRPC) | [None] (DPC)
CS1D | Cabinet status 1 | 16#1EC1 = 7873 | 16#2030/4A | 16#88/01/4A = 136/01/74 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS1D) | [None] (DPD)
CS2D | Cabinet status 2 | 16#1ED5 = 7893 | 16#2030/5E | 16#88/01/5E = 136/01/94 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS2D) | [None] (DPD)
TTSD | Thermal transformer | 16#1EE9 = 7913 | 16#2031/E | 16#88/01/72 = 136/01/114 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTSD) | [None] (DPD)
FRPD | Reference frequency | 16#1EFD = 7933 | 16#2031/22 | 16#88/01/86 = 136/01/134 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRPD) | [None] (DPD)
CS1E | Cabinet status 1 | 16#1EC2 = 7874 | 16#2030/4B | 16#88/01/4B = 136/01/75 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS1E) | [None] (DPE)
CS2E | Cabinet status 2 | 16#1ED6 = 7894 | 16#2030/5F | 16#88/01/5F = 136/01/95 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS2E) | [None] (DPE)
TTSE | Thermal transformer | 16#1EEA = 7914 | 16#2031/F | 16#88/01/73 = 136/01/115 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTSE) | [None] (DPE)
FRPE | Reference frequency | 16#1EFE = 7934 | 16#2031/23 | 16#88/01/87 = 136/01/135 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRPE) | [None] (DPE)
CS1F | Cabinet status 1 | 16#1EC3 = 7875 | 16#2030/4C | 16#88/01/4C = 136/01/76 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 1] (CS1F) | [None] (DPF)
CS2F | Cabinet status 2 | 16#1ED7 = 7895 | 16#2030/60 | 16#88/01/60 = 136/01/96 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cab status 2] (CS2F) | [None] (DPF)
TTSF | Thermal transformer | 16#1EEB = 7915 | 16#2031/10 | 16#88/01/74 = 136/01/116 |  | History parameters | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer] (TTSF) | [None] (DPF)
FRPF | Reference frequency | 16#1EFF = 7935 | 16#2031/24 | 16#88/01/88 = 136/01/136 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Reference Frequency] (FRPF) | [None] (DPF)
PCM0 | Power cell status 1 | 16#9B3D = 39741 |  |  | PCM0 | Actual values parameters | R | WORD (Enumeration) | - |  |  | [Power cell status 1] (PCM0) | [Power Cell Data] (POCM)
PCM1 | Power cell status 2 | 16#9B3E = 39742 |  |  |  | Actual values parameters | R | WORD (BitString16) | - |  |  | [Power cell status 2] (PCM1) | [Power Cell Data] (POCM)
ULN9 | Mains voltage | 16#9B81 = 39809 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULN9) | [None] (DP9)
ILN9 | Mains current | 16#9BBD = 39869 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILN9) | [None] (DP9)
ULNA | Mains voltage | 16#9B82 = 39810 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULNA) | [None] (DPA)
ILNA | Mains current | 16#9BBE = 39870 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILNA) | [None] (DPA)
ULNB | Mains voltage | 16#9B83 = 39811 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULNB) | [None] (DPB)
ILNB | Mains current | 16#9BBF = 39871 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILNB) | [None] (DPB)
ULNC | Mains voltage | 16#9B84 = 39812 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULNC) | [None] (DPC)
ILNC | Mains current | 16#9BC0 = 39872 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILNC) | [None] (DPC)
ULND | Mains voltage | 16#9B85 = 39813 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULND) | [None] (DPD)
ILND | Mains current | 16#9BC1 = 39873 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILND) | [None] (DPD)
ULNE | Mains voltage | 16#9B86 = 39814 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULNE) | [None] (DPE)
ILNE | Mains current | 16#9BC2 = 39874 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILNE) | [None] (DPE)
ULNF | Mains voltage | 16#9B87 = 39815 |  |  |  | History parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Voltage] (ULNF) | [None] (DPF)
ILNF | Mains current | 16#9BC3 = 39875 |  |  |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Mains Current] (ILNF) | [None] (DPF)
SIML | Simulation mode load | 16#9CC5 = 40133 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Sim Mode Load] (SIML) | [Simulation Mode] (SIMM)
SIMM | Simulation mode assignment | 16#9CC4 = 40132 |  |  | SIMM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sim Mode Assign] (SIMM) | [Simulation Mode] (SIMM)
OC00 | Application setting 0 | 16#9DD0 = 40400 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC01 | Application setting 1 | 16#9DD1 = 40401 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC02 | Application setting 2 | 16#9DD2 = 40402 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC03 | Application setting 3 | 16#9DD3 = 40403 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC04 | Application setting 4 | 16#9DD4 = 40404 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC05 | Application setting 5 | 16#9DD5 = 40405 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC06 | Application setting 6 | 16#9DD6 = 40406 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC07 | Application setting 7 | 16#9DD7 = 40407 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC08 | Application setting 8 | 16#9DD8 = 40408 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC09 | Application setting 9 | 16#9DD9 = 40409 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC10 | Application setting 10 | 16#9DDA = 40410 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC11 | Application setting 11 | 16#9DDB = 40411 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC12 | Application setting 12 | 16#9DDC = 40412 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC13 | Application setting 13 | 16#9DDD = 40413 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC14 | Application setting 14 | 16#9DDE = 40414 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC15 | Application setting 15 | 16#9DDF = 40415 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC16 | Application setting 16 | 16#9DE0 = 40416 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC17 | Application setting 17 | 16#9DE1 = 40417 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC18 | Application setting 18 | 16#9DE2 = 40418 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC19 | Application setting 19 | 16#9DE3 = 40419 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC20 | Application setting 20 | 16#9DE4 = 40420 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC21 | Application setting 21 | 16#9DE5 = 40421 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC22 | Application setting 22 | 16#9DE6 = 40422 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC23 | Application setting 23 | 16#9DE7 = 40423 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC24 | Application setting 24 | 16#9DE8 = 40424 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC25 | Application setting 25 | 16#9DE9 = 40425 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC26 | Application setting 26 | 16#9DEA = 40426 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC27 | Application setting 27 | 16#9DEB = 40427 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC28 | Application setting 28 | 16#9DEC = 40428 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC29 | Application setting 29 | 16#9DED = 40429 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC30 | Application setting 30 | 16#9DEE = 40430 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC31 | Application setting 31 | 16#9DEF = 40431 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC32 | Application setting 32 | 16#9DF0 = 40432 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC33 | Application setting 33 | 16#9DF1 = 40433 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC34 | Application setting 34 | 16#9DF2 = 40434 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC35 | Application setting 35 | 16#9DF3 = 40435 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC36 | Application setting 36 | 16#9DF4 = 40436 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC37 | Application setting 37 | 16#9DF5 = 40437 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC38 | Application setting 38 | 16#9DF6 = 40438 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC39 | Application setting 39 | 16#9DF7 = 40439 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC40 | Application setting 40 | 16#9DF8 = 40440 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC41 | Application setting 41 | 16#9DF9 = 40441 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC42 | Application setting 42 | 16#9DFA = 40442 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC43 | Application setting 43 | 16#9DFB = 40443 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC44 | Application setting 44 | 16#9DFC = 40444 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC45 | Application setting 45 | 16#9DFD = 40445 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC46 | Application setting 46 | 16#9DFE = 40446 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC47 | Application setting 47 | 16#9DFF = 40447 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC48 | Application setting 48 | 16#9E00 = 40448 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC49 | Application setting 49 | 16#9E01 = 40449 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC50 | Application setting 50 | 16#9E02 = 40450 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC51 | Application setting 51 | 16#9E03 = 40451 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC52 | Application setting 52 | 16#9E04 = 40452 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC53 | Application setting 53 | 16#9E05 = 40453 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC54 | Application setting 54 | 16#9E06 = 40454 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC55 | Application setting 55 | 16#9E07 = 40455 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC56 | Application setting 56 | 16#9E08 = 40456 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC57 | Application setting 57 | 16#9E09 = 40457 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC58 | Application setting 58 | 16#9E0A = 40458 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC59 | Application setting 59 | 16#9E0B = 40459 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC60 | Application setting 60 | 16#9E0C = 40460 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC61 | Application setting 61 | 16#9E0D = 40461 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC62 | Application setting 62 | 16#9E0E = 40462 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC63 | Application setting 63 | 16#9E0F = 40463 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC64 | Application setting 64 | 16#9E10 = 40464 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC65 | Application setting 65 | 16#9E11 = 40465 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC66 | Application setting 66 | 16#9E12 = 40466 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC67 | Application setting 67 | 16#9E13 = 40467 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC68 | Application setting 68 | 16#9E14 = 40468 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC69 | Application setting 69 | 16#9E15 = 40469 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC70 | Application setting 70 | 16#9E16 = 40470 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC71 | Application setting 71 | 16#9E17 = 40471 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC72 | Application setting 72 | 16#9E18 = 40472 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC73 | Application setting 73 | 16#9E19 = 40473 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC74 | Application setting 74 | 16#9E1A = 40474 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC75 | Application setting 75 | 16#9E1B = 40475 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC76 | Application setting 77 | 16#9E1C = 40476 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC77 | Application setting 77 | 16#9E1D = 40477 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC78 | Application setting 78 | 16#9E1E = 40478 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC79 | Application setting 79 | 16#9E1F = 40479 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC80 | Application setting 80 | 16#9E20 = 40480 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC81 | Application setting 81 | 16#9E21 = 40481 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC82 | Application setting 82 | 16#9E22 = 40482 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC83 | Application setting 83 | 16#9E23 = 40483 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC84 | Application setting 84 | 16#9E24 = 40484 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC85 | Application setting 85 | 16#9E25 = 40485 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC86 | Application setting 86 | 16#9E26 = 40486 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC87 | Application setting 86 | 16#9E27 = 40487 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC88 | Application setting 88 | 16#9E28 = 40488 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC89 | Application setting 89 | 16#9E29 = 40489 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC90 | Application setting 90 | 16#9E2A = 40490 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC91 | Application setting 91 | 16#9E2B = 40491 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC92 | Application setting 92 | 16#9E2C = 40492 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC93 | Application setting 93 | 16#9E2D = 40493 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC94 | Application setting 94 | 16#9E2E = 40494 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC95 | Application setting 95 | 16#9E2F = 40495 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC96 | Application setting 96 | 16#9E30 = 40496 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC97 | Application setting 96 | 16#9E31 = 40497 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC98 | Application setting 98 | 16#9E32 = 40498 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OC99 | Application setting 99 | 16#9E33 = 40499 |  |  |  | External Controller Application Configuration | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OM00 | Application monitoring 0 | 16#9E34 = 40500 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM01 | Application monitoring 1 | 16#9E35 = 40501 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM02 | Application monitoring 2 | 16#9E36 = 40502 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM03 | Application monitoring 3 | 16#9E37 = 40503 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM04 | Application monitoring 4 | 16#9E38 = 40504 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM05 | Application monitoring 5 | 16#9E39 = 40505 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM06 | Application monitoring 6 | 16#9E3A = 40506 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM07 | Application monitoring 7 | 16#9E3B = 40507 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM08 | Application monitoring 8 | 16#9E3C = 40508 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM09 | Application monitoring 9 | 16#9E3D = 40509 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM10 | Application monitoring 10 | 16#9E3E = 40510 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM11 | Application monitoring 11 | 16#9E3F = 40511 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM12 | Application monitoring 12 | 16#9E40 = 40512 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM13 | Application monitoring 13 | 16#9E41 = 40513 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM14 | Application monitoring 14 | 16#9E42 = 40514 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM15 | Application monitoring 15 | 16#9E43 = 40515 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM16 | Application monitoring 16 | 16#9E44 = 40516 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM17 | Application monitoring 17 | 16#9E45 = 40517 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM18 | Application monitoring 18 | 16#9E46 = 40518 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM19 | Application monitoring 19 | 16#9E47 = 40519 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM20 | Application monitoring 20 | 16#9E48 = 40520 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM21 | Application monitoring 21 | 16#9E49 = 40521 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM22 | Application monitoring 22 | 16#9E4A = 40522 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM23 | Application monitoring 23 | 16#9E4B = 40523 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM24 | Application monitoring 24 | 16#9E4C = 40524 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM25 | Application monitoring 25 | 16#9E4D = 40525 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM26 | Application monitoring 26 | 16#9E4E = 40526 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM27 | Application monitoring 27 | 16#9E4F = 40527 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM28 | Application monitoring 28 | 16#9E50 = 40528 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM29 | Application monitoring 29 | 16#9E51 = 40529 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM30 | Application monitoring 30 | 16#9E52 = 40530 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM31 | Application monitoring 31 | 16#9E53 = 40531 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM32 | Application monitoring 32 | 16#9E54 = 40532 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM33 | Application monitoring 33 | 16#9E55 = 40533 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM34 | Application monitoring 34 | 16#9E56 = 40534 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM35 | Application monitoring 35 | 16#9E57 = 40535 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM36 | Application monitoring 36 | 16#9E58 = 40536 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM37 | Application monitoring 37 | 16#9E59 = 40537 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM38 | Application monitoring 38 | 16#9E5A = 40538 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM39 | Application monitoring 39 | 16#9E5B = 40539 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM40 | Application monitoring 40 | 16#9E5C = 40540 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM41 | Application monitoring 41 | 16#9E5D = 40541 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM42 | Application monitoring 42 | 16#9E5E = 40542 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM43 | Application monitoring 43 | 16#9E5F = 40543 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM44 | Application monitoring 44 | 16#9E60 = 40544 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM45 | Application monitoring 45 | 16#9E61 = 40545 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM46 | Application monitoring 46 | 16#9E62 = 40546 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM47 | Application monitoring 47 | 16#9E63 = 40547 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM48 | Application monitoring 48 | 16#9E64 = 40548 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
OM49 | Application monitoring 49 | 16#9E65 = 40549 |  |  |  | External Controller Application Monitoring | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
PLO1 | On lock register | 16#9E98 = 40600 |  |  |  | Actual values parameters | R/W | WORD (BitString16) | - |  |  | [On Lock Register] (PLO1) | [V0_SubmenuCabStatus] (CABS)
BWS0 | MV Mains and Inrush breaker status | 16#9E99 = 40601 |  |  |  | External Controller Function Monitoring | R/W | WORD (BitString16) | - |  |  | [MV CB Status] (BWS0) | [V0_SubmenuMainsCircuitbreaker] (CCMV)
BWS1 | Bypass drive circuit breaker status | 16#9E9A = 40602 |  |  |  | External Controller Function Monitoring | R/W | WORD (BitString16) | - |  |  | [Bypass Drive CB status] (BWS1) | [V0_SubmenuBypassCircuitbreaker] (CCB)
BWS2 | Cabinet status 1 | 16#9E9B = 40603 |  |  |  | External Controller Function Monitoring | R/W | WORD (BitString16) | -
BWS3 | Cabinet status 2 | 16#9E9C = 40604 |  |  |  | External Controller Function Monitoring | R/W | WORD (BitString16) | -
BWC1 | Cabinet Control 1 | 16#9E9E = 40606 |  |  |  | Actual values parameters | R/W | WORD (BitString16) | -
BWC2 | Cabinet Control 2 | 16#9E9F = 40607 |  |  |  | Actual values parameters | R/W | WORD (BitString16) | -
PLS0 | Cabinet switch type | 16#9EA2 = 40610 |  |  | PLS0 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [No] NO
PLI0 | QF1 circuit breaker command signal assignment | 16#9EEE = 40686 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
PLI1 | QF1 circuit breaker Tripped signal assignment | 16#9EEF = 40687 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Digital input DI55 (low level)] D55L
PLI2 | QF1 circuit breaker grounded signal assignment | 16#9EF0 = 40688 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
PLI3 | QF1 circuit breaker isolated signal assignment | 16#9EF1 = 40689 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
PLI4 | Cabinet local forward assignment | 16#9EA4 = 40612 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | Refer to programming manual
PLI5 | Cabinet local reverse assignment | 16#9EA5 = 40613 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | Refer to programming manual
PLI6 | Cabinet local Run Assign | 16#9EA6 = 40614 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | Refer to programming manual
PLI8 | Cabinet local + speed assignment | 16#9EA7 = 40615 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
PLI9 | Cabinet local - speed assignment | 16#9EA8 = 40616 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
PLIA | Inrush breaker QF91 mains feedback assignement | 16#9F1B = 40731 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
PL00 | Circuit breaker QF1 trip behavior | 16#9EF2 = 40690 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL01 | Circuit breaker QF11 trip behavior | 16#9EF3 = 40691 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL02 | Circuit breaker QF2 trip behavior | 16#9EF4 = 40692 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL03 | Circuit breaker QF3 trip behavior | 16#9EF5 = 40693 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL04 | Circuit breaker QF91 trip behavior | 16#9EF6 = 40694 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL05 | Response to fan cooling error | 16#9EB6 = 40630 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL06 | Response to fan supply error | 16#9EB7 = 40631 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL07 | Response to auxiliary supply error | 16#9EBB = 40635 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL08 | Response to cabinet overheat | 16#9EBC = 40636 |  |  | PL00 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Error] FLT
PL09 | Local 2-wire type | 16#9EA9 = 40617 |  |  | TCT | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Transition] TRN
PL10 | Local 2/3-wire control | 16#9EAA = 40618 |  |  | TCC | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [2-wire control] 2C
CMDS | Cabinet switch status | 16#9EAB = 40619 |  |  | CMDS | Actual values parameters | R | WORD (Enumeration) | - |  |  | [Cabinet Switch Status] (CMDS) | [V0_SubmenuCabStatus] (CABS)
ERRQ | Event recorder activation | 16#4025 = 16421 | 16#2086/16 | 16#B3/01/16 = 179/01/22 |  | Event Recorder | R/W | WORD (BitString16) | -
ERDS | Event recorder drive status | 16#401A = 16410 | 16#2086/B | 16#B3/01/0B = 179/01/11 |  | Event Recorder | R | WORD (BitString16) | -
ERHS | Event recorder HMI status | 16#401B = 16411 | 16#2086/C | 16#B3/01/0C = 179/01/12 |  | Event Recorder | R/W | WORD (BitString16) | -
ERPE | Event recorder period | 16#401C = 16412 | 16#2086/D | 16#B3/01/0D = 179/01/13 |  | Event Recorder | R/W | UINT (Unsigned16) | 1 | 15 | 1 ... 65535
ERC1 | Event recorder context 1 | 16#401D = 16413 | 16#2086/E | 16#B3/01/0E = 179/01/14 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Mains voltage] ULN
ERC2 | Event recorder context 2 | 16#401E = 16414 | 16#2086/F | 16#B3/01/0F = 179/01/15 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Mains current] ILN
ERC3 | Event recorder context 3 | 16#401F = 16415 | 16#2086/10 | 16#B3/01/10 = 179/01/16 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Reference frequency before ramp] FRH
ERC4 | Event recorder context 4 | 16#4020 = 16416 | 16#2086/11 | 16#B3/01/11 = 179/01/17 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Motor frequency] RFR
ERC5 | Event recorder context 5 | 16#4021 = 16417 | 16#2086/12 | 16#B3/01/12 = 179/01/18 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Motor current] LCR
ERC6 | Event recorder context 6 | 16#4022 = 16418 | 16#2086/13 | 16#B3/01/13 = 179/01/19 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Motor torque] OTR
ERC7 | Event recorder context 7 | 16#4023 = 16419 | 16#2086/14 | 16#B3/01/14 = 179/01/20 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Maximum motor thermal state] TMM
ERC8 | Event recorder context 8 | 16#4024 = 16420 | 16#2086/15 | 16#B3/01/15 = 179/01/21 | ERC | Event Recorder | R/W | WORD (Enumeration) | - | [Maximum transformer thermal state ] TTM
FTM1 | Fan Thermal Sensor 1 | 16#9F53 = 40787 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
FTM3 | Fan Thermal Sensor 3 | 16#9F55 = 40789 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
FTM2 | Fan Thermal Sensor 2 | 16#9F54 = 40788 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
FTM5 | Fan Thermal Sensor 5 | 16#9F57 = 40791 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
FTM7 | Fan Thermal Sensor 7 | 16#9F59 = 40793 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
FTM6 | Fan Thermal Sensor 6 | 16#9F58 = 40792 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
IFAB | Monitoring circuit B assignment | 16#413D = 16701 | 16#2089/2 | 16#B4/01/66 = 180/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit B Assign] (IFAB) | [Monitoring circuit B] (CMCB)
IFAC | Monitoring circuit C assignment | 16#413E = 16702 | 16#2089/3 | 16#B4/01/67 = 180/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit C Assign] (IFAC) | [Monitoring circuit C] (CMCC)
IFAA | Monitoring circuit A assignment | 16#413C = 16700 | 16#2089/1 | 16#B4/01/65 = 180/01/101 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit A Assign] (IFAA) | [Monitoring circuit A] (CMCA)
OVMA | Overmodulation activation | 16#3634 = 13876 | 16#206C/4D | 16#A6/01/4D = 166/01/77 | OVMA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Default] DEFAULT |  | [Overmodul. Activation] (OVMA) | [Motor control] (DRC)
QF16 | QF11 Opening Filter time | 16#9F11 = 40721 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF14 | QF11 Switch OFF delay | 16#9F07 = 40711 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF15 | QF11 Closing Filter time | 16#9F0C = 40716 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF12 | QF11 Open pulse time | 16#9EFD = 40701 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
PSST | Password status | 16#1F72 = 8050 | 16#2032/33 | 16#89/01/33 = 137/01/51 | PSST | Status parameters | R | WORD (Enumeration) | - |  |  | [Password status] (PSST) | [Password] (COD)
QF11 | QF11 Close pulse time | 16#9EF8 = 40696 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
M2CT | Mdb NET frames | 16#178F = 6031 | 16#201E/20 | 16#7F/01/20 = 127/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb NET frames] (M2CT) | [Modbus HMI Diag] (MDH)
CFRC | Response to cabinet circuit C error | 16#417E = 16766 | 16#2089/43 | 16#B4/01/A7 = 180/01/167 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit C ErrorResp] (CFRC) | [Cabinet circuit C] (CCMC)
FXT | M/S Local torque reference | 16#41D3 = 16851 | 16#208A/34 | 16#B5/01/34 = 181/01/52 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [M/S Local Torq Ref] (FXT) | [M/S System Display] (MSR)
FWAP | Update firmware | 16#FFD7 = 65495 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - | [No] NO |  | [Update Firmware] (FWAP) | [Firmware update] (FWUP)
THM4 | Thermal bearing 1 | 16#9ECE = 40654 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal bearing 1] (THM4) | [Motor Thermal Data] (MTHP)
BYS0 | Drive Bypass Status | 16#9F2C = 40748 |  |  | BYS0 | External Controller Function Configuration | R/W | WORD (Enumeration) | -
D54D | DI54 delay | 16#0FCC = 4044 | 16#200A/2D | 16#75/01/2D = 117/01/45 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI54 delay] (D54D) | [DI54 configuration] (DI54)
QF13 | QF11 Switch ON delay | 16#9F02 = 40706 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
FTM4 | Fan Thermal Sensor 4 | 16#9F56 = 40790 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
DLR | Download rights | 16#1F6A = 8042 | 16#2032/2B | 16#89/01/2B = 137/01/43 | DLR | Configuration and settings | R/W | WORD (Enumeration) | - | [Drive unlocked] DLR1 |  | [Download rights] (DLR) | [Password] (COD)
ETXO | Ethernet option Tx frames | 16#FBD4 = 64468 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Tx frames] (ETXO) | [Ethernet Module Diag] (MTE)
M1CT | Mdb frame number | 16#177B = 6011 | 16#201E/C | 16#7F/01/0C = 127/01/12 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb Frame Nb] (M1CT) | [Modbus network diag] (MND)
QF0S | QF1 Command State | 16#9F15 = 40725 |  |  | QF0S | External Controller Function Configuration | R/W | WORD (Enumeration) | - |  |  | [QF1 Command State] (QF0S) | [V0_SubmenuMainsCircuitbreaker] (CCMV)
ERXE | Ethernet embedded Rx frames | 16#FBA0 = 64416 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb Rx frames] (ERXE) | [Ethernet Emb Diag] (MPE)
QF03 | QF1 Switch ON delay | 16#9F01 = 40705 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF02 | QF1 Open pulse time | 16#9EFC = 40700 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF05 | QF1 Closing Filter time | 16#9F0B = 40715 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF04 | QF1 Switch OFF delay | 16#9F06 = 40710 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF06 | QF1 Opening Filter time | 16#9F10 = 40720 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
STMM | Synchro to mains monitoring | 16#41FB = 16891 | 16#208A/5C | 16#B5/01/5C = 181/01/92 | STM | Synchronization to mains monitoring | R | WORD (Enumeration) | -
TP14 | Transmit PDO1-4 | 16#32FE = 13054 | 16#2064/37 | 16#A2/01/37 = 162/01/55 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-4] (TP14) | [PDO1 image] (P01)
PSRT | Drive Systems pre-settings unlock | 16#1F7E = 8062 | 16#2032/3F | 16#89/01/3F = 137/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
CFRA | Response to cabinet circuit A error | 16#417C = 16764 | 16#2089/41 | 16#B4/01/A5 = 180/01/165 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit A ErrorResp] (CFRA) | [Cabinet circuit A] (CCMA)
CFRB | Response to cabinet circuit B error | 16#417D = 16765 | 16#2089/42 | 16#B4/01/A6 = 180/01/166 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit B ErrorResp] (CFRB) | [Cabinet circuit B ] (CCMB)
TTM | Maximum transformer thermal state | 16#9EEC = 40684 |  |  |  | External controller thermal transformer monitoring | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
TILR | Level of Lf injection for autotuning | 16#259C = 9628 | 16#2042/1D | 16#91/01/1D = 145/01/29 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 400 %
PVIS | PARAMETERS | 16#FA23 = 64035 |  |  | PVIS | Configuration and settings | R/W | WORD (Enumeration) | - | [Active parameters] ACT |  | [PARAMETERS] (PVIS) | [Visibility] (VIS)
IFMA | Monitoring circuit A error monitoring type | 16#4150 = 16720 | 16#2089/15 | 16#B4/01/79 = 180/01/121 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit A Monitor] (IFMA) | [Monitoring circuit A] (CMCA)
BYS1 | Bypass Circuit Breaker status | 16#9F2D = 40749 |  |  | BYS1 | External Controller Function Configuration | R/W | WORD (Enumeration) | -
THM7 | Thermal winding W2 | 16#9ED1 = 40657 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
SMFT | Synchro to mains error timeout | 16#41FA = 16890 | 16#208A/5B | 16#B5/01/5B = 181/01/91 |  | Synchronization to mains failure timeout | R/WS | UINT (Unsigned16) | 0.1 s | 30.0 s | 0.0 s ... 120.0 s
ARDE | Ethernet rate data | 16#FB9D = 64413 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Ethernet Rate Data] (ARDE) | [Ethernet Emb Diag] (MPE)
IFAD | Monitoring circuit D assignment | 16#413F = 16703 | 16#2089/4 | 16#B4/01/68 = 180/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit D Assign] (IFAD) | [Monitoring circuit D] (CMCD)
FWST | Firmware Update Status | 16#FFDB = 65499 |  |  | FWST | Status parameters | R | WORD (Enumeration) | - |  |  | [Firmware Update Status] (FWST) | [Firmware update diag] (FWUD)
D58D | DI58 delay | 16#0FD0 = 4048 | 16#200A/31 | 16#75/01/31 = 117/01/49 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI58 delay] (D58D) | [DI58 configuration] (DI58)
TT1M | Transformer cabinet temperature 1 | 16#9EC1 = 40641 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Transfo Cab Temp 1] (TT1M) | [Power Stage Data] (TTHP)
RHOC | Liquid density used to characterize pump | 16#3D9C = 15772 | 16#207F/49 | 16#AF/01/AD = 175/01/173 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 kg/m³ | 1000 kg/m³ | 100 kg/m³ ... 10000 kg/m³ | [Pump Liquid Density] (RHOC) | [Pump characteristics] (PCR)
SMMT | Synchro to mains magnitude threshold | 16#41F9 = 16889 | 16#208A/5A | 16#B5/01/5A = 181/01/90 |  | Synchronization to mains magnitude threshold | R/WS | UINT (Unsigned16) | 0.1 V | 6.0 V | 0.0 V ... 100.0 V
THMA | Thermal bearing 4 | 16#9ED4 = 40660 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal bearing 4] (THMA) | [Motor Thermal Data] (MTHP)
TLFR | Autotuning flux frequency | 16#267A = 9850 | 16#2044/33 | 16#92/01/33 = 146/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 300.0 Hz | [Autotuning Flux Freq] (TLFR) | [Autotuning flux] (TUNR)
FPM2 | Fan Pressure Sensor 2 | 16#9F5B = 40795 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
FTTS | nothing | 16#FA10 = 64016 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 50 | 0 ... 100000
BYP1 | Bypass PoC Max Number | 16#9B42 = 39746 |  |  |  | Power cell configuration | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 4
PKVS | Package version | 16#FFD3 = 65491 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Package Version] (PKVS) | [Package version] (PFV)
QF1S | QF11 Command State | 16#9F16 = 40726 |  |  | QF0S | External Controller Function Configuration | R/W | WORD (Enumeration) | - |  |  | [QF11 Command State] (QF1S) | [V0_SubmenuBypassCircuitbreaker] (CCB)
SDFT | Synchro to drive error timeout | 16#4401 = 17409 | 16#2090/A | 16#B8/01/0A = 184/01/10 |  | Synchronization to drive failure timeout | R/WS | UINT (Unsigned16) | 0.1 s | 30.0 s | 0.0 s ... 120.0 s
R60S | R60 Active at | 16#10CC = 4300 | 16#200D/1 | 16#76/01/65 = 118/01/101 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R60 Active at] (R60S) | [R60 configuration] (R60)
R60D | R60 Delay time | 16#10CD = 4301 | 16#200D/2 | 16#76/01/66 = 118/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R60 Delay time] (R60D) | [R60 configuration] (R60)
TT2M | Transformer cabinet temperature 2 | 16#9EC5 = 40645 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Transfo Cab Temp 2] (TT2M) | [Power Stage Data] (TTHP)
LFR1 | Modbus reference frequency | 16#2149 = 8521 | 16#2037/16 | 16#8B/01/7A = 139/01/122 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -3276.7 Hz ... 3276.7 Hz | [Modbus Ref Freq] (LFR1) | [Freq. ref. word map] (RWI)
LFR2 | CANopen reference frequency | 16#214A = 8522 | 16#2037/17 | 16#8B/01/7B = 139/01/123 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -3276.7 Hz ... 3276.7 Hz | [CAN Ref Freq] (LFR2) | [Freq. ref. word map] (RWI)
LFR3 | Communication module reference frequency | 16#214B = 8523 | 16#2037/18 | 16#8B/01/7C = 139/01/124 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -3276.7 Hz ... 3276.7 Hz | [Com Module Ref Freq] (LFR3) | [Freq. ref. word map] (RWI)
LFR5 | Embedded ethernet reference frequency | 16#214D = 8525 | 16#2037/1A | 16#8B/01/7E = 139/01/126 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -3276.7 Hz ... 3276.7 Hz | [Ethernet Embd Ref Freq] (LFR5) | [Freq. ref. word map] (RWI)
LFR6 | Modbus 2 reference frequency | 16#214E = 8526 | 16#2037/1B | 16#8B/01/7F = 139/01/127 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -3276.7 Hz ... 3276.7 Hz | [Modbus 2 Ref Freq] (LFR6) | [Freq. ref. word map] (RWI)
LFR7 | Controller embedded reference frequency | 16#214F = 8527 | 16#2037/1C | 16#8B/01/80 = 139/01/128 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -3276.7 Hz ... 3276.7 Hz | [Controller Embd Ref] (LFR7) | [Freq. ref. word map] (RWI)
SDMB | Synchro to drive magnitude bandwidth | 16#43FC = 17404 | 16#2090/5 | 16#B8/01/05 = 184/01/05 |  | Synchronization to drive magnitude bandwidth | R/WS | UINT (Unsigned16) | 0.01 Hz | 0.10 Hz | 0.01 Hz ... 1.00 Hz
SDMD | Synchro to drive magnitude damping coefficient | 16#4406 = 17414 | 16#2090/F | 16#B8/01/0F = 184/01/15 |  | Synchronization to drive magnitude damping factor | R/WS | UINT (Unsigned16) | 0.01 | 1.50 | 0.00 ... 10.00
R64S | R64 Active at | 16#10D8 = 4312 | 16#200D/D | 16#76/01/71 = 118/01/113 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R64 Active at] (R64S) | [R64 configuration] (R64)
POEF | POEx Digital Input state | 16#9F36 = 40758 |  |  |  | Status parameters | R | WORD (BitString16) | -
THT4 | Thermal error level for bearing 2 | 16#9EDC = 40668 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 115 °C | 0 °C ... 2500 °C
POES | Power Output Enable function status | 16#9F35 = 40757 |  |  | POES | Power Output Enable function | R | WORD (Enumeration) | -
EERO | Ethernet option error frames | 16#FBD6 = 64470 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt error frames] (EERO) | [Ethernet Module Diag] (MTE)
TS1U | Thermal transformer Secondary U1 | 16#9F39 = 40761 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer Secondary U1] (TS1U) | [Power Stage Data] (TTHP)
TS1V | Thermal transformer Secondary V1 | 16#9F3A = 40762 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer Secondary V1] (TS1V) | [Power Stage Data] (TTHP)
TS1W | Thermal transformer Secondary W1 | 16#9F3B = 40763 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer Secondary W1] (TS1W) | [Power Stage Data] (TTHP)
R64D | R64 Delay time | 16#10D9 = 4313 | 16#200D/E | 16#76/01/72 = 118/01/114 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R64 Delay time] (R64D) | [R64 configuration] (R64)
STO | Torque/I limit. timeout | 16#2419 = 9241 | 16#203E/2A | 16#8F/01/2A = 143/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 1000 ms | 0 ms ... 9999 ms | [Trq/I Limit Timeout] (STO) | [Torque limitation] (TOL) [Torque or I limit detect] (TID)
NMTS | Canopen NMT state | 16#17A9 = 6057 | 16#201E/3A | 16#7F/01/3A = 127/01/58 | NMTS | Status parameters | R | WORD (Enumeration) | - |  |  | [Canopen NMT state] (NMTS) | [CANopen map] (CNM)
EMDT | Energy Dashboard | 16#FA31 = 64049 |  |  | EMDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Instantaneous kW trend] CVE
D51D | DI51 delay | 16#0FC9 = 4041 | 16#200A/2A | 16#75/01/2A = 117/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI51 delay] (D51D) | [DI51 configuration] (DI51)
TFDA | Motor winding A delay after Run | 16#416B = 16747 | 16#2089/30 | 16#B4/01/94 = 180/01/148 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorWinding A Delay] (TFDA) | [Motor winding A] (CTIA)
SDST | Synchro to drive stabilization time | 16#43FE = 17406 | 16#2090/7 | 16#B8/01/07 = 184/01/07 |  | Synchronization to drive stabilization time | R/WS | UINT (Unsigned16) | 0.1 s | 2.0 s | 0.1 s ... 120.0 s
THM6 | Thermal winding V2 | 16#9ED0 = 40656 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal winding V2] (THM6) | [Motor Thermal Data] (MTHP)
THM3 | Thermal winding W1 | 16#9ECD = 40653 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal winding W1] (THM3) | [Motor Thermal Data] (MTHP)
THM2 | Thermal winding V1 | 16#9ECC = 40652 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal winding V1] (THM2) | [Motor Thermal Data] (MTHP)
THM1 | Thermal winding U1 | 16#9ECB = 40651 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal winding U1] (THM1) | [Motor Thermal Data] (MTHP)
THM9 | Thermal bearing 3 | 16#9ED3 = 40659 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal bearing 3] (THM9) | [Motor Thermal Data] (MTHP)
THM8 | Thermal bearing 2 | 16#9ED2 = 40658 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal bearing 2] (THM8) | [Motor Thermal Data] (MTHP)
R61S | R61 Active at | 16#10CF = 4303 | 16#200D/4 | 16#76/01/68 = 118/01/104 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R61 Active at] (R61S) | [R61 configuration] (R61)
R61D | R61 Delay time | 16#10D0 = 4304 | 16#200D/5 | 16#76/01/69 = 118/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R61 Delay time] (R61D) | [R61 configuration] (R61)
R61H | R61 Holding time | 16#10D1 = 4305 | 16#200D/6 | 16#76/01/6A = 118/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R61 Holding time] (R61H) | [R61 configuration] (R61)
RP24 | Receive PDO2-4 | 16#32E0 = 13024 | 16#2064/19 | 16#A2/01/19 = 162/01/25 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-4] (RP24) | [PDO2 image] (P02)
RP21 | Receive PDO2-1 | 16#32DD = 13021 | 16#2064/16 | 16#A2/01/16 = 162/01/22 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-1] (RP21) | [PDO2 image] (P02)
RP22 | Receive PDO2-2 | 16#32DE = 13022 | 16#2064/17 | 16#A2/01/17 = 162/01/23 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-2] (RP22) | [PDO2 image] (P02)
RP23 | Receive PDO2-3 | 16#32DF = 13023 | 16#2064/18 | 16#A2/01/18 = 162/01/24 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-3] (RP23) | [PDO2 image] (P02)
CMD6 | Modbus 2 command register | 16#2144 = 8516 | 16#2037/11 | 16#8B/01/75 = 139/01/117 |  | Configuration and settings | R/W | WORD (BitString16) | - |  |  | [Modbus 2 Cmd] (CMD6) | [Command word image] (CWI)
CMD7 | Controller Embedded command register | 16#2145 = 8517 | 16#2037/12 | 16#8B/01/76 = 139/01/118 |  | Configuration and settings | R | WORD (BitString16) | - |  |  | [Controller Embd Cmd] (CMD7) | [Command word image] (CWI)
BYC4 | Bypass drive switch assign | 16#9F28 = 40744 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
CMDC | Command channel | 16#FA28 = 64040 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (CMDC) | [Communication map] (CMM)
DOFC | Downward optical error counter | 16#9B49 = 39753 |  |  |  | Power cell configuration | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
OTRN | Motor Torque in Nm | 16#0C90 = 3216 | 16#2002/11 | 16#71/01/11 = 113/01/17 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor Torque (Nm)] (OTRN) | [Motor parameters] (MMO)
SMST | Synchro to mains stabilization time | 16#41F6 = 16886 | 16#208A/57 | 16#B5/01/57 = 181/01/87 |  | Synchronization to mains stabilization time | R/WS | UINT (Unsigned16) | 0.1 s | 2.0 s | 0.1 s ... 120.0 s
TFDB | Motor winding B delay after Run | 16#416C = 16748 | 16#2089/31 | 16#B4/01/95 = 180/01/149 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorWinding B Delay] (TFDB) | [Motor winding B] (CTIB)
TFDC | Motor bearing A delay after Run | 16#416D = 16749 | 16#2089/32 | 16#B4/01/96 = 180/01/150 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorBearing A Delay] (TFDC) | [Motor bearing A] (CTIC)
TFDD | Motor bearing B delay after Run | 16#416E = 16750 | 16#2089/33 | 16#B4/01/97 = 180/01/151 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorBearing B Delay] (TFDD) | [Motor bearing B] (CTID)
RP33 | Receive PDO3-3 | 16#32CB = 13003 | 16#2064/4 | 16#A2/01/04 = 162/01/04 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-3] (RP33) | [PDO3 image] (P03)
RP32 | Receive PDO3-2 | 16#32CA = 13002 | 16#2064/3 | 16#A2/01/03 = 162/01/03 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-2] (RP32) | [PDO3 image] (P03)
SMAS | Synchro to mains anti-start delay | 16#41FE = 16894 | 16#208A/5F | 16#B5/01/5F = 181/01/95 |  | Synchronization to mains load time | R/WS | UINT (Unsigned16) | 0.1 s | 1.0 s | 0.0 s ... 100.0 s
SMAP | Synchro to mains angle phase-shift | 16#41F3 = 16883 | 16#208A/54 | 16#B5/01/54 = 181/01/84 |  | Synchronization to mains angle phase-shift | R/W | INT (Signed16) | 0.01 ° | 0.00 ° | -180.00 ° ... 180.00 °
SMAT | Synchro to mains angle threshold | 16#41F8 = 16888 | 16#208A/59 | 16#B5/01/59 = 181/01/89 |  | Synchronization to mains angle threshold | R/WS | UINT (Unsigned16) | 0.01 ° | 1.50 ° | 0.00 ° ... 180.00 °
LAC | Access Level | 16#0BBE = 3006 | 16#2000/7 | 16#70/01/07 = 112/01/07 | LAC | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard access] STD |  | [Access Level] (LAC) | [My preferences] (MYP)
SMAB | Synchro to mains angle bandwidth | 16#41F2 = 16882 | 16#208A/53 | 16#B5/01/53 = 181/01/83 |  | Synchronization to mains angle bandwidth | R/WS | UINT (Unsigned16) | 0.01 Hz | 0.15 Hz | 0.01 Hz ... 1.00 Hz
QF3S | QF3 Command State | 16#9F18 = 40728 |  |  | QF0S | External Controller Function Configuration | R/W | WORD (Enumeration) | - |  |  | [QF3 Command State] (QF3S) | [V0_SubmenuBypassCircuitbreaker] (CCB)
QF55 | QF5 Closing Filter time | 16#9F67 = 40807 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
R62D | R62 Delay time | 16#10D3 = 4307 | 16#200D/8 | 16#76/01/6C = 118/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R62 Delay time] (R62D) | [R62 configuration] (R62)
R62H | R62 Holding time | 16#10D4 = 4308 | 16#200D/9 | 16#76/01/6D = 118/01/109 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R62 Holding time] (R62H) | [R62 configuration] (R62)
COM1 | Modbus com. status | 16#FA2F = 64047 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM1) | [Modbus Fieldbus] (MD1)
COM2 | Mdb com stat | 16#FA30 = 64048 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM2) | [Modbus HMI] (MD2)
NSV | Number of power on | 16#35E0 = 13792 | 16#206B/5D | 16#A5/01/C1 = 165/01/193 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Nb of MV Power On] (NSV) | [Counter Management] (ELT)
D64D | DI64 delay | 16#0FD6 = 4054 | 16#200A/37 | 16#75/01/37 = 117/01/55 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI64 delay] (D64D) | [DI64 configuration] (DI64)
TLNC | Overload Nominal Current | 16#1B7E = 7038 | 16#2028/27 | 16#84/01/27 = 132/01/39 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535
IFMD | Monitoring circuit D error monitoring type | 16#4153 = 16723 | 16#2089/18 | 16#B4/01/7C = 180/01/124 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit D Monitor] (IFMD) | [Monitoring circuit D] (CMCD)
REC1 | RX Error Counter | 16#17AB = 6059 | 16#201E/3C | 16#7F/01/3C = 127/01/60 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [RX Error Counter] (REC1) | [CANopen map] (CNM)
R62S | R62 Active at | 16#10D2 = 4306 | 16#200D/7 | 16#76/01/6B = 118/01/107 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R62 Active at] (R62S) | [R62 configuration] (R62)
BYP2 | Bypass PoC Reset | 16#9B43 = 39747 |  |  | BYP2 | Power cell configuration | R/WS | WORD (Enumeration) | - | [Never] NEVER
QF52 | QF5 Open pulse time | 16#9F64 = 40804 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF51 | QF5 Close pulse time | 16#9F63 = 40803 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
SYTM | Synchro to mains selection | 16#41F0 = 16880 | 16#208A/51 | 16#B5/01/51 = 181/01/81 | PSLIN | Synchronization to mains selection | R/WS | WORD (Enumeration) | - | [Not assigned] NO
R63 | R63 Assignment | 16#13B3 = 5043 | 16#2014/2C | 16#7A/01/2C = 122/01/44 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R63 Assignment] (R63) | [R63 configuration] (R63)
R62 | R62 Assignment | 16#13B2 = 5042 | 16#2014/2B | 16#7A/01/2B = 122/01/43 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R62 Assignment] (R62) | [R62 configuration] (R62)
R61 | R61 Assignment | 16#13B1 = 5041 | 16#2014/2A | 16#7A/01/2A = 122/01/42 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R61 Assignment] (R61) | [R61 configuration] (R61)
R60 | R60 Assignment | 16#13B0 = 5040 | 16#2014/29 | 16#7A/01/29 = 122/01/41 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [R60 Assignment] (R60) | [R60 configuration] (R60)
R67 | R67 Assignment | 16#13B7 = 5047 | 16#2014/30 | 16#7A/01/30 = 122/01/48 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R67 Assignment] (R67) | [R67 configuration] (R67)
R66 | R66 Assignment | 16#13B6 = 5046 | 16#2014/2F | 16#7A/01/2F = 122/01/47 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R66 Assignment] (R66) | [R66 configuration] (R66)
R65 | R65 Assignment | 16#13B5 = 5045 | 16#2014/2E | 16#7A/01/2E = 122/01/46 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R65 Assignment] (R65) | [R65 configuration] (R65)
R64 | R64 Assignment | 16#13B4 = 5044 | 16#2014/2D | 16#7A/01/2D = 122/01/45 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R64 Assignment] (R64) | [R64 configuration] (R64)
TEC1 | TX Error Counter | 16#17AA = 6058 | 16#201E/3B | 16#7F/01/3B = 127/01/59 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [TX Error Counter] (TEC1) | [CANopen map] (CNM)
IPAE | iPar service status | 16#FB17 = 64279 |  |  | IPAE | Configuration and settings | R/W | WORD (Enumeration) | - | [Idle State] IDLE |  | [iPar Status] (IPAE) | [PROFINET DIAG] (PRN)
IPAT | iPar autosave timer | 16#FB16 = 64278 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 9999 | [iPar Autosave Timer] (IPAT) | [Profinet] (PNC)
IPAV | iPar service activation | 16#FB12 = 64274 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Activation] (IPAV) | [Profinet] (PNC)
IPAS | iPar autosave activation | 16#FB13 = 64275 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Autosave Act] (IPAS) | [Profinet] (PNC)
IQM | Motor current Iq | 16#25B7 = 9655 | 16#2042/38 | 16#91/01/38 = 145/01/56 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor Current Iq] (IQM) | [Motor parameters] (MMO) [data] (MTD)
R63S | R63 Active at | 16#10D5 = 4309 | 16#200D/A | 16#76/01/6E = 118/01/110 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R63 Active at] (R63S) | [R63 configuration] (R63)
R63H | R63 Holding time | 16#10D7 = 4311 | 16#200D/C | 16#76/01/70 = 118/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R63 Holding time] (R63H) | [R63 configuration] (R63)
R63D | R63 Delay time | 16#10D6 = 4310 | 16#200D/B | 16#76/01/6F = 118/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R63 Delay time] (R63D) | [R63 configuration] (R63)
KLCK | Display Terminal locked | 16#FA12 = 64018 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 5 min | 0 min ... 10 min | [Display Terminal locked] (KLCK) | [LCD settings] (CNL)
PMDT | Pump Screen | 16#FA57 = 64087 |  |  | PMDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Parameters List] NO
POCS | Power cell selection | 16#9B3C = 39740 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1 | 1 ... 36 | [Power Cell Selection] (POCS) | [Power Cell Data] (POCM)
FPM7 | Fan Pressure Sensor 7 | 16#9F60 = 40800 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
FPM1 | Fan Pressure Sensor 1 | 16#9F5A = 40794 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
TP21 | Transmit PDO2-1 | 16#32E7 = 13031 | 16#2064/20 | 16#A2/01/20 = 162/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-1] (TP21) | [PDO2 image] (P02)
M1EC | Mdb NET CRC errors | 16#177A = 6010 | 16#201E/B | 16#7F/01/0B = 127/01/11 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mb NET CRC errors] (M1EC) | [Modbus network diag] (MND)
SDTL | Synchro to drive load time | 16#4404 = 17412 | 16#2090/D | 16#B8/01/0D = 184/01/13 |  | Synchronization to drive load time | R/WS | UINT (Unsigned16) | 0.1 s | 2.0 s | 0.0 s ... 100.0 s
VLIM | Output voltage limitation | 16#3637 = 13879 | 16#206C/50 | 16#A6/01/50 = 166/01/80 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | VLIM_DEFAULT | 0 V ... 65535 V | [Output Voltage Limit] (VLIM) | [Motor control] (DRC)
TS2U | Thermal transformer Secondary U2 | 16#9F3C = 40764 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer Secondary U2] (TS2U) | [Power Stage Data] (TTHP)
TS2W | Thermal transformer Secondary W2 | 16#9F3E = 40766 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer Secondary W2] (TS2W) | [Power Stage Data] (TTHP)
TS2V | Thermal transformer Secondary V2 | 16#9F3D = 40765 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer Secondary V2] (TS2V) | [Power Stage Data] (TTHP)
SMMV | Synchro to mains magnitude Vlim coefficient | 16#41F5 = 16885 | 16#208A/56 | 16#B5/01/56 = 181/01/86 |  | Synchronization to mains magnitude Vlim coefficient | R/WS | UINT (Unsigned16) | 0.1 | 1.0 | 0.1 ... 5.0
SMMD | Synchro to mains magnitude damping coefficient | 16#4405 = 17413 | 16#2090/E | 16#B8/01/0E = 184/01/14 |  | Synchronization to mains magnitude damping factor | R/WS | UINT (Unsigned16) | 0.01 | 1.50 | 0.00 ... 10.00
SMMB | Synchro to mains magnitude bandwidth | 16#41F4 = 16884 | 16#208A/55 | 16#B5/01/55 = 181/01/85 |  | Synchronization to mains magnitude bandwidth | R/WS | UINT (Unsigned16) | 0.01 Hz | 0.10 Hz | 0.01 Hz ... 1.00 Hz
SMMO | Synchro to drive magnitude offset | 16#41FC = 16892 | 16#208A/5D | 16#B5/01/5D = 181/01/93 |  | Synchronization to mains magnitude offset | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 100.0 V
WPXF | Pump operating point filter | 16#3EBC = 16060 | 16#2082/3D | 16#B1/01/3D = 177/01/61 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.00 s ... 60.00 s | [Pump Op Point Filter] (WPXF) | [Pump characteristics] (PCR) [Settings] (SET) [Flow estimation] (SFE)
R64H | R64 Holding time | 16#10DA = 4314 | 16#200D/F | 16#76/01/73 = 118/01/115 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R64 Holding time] (R64H) | [R64 configuration] (R64)
CFDC | Cabinet circuit C delay after Run | 16#416A = 16746 | 16#2089/2F | 16#B4/01/93 = 180/01/147 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit C Delay] (CFDC) | [Cabinet circuit C] (CCMC)
CFDB | Cabinet circuit B delay after Run | 16#4169 = 16745 | 16#2089/2E | 16#B4/01/92 = 180/01/146 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit B Delay] (CFDB) | [Cabinet circuit B ] (CCMB)
CFDA | Cabinet circuit A delay after Run | 16#4168 = 16744 | 16#2089/2D | 16#B4/01/91 = 180/01/145 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit A Delay] (CFDA) | [Cabinet circuit A] (CCMA)
QF25 | QF2 Closing Filter time | 16#9F0D = 40717 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
BWS4 | Bypass drive circuit breaker status 2 | 16#9E9D = 40605 |  |  |  | External controller function monitoring | R/W | WORD (BitString16) | -
D53D | DI53 delay | 16#0FCB = 4043 | 16#200A/2C | 16#75/01/2C = 117/01/44 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI53 delay] (D53D) | [DI53 configuration] (DI53)
IM00 | IP Mode Ethernet Embd | 16#FB90 = 64400 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [IP Mode Ether. Embd] (IM00) | [Embd Eth Config] (ETE)
RP34 | Receive PDO3-4 | 16#32CC = 13004 | 16#2064/5 | 16#A2/01/05 = 162/01/05 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-4] (RP34) | [PDO3 image] (P03)
RP14 | Receive PDO1-4 | 16#32F4 = 13044 | 16#2064/2D | 16#A2/01/2D = 162/01/45 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-4] (RP14) | [PDO1 image] (P01)
RP11 | Receive PDO1-1 | 16#32F1 = 13041 | 16#2064/2A | 16#A2/01/2A = 162/01/42 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-1] (RP11) | [PDO1 image] (P01)
RP13 | Receive PDO1-3 | 16#32F3 = 13043 | 16#2064/2C | 16#A2/01/2C = 162/01/44 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-3] (RP13) | [PDO1 image] (P01)
RP12 | Receive PDO1-2 | 16#32F2 = 13042 | 16#2064/2B | 16#A2/01/2B = 162/01/43 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-2] (RP12) | [PDO1 image] (P01)
RP31 | Receive PDO3-1 | 16#32C9 = 13001 | 16#2064/2 | 16#A2/01/02 = 162/01/02 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-1] (RP31) | [PDO3 image] (P03)
OD2T | Controller inside type | 16#0F32 = 3890 | 16#2008/5B | 16#74/01/5B = 116/01/91 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Controller Inside Type] (OD2T) | [PLC Inside Data] (PLCI)
D62D | DI62 delay | 16#0FD4 = 4052 | 16#200A/35 | 16#75/01/35 = 117/01/53 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI62 delay] (D62D) | [DI62 configuration] (DI62)
BYPM | Bypass PoC Reset Assign | 16#9B44 = 39748 |  |  | PSLIN | Power cell configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
TP2M | Thermal winding MAX(TP2U, TP2V, TP2W) | 16#9F4E = 40782 |  |  |  | External controller thermal transformer monitoring | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
ETXE | Ethernet embedded Tx frames | 16#FBA2 = 64418 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb Tx frames] (ETXE) | [Ethernet Emb Diag] (MPE)
TP2U | Thermal transformer U2 | 16#9EC6 = 40646 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer U2] (TP2U) | [Power Stage Data] (TTHP)
TLNL | Overload Nominal Current Ratio | 16#1B7F = 7039 | 16#2028/28 | 16#84/01/28 = 132/01/40 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 120 % | 100 % ... 200 %
TTO2 | Modbus 2 timeout | 16#1789 = 6025 | 16#201E/1A | 16#7F/01/1A = 127/01/26 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Modbus 2 Timeout] (TTO2) | [Modbus HMI] (MD2)
D56D | DI56 delay | 16#0FCE = 4046 | 16#200A/2F | 16#75/01/2F = 117/01/47 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI56 delay] (D56D) | [DI56 configuration] (DI56)
CFAC | Cabinet circuit C assignment | 16#4142 = 16706 | 16#2089/7 | 16#B4/01/6B = 180/01/107 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit C Assign] (CFAC) | [Cabinet circuit C] (CCMC)
SDAD | Synchro to drive angle damping coefficient | 16#43F9 = 17401 | 16#2090/2 | 16#B8/01/02 = 184/01/02 |  | Synchronization to drive angle damping factor | R/WS | UINT (Unsigned16) | 0.01 | 1.50 | 0.00 ... 10.00
SDAB | Synchro to drive angle bandwidth | 16#43FA = 17402 | 16#2090/3 | 16#B8/01/03 = 184/01/03 |  | Synchronization to drive angle bandwidth | R/WS | UINT (Unsigned16) | 0.01 Hz | 0.15 Hz | 0.01 Hz ... 1.00 Hz
SDAT | Synchro to drive angle threshold | 16#43FF = 17407 | 16#2090/8 | 16#B8/01/08 = 184/01/08 |  | Synchronization to drive angle threshold | R/WS | UINT (Unsigned16) | 0.01 ° | 1.50 ° | 0.00 ° ... 180.00 °
SDAP | Synchro to drive angle phase-shift | 16#43FB = 17403 | 16#2090/4 | 16#B8/01/04 = 184/01/04 |  | Synchronization to drive angle phase-shift | R/W | INT (Signed16) | 0.01 ° | 0.00 ° | -180.00 ° ... 180.00 °
CFMA | Cabinet circuit A monitoring type | 16#4154 = 16724 | 16#2089/19 | 16#B4/01/7D = 180/01/125 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit A Monitor] (CFMA) | [Cabinet circuit A] (CCMA)
OCT6 | Fan thermal sensor monitoring register | 16#9F51 = 40785 |  |  |  | External controller thermal transformer monitoring | R | WORD (BitString16) | -
OCT7 | Fan pressure sensor monitoring register | 16#9F52 = 40786 |  |  |  | External controller thermal transformer monitoring | R | WORD (BitString16) | -
OCT5 | PLC module configuration register | 16#9F38 = 40760 |  |  |  | External controller thermal transformer monitoring | R | WORD (BitString16) | -
OCT2 | Cabinet transformer PT100 usage | 16#9EC0 = 40640 |  |  |  | External controller thermal transformer monitoring | R | WORD (BitString16) | - |  |  | [Cab Transfo PT100] (OCT2) | [Power Stage Data] (TTHP)
OCT3 | Cabinet configuration register | 16#9EDD = 40669 |  |  |  | External controller thermal motor monitoring | R/W | WORD (BitString16) | -
AV1A | AIV1 assignment | 16#12FD = 4861 | 16#2012/3E | 16#79/01/3E = 121/01/62 | CSA | Configuration and settings | R | WORD (Enumeration) | - |  |  | [AIV1 assignment] (AV1A) | [AIV1 assignment] (AV1A) [Virtual AI1] (AV1)
NBRP | Number of RX PDO | 16#330F = 13071 | 16#2064/48 | 16#A2/01/48 = 162/01/72 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of RX PDO] (NBRP) | [CANopen map] (CNM)
OD1T | HMI panel type | 16#0F28 = 3880 | 16#2008/51 | 16#74/01/51 = 116/01/81 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [HMI Panel Type] (OD1T) | [HMI Panel Status] (HMIP)
D63D | DI63 delay | 16#0FD5 = 4053 | 16#200A/36 | 16#75/01/36 = 117/01/54 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI63 delay] (D63D) | [DI63 configuration] (DI63)
R65S | R65 Active at | 16#10DB = 4315 | 16#200D/10 | 16#76/01/74 = 118/01/116 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R65 Active at] (R65S) | [R65 configuration] (R65)
R65H | R65 Holding time | 16#10DD = 4317 | 16#200D/12 | 16#76/01/76 = 118/01/118 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R65 Holding time] (R65H) | [R65 configuration] (R65)
R65D | R65 Delay time | 16#10DC = 4316 | 16#200D/11 | 16#76/01/75 = 118/01/117 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R65 Delay time] (R65D) | [R65 configuration] (R65)
IM10 | Ethernet option IP mode | 16#FBC2 = 64450 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [ETH Option IP Mode] (IM10) | [Eth Module Config] (ETO)
BYP0 | Bypass PoC Config | 16#9B41 = 39745 |  |  | BYP0 | Power cell configuration | R/WS | WORD (Enumeration) | - | [Not configured] NO
THT1 | Thermal error level for winding 1 | 16#9ED9 = 40665 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 150 °C | 0 °C ... 2500 °C
R60H | R60 Holding time | 16#10CE = 4302 | 16#200D/3 | 16#76/01/67 = 118/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R60 Holding time] (R60H) | [R60 configuration] (R60)
OCT1 | Motor PT100 usage | 16#9ECA = 40650 |  |  |  | External controller thermal motor monitoring | R | WORD (BitString16) | - |  |  | [Motor PT100 Usage] (OCT1) | [Motor Thermal Data] (MTHP)
BYC6 | Drive bypass delay after error | 16#9F2B = 40747 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 6553.5 s
BYC5 | Bypass transfer Drive to DOL on error | 16#9F29 = 40745 |  |  | PSLIN | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Not assigned] NO
BYC3 | Drive bypass command word | 16#445D = 17501 | 16#2091/2 | 16#B8/01/66 = 184/01/102 |  | External Controller Function Configuration | R/W | WORD (BitString16) | - | 0
BYC0 | Drive Bypass Type | 16#9F24 = 40740 |  |  | BYC0 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Bypass drive not configured] NO
BYC1 | Drive Bypass Config | 16#9F25 = 40741 |  |  |  | External Controller Function Configuration | R/W | WORD (BitString16) | - | 3
TFRA | Response to motor winding A error | 16#417F = 16767 | 16#2089/44 | 16#B4/01/A8 = 180/01/168 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorWinding A ErrorResp] (TFRA) | [Motor winding A] (CTIA)
TFRC | Response to motor bearing A error | 16#4181 = 16769 | 16#2089/46 | 16#B4/01/AA = 180/01/170 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorBearing A ErrorResp] (TFRC) | [Motor bearing A] (CTIC)
TFRD | Response to motor bearing B error | 16#4182 = 16770 | 16#2089/47 | 16#B4/01/AB = 180/01/171 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorBearing B ErrorResp] (TFRD) | [Motor bearing B] (CTID)
D52D | DI52 delay | 16#0FCA = 4042 | 16#200A/2B | 16#75/01/2B = 117/01/43 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI52 delay] (D52D) | [DI52 configuration] (DI52)
QF01 | QF1 Close pulse time | 16#9EF7 = 40695 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
PKTP | Package type | 16#FFD4 = 65492 |  |  | PKTP | Status parameters | R | WORD (Enumeration) | - |  |  | [Package Type] (PKTP) | [Package version] (PFV)
TMM | Maximum motor thermal state | 16#9EED = 40685 |  |  |  | External controller thermal motor configuration | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
R67D | R67 Delay time | 16#10E2 = 4322 | 16#200D/17 | 16#76/01/7B = 118/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R67 Delay time] (R67D) | [R67 configuration] (R67)
R67H | R67 Holding time | 16#10E3 = 4323 | 16#200D/18 | 16#76/01/7C = 118/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R67 Holding time] (R67H) | [R67 configuration] (R67)
TP1W | Thermal transformer W1 | 16#9EC4 = 40644 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer W1] (TP1W) | [Power Stage Data] (TTHP)
TP1V | Thermal transformer V1 | 16#9EC3 = 40643 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer V1] (TP1V) | [Power Stage Data] (TTHP)
TP1U | Thermal transformer U1 | 16#9EC2 = 40642 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer U1] (TP1U) | [Power Stage Data] (TTHP)
TP1M | Thermal winding MAX(TP1U, TP1V, TP1W) | 16#9F4D = 40781 |  |  |  | External controller thermal cabinet monitoring | R | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C
TP13 | Transmit PDO1-3 | 16#32FD = 13053 | 16#2064/36 | 16#A2/01/36 = 162/01/54 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-3] (TP13) | [PDO1 image] (P01)
TP12 | Transmit PDO1-2 | 16#32FC = 13052 | 16#2064/35 | 16#A2/01/35 = 162/01/53 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-2] (TP12) | [PDO1 image] (P01)
TP11 | Transmit PDO1-1 | 16#32FB = 13051 | 16#2064/34 | 16#A2/01/34 = 162/01/52 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-1] (TP11) | [PDO1 image] (P01)
R66D | R66 Delay time | 16#10DF = 4319 | 16#200D/14 | 16#76/01/78 = 118/01/120 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R66 Delay time] (R66D) | [R66 configuration] (R66)
R66H | R66 Holding time | 16#10E0 = 4320 | 16#200D/15 | 16#76/01/79 = 118/01/121 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R66 Holding time] (R66H) | [R66 configuration] (R66)
R66S | R66 Active at | 16#10DE = 4318 | 16#200D/13 | 16#76/01/77 = 118/01/119 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R66 Active at] (R66S) | [R66 configuration] (R66)
D60D | DI60 delay | 16#0FD2 = 4050 | 16#200A/33 | 16#75/01/33 = 117/01/51 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI60 delay] (D60D) | [DI60 configuration] (DI60)
EERE | Ethernet embedded error frames | 16#FBA4 = 64420 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb error frames] (EERE) | [Ethernet Emb Diag] (MPE)
THT2 | Thermal error level for winding 2 | 16#9EDA = 40666 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 150 °C | 0 °C ... 2500 °C
THT3 | Thermal error level for bearing 1 | 16#9EDB = 40667 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 115 °C | 0 °C ... 2500 °C
PHI0 | Nameplate nominal flux | 16#267B = 9851 | 16#2044/34 | 16#92/01/34 = 146/01/52 |  | Actual values parameters | R | UINT (Unsigned16) | 0.01 Wb |  | 0.00 Wb ... 655.35 Wb | [Nameplate Nominal Flux] (PHI0) | [data] (MTD) [Autotuning flux] (TUNR)
QF5S | QF5 Command State | 16#9F69 = 40809 |  |  | QF0S | External Controller Function Configuration | R/W | WORD (Enumeration) | -
TFAA | Motor winding A assignment | 16#4143 = 16707 | 16#2089/8 | 16#B4/01/6C = 180/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorWinding A Assign] (TFAA) | [Motor winding A] (CTIA)
TFAC | Motor bearing A assignment | 16#4145 = 16709 | 16#2089/A | 16#B4/01/6E = 180/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorBearing A Assign] (TFAC) | [Motor bearing A] (CTIC)
TFAB | Motor winding B assignment | 16#4144 = 16708 | 16#2089/9 | 16#B4/01/6D = 180/01/109 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorWinding B Assign] (TFAB) | [Motor winding B] (CTIB)
QF56 | QF5 Opening Filter time | 16#9F68 = 40808 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
TFAD | Motor bearing B assignment | 16#4146 = 16710 | 16#2089/B | 16#B4/01/6F = 180/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorBearing B Assign] (TFAD) | [Motor bearing B] (CTID)
QF54 | QF5 Switch OFF delay | 16#9F66 = 40806 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
FPM5 | Fan Pressure Sensor 5 | 16#9F5E = 40798 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
FPM4 | Fan Pressure Sensor 4 | 16#9F5D = 40797 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
TP24 | Transmit PDO2-4 | 16#32EA = 13034 | 16#2064/23 | 16#A2/01/23 = 162/01/35 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-4] (TP24) | [PDO2 image] (P02)
FPM6 | Fan Pressure Sensor 6 | 16#9F5F = 40799 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
TP22 | Transmit PDO2-2 | 16#32E8 = 13032 | 16#2064/21 | 16#A2/01/21 = 162/01/33 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-2] (TP22) | [PDO2 image] (P02)
TP23 | Transmit PDO2-3 | 16#32E9 = 13033 | 16#2064/22 | 16#A2/01/22 = 162/01/34 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-3] (TP23) | [PDO2 image] (P02)
FPM3 | Fan Pressure Sensor 3 | 16#9F5C = 40796 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 0.1 Pa |  | -3200.3 Pa ... 3200.0 Pa
BCKL | Red Backlight | 16#FA13 = 64019 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [Red Backlight] (BCKL) | [LCD settings] (CNL)
FMTR | M/S Master torque reference | 16#41D2 = 16850 | 16#208A/33 | 16#B5/01/33 = 181/01/51 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [M/S Master Torq Ref] (FMTR) | [M/S Local Display] (MSO)
FPMC | Fan Pressure Sensor Scaling | 16#9F61 = 40801 |  |  |  | External controller thermal transformer monitoring | R/WS | UINT (Unsigned16) | 0.1 Pa | 0.0 Pa | 0.0 Pa ... 3276.7 Pa
TP2V | Thermal transformer V2 | 16#9EC7 = 40647 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer V2] (TP2V) | [Power Stage Data] (TTHP)
TP2W | Thermal transformer W2 | 16#9EC8 = 40648 |  |  |  | External controller thermal transformer monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal transformer W2] (TP2W) | [Power Stage Data] (TTHP)
CFAA | Cabinet circuit A assignment | 16#4140 = 16704 | 16#2089/5 | 16#B4/01/69 = 180/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit A Assign] (CFAA) | [Cabinet circuit A] (CCMA)
CFAB | Cabinet circuit B assignment | 16#4141 = 16705 | 16#2089/6 | 16#B4/01/6A = 180/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit B Assign] (CFAB) | [Cabinet circuit B ] (CCMB)
D61D | DI61 delay | 16#0FD3 = 4051 | 16#200A/34 | 16#75/01/34 = 117/01/52 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI61 delay] (D61D) | [DI61 configuration] (DI61)
FWER | Firmware Update error code | 16#FFD6 = 65494 |  |  | FWER | Status parameters | R | WORD (Enumeration) | - |  |  | [Firmware Update Error] (FWER) | [Firmware update diag] (FWUD)
NBTP | Number of TX PDO | 16#330E = 13070 | 16#2064/47 | 16#A2/01/47 = 162/01/71 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of TX PDO] (NBTP) | [CANopen map] (CNM)
R67S | R67 Active at | 16#10E1 = 4321 | 16#200D/16 | 16#76/01/7A = 118/01/122 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R67 Active at] (R67S) | [R67 configuration] (R67)
MDT | HMI displayed value type | 16#FA20 = 64032 |  |  | MDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Digital values] DEC |  | [Display value type] (MDT) | [Display screen type] (MSC)
D50D | DI50 delay | 16#0FC8 = 4040 | 16#200A/29 | 16#75/01/29 = 117/01/41 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI50 delay] (D50D) | [DI50 configuration] (DI50)
THM5 | Thermal winding U2 | 16#9ECF = 40655 |  |  |  | External controller thermal motor monitoring | R/W | INT (Signed16) | 1 °C |  | -32003 °C ... 32000 °C | [Thermal winding U2] (THM5) | [Motor Thermal Data] (MTHP)
QF24 | QF2 Switch OFF delay | 16#9F08 = 40712 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF4S | QF91 Command State | 16#9F19 = 40729 |  |  | QF0S | External Controller Function Configuration | R/W | WORD (Enumeration) | - |  |  | [QF91 Command State] (QF4S) | [V0_SubmenuMainsCircuitbreaker] (CCMV)
IFDD | Monitoring circuit D delay after Run | 16#4167 = 16743 | 16#2089/2C | 16#B4/01/90 = 180/01/144 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit D Delay] (IFDD) | [Monitoring circuit D] (CMCD)
IFDA | Monitoring circuit A delay after Run | 16#4164 = 16740 | 16#2089/29 | 16#B4/01/8D = 180/01/141 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit A Delay] (IFDA) | [Monitoring circuit A] (CMCA)
IFDC | Monitoring circuit C delay after Run | 16#4166 = 16742 | 16#2089/2B | 16#B4/01/8F = 180/01/143 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit C Delay] (IFDC) | [Monitoring circuit C] (CMCC)
IFDB | Monitoring circuit B delay after Run | 16#4165 = 16741 | 16#2089/2A | 16#B4/01/8E = 180/01/142 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit B Delay] (IFDB) | [Monitoring circuit B] (CMCB)
TP31 | Transmit PDO3-1 | 16#32D3 = 13011 | 16#2064/C | 16#A2/01/0C = 162/01/12 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-1] (TP31) | [PDO3 image] (P03)
TP33 | Transmit PDO3-3 | 16#32D5 = 13013 | 16#2064/E | 16#A2/01/0E = 162/01/14 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-3] (TP33) | [PDO3 image] (P03)
TP32 | Transmit PDO3-2 | 16#32D4 = 13012 | 16#2064/D | 16#A2/01/0D = 162/01/13 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-2] (TP32) | [PDO3 image] (P03)
TP34 | Transmit PDO3-4 | 16#32D6 = 13014 | 16#2064/F | 16#A2/01/0F = 162/01/15 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-4] (TP34) | [PDO3 image] (P03)
QF45 | QF91 Closing Filter time | 16#9F0F = 40719 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF47 | QF91 circuit breaker delay time | 16#9F1A = 40730 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 2.5 s | 0.0 s ... 10.0 s
IDM | Motor current Id | 16#25B2 = 9650 | 16#2042/33 | 16#91/01/33 = 145/01/51 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor Current Id] (IDM) | [Motor parameters] (MMO) [data] (MTD)
QF41 | QF91 Close pulse time | 16#9EFB = 40699 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF43 | QF91 Switch ON delay | 16#9F05 = 40709 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF42 | QF91 Open pulse time | 16#9F00 = 40704 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF48 | Mains detection inrush level (%VNOM) | 16#9F23 = 40739 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 % | 85.0 % | 10.0 % ... 200.0 %
IFRD | Response to monitoring circuit D error | 16#417B = 16763 | 16#2089/40 | 16#B4/01/A4 = 180/01/164 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit D ErrorResp] (IFRD) | [Monitoring circuit D] (CMCD)
UOFC | Upward optical error counter | 16#9B48 = 39752 |  |  |  | Power cell configuration | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
D57D | DI57 delay | 16#0FCF = 4047 | 16#200A/30 | 16#75/01/30 = 117/01/48 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI57 delay] (D57D) | [DI57 configuration] (DI57)
ASV | Offset value between motor and encoder | 16#3662 = 13922 | 16#206D/17 | 16#A6/01/7B = 166/01/123 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | -1 | -1 ... 8192 | [Angle offset value] (ASV) | [Angle test setting] (ASA)
FCSI | Source configuration | 16#FA51 = 64081 |  |  | FCSI | Configuration and settings | R/WS | WORD (Enumeration) | - | [Macro configuration] INI |  | [Config. Source] (FCSI) | [Factory settings] (FCS)
RFCC | Channel for reference frequency | 16#FA29 = 64041 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (RFCC) | [Communication map] (CMM)
FTOR | M/S device torque reference | 16#41D4 = 16852 | 16#208A/35 | 16#B5/01/35 = 181/01/53 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [M/S Device Torq Ref] (FTOR) | [M/S Local Display] (MSO) [M/S System Display] (MSR)
BYC2 | Drive bypass command channel | 16#9F26 = 40742 |  |  | BYC2 | External Controller Function Configuration | R/WS | WORD (Enumeration) | - | [Terminal] TER
SDMO | Synchro to drive magnitude offset | 16#4403 = 17411 | 16#2090/C | 16#B8/01/0C = 184/01/12 |  | Synchronization to drive magnitude offset | R/W | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 100.0 V
TFMD | Motor bearing B monitoring | 16#415A = 16730 | 16#2089/1F | 16#B4/01/83 = 180/01/131 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorBearing B Monitor] (TFMD) | [Motor bearing B] (CTID)
TFMA | Motor winding A monitoring | 16#4157 = 16727 | 16#2089/1C | 16#B4/01/80 = 180/01/128 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorWinding A Monitor] (TFMA) | [Motor winding A] (CTIA)
TFRB | Response to motor winding B error | 16#4180 = 16768 | 16#2089/45 | 16#B4/01/A9 = 180/01/169 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorWinding B ErrorResp] (TFRB) | [Motor winding B] (CTIB)
TFMC | Motor bearing A monitoring | 16#4159 = 16729 | 16#2089/1E | 16#B4/01/82 = 180/01/130 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorBearing A Monitor] (TFMC) | [Motor bearing A] (CTIC)
TFMB | Motor winding B monitoring | 16#4158 = 16728 | 16#2089/1D | 16#B4/01/81 = 180/01/129 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorWinding B Monitor] (TFMB) | [Motor winding B] (CTIB)
IFMB | Monitoring circuit B error monitoring type | 16#4151 = 16721 | 16#2089/16 | 16#B4/01/7A = 180/01/122 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit B Monitor] (IFMB) | [Monitoring circuit B] (CMCB)
IFMC | Monitoring circuit C error monitoring type | 16#4152 = 16722 | 16#2089/17 | 16#B4/01/7B = 180/01/123 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit C Monitor] (IFMC) | [Monitoring circuit C] (CMCC)
SDMV | Synchro to drive magnitude Vlim coefficient | 16#43FD = 17405 | 16#2090/6 | 16#B8/01/06 = 184/01/06 |  | Synchronization to drive magnitude Vlim coefficient | R/WS | UINT (Unsigned16) | 0.1 | 1.0 | 0.1 ... 5.0
SDMT | Synchro to drive magnitude threshold | 16#4400 = 17408 | 16#2090/9 | 16#B8/01/09 = 184/01/09 |  | Synchronization to drive magnitude threshold | R/WS | UINT (Unsigned16) | 0.1 V | 6.0 V | 0.0 V ... 100.0 V
IPAF | iPar response to detected error | 16#FB15 = 64277 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [iPar Error Response] (IPAF) | [Profinet] (PNC)
SMAD | Synchro to mains angle damping coefficient | 16#41F1 = 16881 | 16#208A/52 | 16#B5/01/52 = 181/01/82 |  | Synchronization to mains angle damping factor | R/WS | UINT (Unsigned16) | 0.01 | 1.00 | 0.00 ... 10.00
IPLT | Mains phase loss fault time | 16#9B40 = 39744 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 10.0 s | [None] (IPLT) | [None] (IPLT)
SYTD | Synchro to drive selection | 16#43F8 = 17400 | 16#2090/1 | 16#B8/01/01 = 184/01/01 | PSLIN | Synchronization to drive selection | R/WS | WORD (Enumeration) | - | [Not assigned] NO
QF31 | QF3 Close pulse time | 16#9EFA = 40698 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF32 | QF3 Open pulse time | 16#9EFF = 40703 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF33 | QF3 Switch ON delay | 16#9F04 = 40708 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF34 | QF3 Switch OFF delay | 16#9F09 = 40713 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF35 | QF3 Closing Filter time | 16#9F0E = 40718 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF36 | QF3 Opening Filter time | 16#9F13 = 40723 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
M2EC | Mdb NET CRC errors | 16#178E = 6030 | 16#201E/1F | 16#7F/01/1F = 127/01/31 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb NET CRC errors] (M2EC) | [Modbus HMI Diag] (MDH)
UMV | Mains unbalance ratio | 16#2992 = 10642 | 16#204C/2B | 16#96/01/2B = 150/01/43 |  | Status parameters | R | INT (Signed16) | 0.01 % |  | -327.67 % ... 327.67 % | [Mains Unbalance Ratio] (UMV) | [Drive parameters] (MPI)
SCSI | Save configuration | 16#FA50 = 64080 |  |  | SCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Save Configuration] (SCSI) | [Factory settings] (FCS)
STDM | Synchro to drive monitoring | 16#4402 = 17410 | 16#2090/B | 16#B8/01/0B = 184/01/11 | STM | Synchronization to drive monitoring | R | WORD (Enumeration) | -
SMTL | Synchro to mains load time | 16#41FD = 16893 | 16#208A/5E | 16#B5/01/5E = 181/01/94 |  | Synchronization to mains load time | R/WS | UINT (Unsigned16) | 0.1 s | 2.0 s | 0.0 s ... 100.0 s
FWCL | Abort firmware update | 16#FFD5 = 65493 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Abort Firmware Update] (FWCL) | [Firmware update] (FWUP)
THW4 | Thermal warning level for bearing 2 | 16#9ED8 = 40664 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 105 °C | 0 °C ... 2500 °C
THW1 | Thermal warning level for winding 1 | 16#9ED5 = 40661 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 130 °C | 0 °C ... 2500 °C
THW3 | Thermal warning level for bearing 1 | 16#9ED7 = 40663 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 105 °C | 0 °C ... 2500 °C
THW2 | Thermal warning level for winding 2 | 16#9ED6 = 40662 |  |  |  | External controller thermal motor configuration | R/W | UINT (Unsigned16) | 1 °C | 130 °C | 0 °C ... 2500 °C
IPM | IP mode | 16#FAFA = 64250 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [IP mode] (IPM) | [Profinet] (PNC)
RCRP | RCI round number | 16#366C = 13932 | 16#206D/21 | 16#A6/01/85 = 166/01/133 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | RCSP_AUTO | -1 ... 32767 | [RCI Round Nb] (RCRP) | [Motor tune] (MTU)
D59D | DI59 delay | 16#0FD1 = 4049 | 16#200A/32 | 16#75/01/32 = 117/01/50 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI59 delay] (D59D) | [DI59 configuration] (DI59)
RWPO | Reset Option Web Password | 16#FBD9 = 64473 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Reset OptWeb Pwd] (RWPO) | [Webserver] (WBS)
RWPE | Reset Embedded Web | 16#FBA7 = 64423 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Reset EmbWeb] (RWPE) | [Webserver] (WBS)
CFMB | Cabinet circuit B monitoring type | 16#4155 = 16725 | 16#2089/1A | 16#B4/01/7E = 180/01/126 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit B Monitor] (CFMB) | [Cabinet circuit B ] (CCMB)
CFMC | Cabinet circuit C monitoring type | 16#4156 = 16726 | 16#2089/1B | 16#B4/01/7F = 180/01/127 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit C Monitor] (CFMC) | [Cabinet circuit C] (CCMC)
ERXO | Ethernet option Rx frames | 16#FBD2 = 64466 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Rx frames] (ERXO) | [Ethernet Module Diag] (MTE)
QF2S | QF2 Command State | 16#9F17 = 40727 |  |  | QF0S | External Controller Function Configuration | R/W | WORD (Enumeration) | - |  |  | [QF2 Command State] (QF2S) | [V0_SubmenuBypassCircuitbreaker] (CCB)
TAFI | DC injection angle | 16#2903 = 10499 | 16#204A/64 | 16#95/01/64 = 149/01/100 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ° | 0 ° | 0 ° ... 360 ° | [DC injection angle] (TAFI) | [Mot. ctrl hidden menu] (MCW)
QF44 | QF91 Switch OFF delay | 16#9F0A = 40714 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
ICFG | iPAR local configuration | 16#FB14 = 64276 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Local Conf] (ICFG) | [Profinet] (PNC)
QF46 | QF91 Opening Filter time | 16#9F14 = 40724 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF23 | QF2 Switch ON delay | 16#9F03 = 40707 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
QF22 | QF2 Open pulse time | 16#9EFE = 40702 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF21 | QF2 Close pulse time | 16#9EF9 = 40697 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
QF26 | QF2 Opening Filter time | 16#9F12 = 40722 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.0 s ... 60.0 s
IDL | NLD Law Current Min Level | 16#25B8 = 9656 | 16#2042/39 | 16#91/01/39 = 145/01/57 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 50.0 % | 10.0 % ... 100.0 %
IFRC | Response to monitoring circuit C error | 16#417A = 16762 | 16#2089/3F | 16#B4/01/A3 = 180/01/163 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit C ErrorResp] (IFRC) | [Monitoring circuit C] (CMCC)
IFRB | Response to monitoring circuit B error | 16#4179 = 16761 | 16#2089/3E | 16#B4/01/A2 = 180/01/162 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit B ErrorResp] (IFRB) | [Monitoring circuit B] (CMCB)
IFRA | Response to monitoring circuit A error | 16#4178 = 16760 | 16#2089/3D | 16#B4/01/A1 = 180/01/161 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit A ErrorResp] (IFRA) | [Monitoring circuit A] (CMCA)
D55D | DI55 delay | 16#0FCD = 4045 | 16#200A/2E | 16#75/01/2E = 117/01/46 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | 2 ms | 0 ms ... 200 ms | [DI55 delay] (D55D) | [DI55 configuration] (DI55)
QF53 | QF5 Switch ON delay | 16#9F65 = 40805 |  |  |  | External Controller Function Configuration | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s
MVCB | QF1 state | 16#9F1E = 40734 |  |  | MVCB | External Controller Function Configuration | R/W | WORD (Enumeration) | -
ULR | Upload rights | 16#1F69 = 8041 | 16#2032/2A | 16#89/01/2A = 137/01/42 | ULR | Configuration and settings | R/W | WORD (Enumeration) | - | [Upload access allowed] ULR0 |  | [Upload rights] (ULR) | [Password] (COD)
RTC | Alignment Rotational Torque Current | 16#3669 = 13929 | 16#206D/1E | 16#A6/01/82 = 166/01/130 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 0 % | 0 % ... 300 % | [Rotational Torque Current] (RTC) | [Motor tune] (MTU)

## Enumerations
List ID | Value | Display | Description
ABMF | 15 | [150 kHz] (150K) | 150 kHz
| 30 | [300 kHz] (300K) | 300 kHz
| 50 | [500 kHz] (500K) | 500 kHz
| 100 | [1000 kHz] (1M) | 1000 kHz
ACT | 0 | [Not Done] (TAB) | Not done
| 1 | [Pending] (PEND) | Test is pending
| 2 | [In Progress] (PROG) | Test in progress
| 3 | [Error] (FAIL) | Error detected
| 4 | [Autotuning Done] (DONE) | Autotuning Done
ACTION | 0 | [No action] (NO) | No action
| 1 | [Apply Autotuning] (YES) | Apply autotuning
| 2 | [Erase Autotuning] (CLR) | Erase autotuning
ADC | 0 | [No] (NO) | No DC injection
| 1 | [Yes] (YES) | DC injection
| 2 | [Continuous] (CT) | Continuous DC injection
AIOT | 1 | [Voltage] (10U) | Voltage
| 2 | [Current] (0A) | Current
| 5 | [Voltage +/-] (N10U) | AI bipolar volts selected
| 7 | [PTC MANAGEMENT] (PTC) | PTC MANAGEMENT
| 8 | [KTY] (KTY) | KTY
| 9 | [PT1000] (1PT3) | PT1000
| 10 | [PT100] (1PT2) | PT100
| 12 | [3 PT1000] (3PT3) | 3 PT1000
| 13 | [3 PT100] (3PT2) | 3 PT100
| 14 | [PT1000 in 3 wires] (1PT33) | PT1000 in 3 wires
| 15 | [PT100 in 3 wires] (1PT23) | PT100 in 3 wires
| 16 | [3 PT1000 in 3 wires] (3PT33) | 3 PT1000 in 3 wires
| 17 | [3 PT100 in 3 wires] (3PT23) | 3 PT100 in 3 wires
ALR | 0 | [No Warning stored] (NOA) | No Warning stored
| 1 | [Fallback Frequency] (FRF) | Fallback Frequency reaction
| 2 | [Speed Maintained] (RLS) | Speed maintained
| 3 | [Type of stop] (STT) | Type of stop
| 4 | [Ref Frequency Warning] (SRA) | Reference Frequency Warning
| 5 | [Life Cycle Warn 1] (LCA1) | Life Cycle Warning 1
| 6 | [Life Cycle Warn 2] (LCA2) | Life Cycle Warning 2
| 7 | [Dry Run Warning] (DRYA) | Dry run warning
| 13 | [PumpCycle warning] (PCPA) | Pump cycle warning
| 18 | [PID error Warning] (PEE) | PID error Warning
| 19 | [PID Feedback Warn] (PFA) | PID feedback Warning
| 20 | [PID High Fdbck Warn] (PFAH) | PID High Feedback Warning
| 21 | [PID Low Fdbck Warn] (PFAL) | PID Low Feedback Warning
| 22 | [Regulation Warning] (PISH) | Regulation Warning
| 27 | [AI3 Th Warning] (TP3A) | AI3 thermal sensor warning
| 28 | [AI4 Th Warning] (TP4A) | AI4 thermal sensor warning
| 29 | [AI5 Th Warning] (TP5A) | AI5 thermal sensor warning
| 30 | [AI1 4-20 Loss Warning] (AP1) | AI1 4-20 loss Warning
| 32 | [AI3 4-20 Loss Warning] (AP3) | AI3 4-20 loss Warning
| 33 | [AI4 4-20 Loss Warning] (AP4) | AI4 4-20 loss Warning
| 34 | [AI5 4-20 Loss Warning] (AP5) | AI5 4-20 loss Warning
| 35 | [Drive Thermal Warning] (THA) | Drive thermal state Warning
| 37 | [Fan Counter Warning] (FCTA) | Fan Counter Warning
| 38 | [Fan Feedback Warning] (FFDA) | Fan Feedback Warning
| 40 | [Ext. Error Warning] (EFA) | External error warning
| 41 | [Undervoltage Warning] (USA) | Undervoltage Warning
| 42 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 43 | [Forced Run] (ERN) | Drive in forced run
| 44 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 45 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 46 | [Pulse Warn Thd Reached] (FQLA) | Pulse warning threshold reached
| 47 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 48 | [High Speed Reached] (FLA) | High Speed Reached
| 49 | [Ref Freq High Thd reached] (RTAH) | Reference frequency high threshold reached
| 50 | [Ref Freq Low Thd reached] (RTAL) | Reference frequency low threshold reached
| 51 | [2nd Freq Thd Reached] (F2A) | 2nd Frequency Threshold Reached
| 52 | [Current Thd Reached] (CTA) | Current Threshold Reached
| 53 | [Low Current Reached] (CTAL) | Low Current Threshold Reached
| 54 | [High Torque Warning] (TTHA) | High torque Warning
| 55 | [Low Torque Warning] (TTLA) | Low torque Warning
| 56 | [Process Undld Warning] (ULA) | Process underload Warning
| 57 | [Process Overload Warning] (OLA) | Process Overload Warning
| 58 | [Torque Limit Reached] (SSA) | Torque Limit Reached
| 59 | [Torque Control Warning] (RTA) | Torque control Warning
| 60 | [Drv Therm Thd reached] (TAD) | Drive thermal threshold reached
| 61 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 62 | [Mot2 Therm Thd reached] (TS2) | Motor 2 thermal threshold reached
| 63 | [Mot3 Therm Thd reached] (TS3) | Motor 3 thermal threshold reached
| 64 | [Mot4 Therm Thd reached] (TS4) | Motor 4 thermal threshold reached
| 65 | [Power High Threshold] (PTHA) | Power high threshold reached
| 66 | [Power Low Threshold] (PTHL) | Power Low threshold reached
| 67 | [Cust Warning 1] (CAS1) | Customer Warning 1
| 68 | [Cust Warning 2] (CAS2) | Customer Warning 2
| 69 | [Cust Warning 3] (CAS3) | Customer Warning 3
| 70 | [Cust Warning 4] (CAS4) | Customer Warning 4
| 71 | [Cust Warning 5] (CAS5) | Customer Warning 5
| 73 | [Power Cons Warning] (POWD) | Power Consumption Warning
| 83 | [Slipping warn] (ANA) | Slipping warning
| 85 | [Load Mvt Warn] (BSA) | Load movement warning
| 86 | [Brake Cont Warn] (BCA) | Brake contact warning
| 87 | [AI1 Th Warning] (TP1A) | AI1 thermal sensor warning
| 97 | [MonitorCircuit A Warn] (IWA) | Monitoring circuit A warning
| 98 | [MonitorCircuit B Warn] (IWB) | Monitoring circuit B warning
| 99 | [MonitorCircuit C Warn] (IWC) | Monitoring circuit C warning
| 100 | [MonitorCircuit D Warn] (IWD) | Monitoring circuit D warning
| 101 | [CabinetCircuit A Warn] (CWA) | Cabinet circuit A warning
| 102 | [CabinetCircuit B Warn] (CWB) | Cabinet circuit B warning
| 103 | [CabinetCircuit C Warn] (CWC) | Cabinet circuit C warning
| 104 | [MotorWinding A Warn] (TWA) | Motor winding A warning
| 105 | [MotorWinding B Warn] (TWB) | Motor winding B warning
| 106 | [MotorBearing A Warn] (TWC) | Motor bearing A warning
| 107 | [MotorBearing B Warn] (TWD) | Motor bearing B warning
| 119 | [Cabinet Overheat Warn] (CHA) | Cabinet overheat warning
| 124 | [M/S Device Warn] (MSDA) | M/S device warning
| 125 | [Backlash Warn] (BSQA) | Backlash warning
| 126 | [Encoder Thermal Warn] (TPEA) | Encoder module thermal warning
| 132 | [Over-voltage Warn] (OBW) | Over-voltage warning
| 133 | [Temp Sens AI1 Warn] (TS1A) | Temperature sensor AI1 warning
| 135 | [Temp Sens AI3 Warn] (TS3A) | Temperature sensor AI3 warning
| 136 | [Temp Sens AI4 Warn] (TS4A) | Temperature sensor AI4 warning
| 137 | [Temp Sens AI5 Warn] (TS5A) | Temperature sensor AI5 warning
| 138 | [Motor Scaling Warn] (MOTW) | Motor scaling warning
| 139 | [Mains Ground Warn] (IGW) | Mains ground warning
| 140 | [Motor Ground Warn] (OGW) | Motor ground warning
| 141 | [Controller Emb RTC Battery Warn] (CW01) | Controller embedded RTC battery warning
| 142 | [Cooling Fan Warn] (CW02) | Cooling fan warning
| 143 | [Cabinet Overheat] (CW03) | Cabinet overheating
| 144 | [Cabinet Warning 4] (CW04) | Cabinet Warning 4
| 145 | [Fan Power Supply Warn] (CW05) | Fan power supply warning
| 146 | [Auxiliary Power Supply Warn] (CW06) | Auxiliary power supply warning
| 147 | [LV Surge Arrestor Warn] (CW07) | LV surge arrestor warning
| 148 | [Cabinet Warning 8] (CW08) | Cabinet Warning 8
| 149 | [Cabinet Warning 9] (CW09) | Cabinet Warning 9
| 150 | [Cabinet Warning 10] (CW10) | Cabinet Warning 10
| 151 | [QF2 Feedback Warn] (CW11) | QF2 feedback warning
| 152 | [QF3 Feedback Warn] (CW12) | QF3 feedback warning
| 153 | [QF4 Feedback Warn] (CW13) | QF4 feedback warning
| 154 | [QF11 Feedback Warn] (CW14) | QF11 feedback warning
| 155 | [PLC Cabinet Warning 15] (CW15) | PLC Cabinet Warning 15
| 156 | [Cabinet Warning 16] (CW16) | Cabinet Warning 16
| 157 | [Transformer 1 Th Warn] (CW17) | Transformer 1 thermal warning
| 158 | [Transformer 2 Th Warn] (CW18) | Transformer 2 thermal warning
| 159 | [MotorWinding 1 Error] (CW19) | Motor winding 1 error
| 160 | [MotorWinding 2 Error] (CW20) | Motor winding 2 error
| 161 | [MotorBearing 1 Error] (CW21) | Motor bearing 1 error
| 162 | [MotorBearing 2 Error] (CW22) | Motor bearing 2 error
| 163 | [Cabinet Warning 23] (CW23) | Cabinet Warning 23
| 164 | [Cabinet Warning 24] (CW24) | Cabinet Warning 24
| 165 | [Cabinet Warning 25] (CW25) | Cabinet Warning 25
| 166 | [Cabinet Warning 26] (CW26) | Cabinet Warning 26
| 167 | [Cabinet Warning 27] (CW27) | Cabinet Warning 27
| 168 | [Cabinet Warning 28] (CW28) | Cabinet Warning 28
| 169 | [Cabinet Warning 29] (CW29) | Cabinet Warning 29
| 170 | [Cabinet Warning 30] (CW30) | Cabinet Warning 30
| 171 | [Cabinet Warning 31] (CW31) | Cabinet Warning 31
| 172 | [Cabinet Warning 32] (CW32) | Cabinet Warning 32
| 173 | [App Warning 1] (AW01) | Application Warning 1
| 174 | [App Warning 2] (AW02) | Application Warning 2
| 175 | [App Warning 3] (AW03) | Application Warning 3
| 176 | [App Warning 4] (AW04) | Application Warning 4
| 177 | [App Warning 5] (AW05) | Application Warning 5
| 178 | [App Warning 6] (AW06) | Application Warning 6
| 179 | [App Warning 7] (AW07) | Application Warning 7
| 180 | [App Warning 8] (AW08) | Application Warning 8
| 181 | [App Warning 9] (AW09) | Application Warning 9
| 182 | [App Warning 10] (AW10) | Application Warning 10
| 183 | [App Warning 11] (AW11) | Application Warning 11
| 184 | [App Warning 12] (AW12) | Application Warning 12
| 185 | [App Warning 13] (AW13) | Application Warning 13
| 186 | [App Warning 14] (AW14) | Application Warning 14
| 187 | [App Warning 15] (AW15) | Application Warning 15
| 188 | [App Warning 16] (AW16) | Application Warning 16
| 189 | [Bypass Poc Warning 1] (BYW1) | Bypass Poc Warning 1
| 190 | [Bypass Poc Warning 2] (BYW2) | Bypass Poc Warning 2
APPS | 0 | [Running ] (RUN) | Running
| 1 | [Stop] (STOP) | Stop
| 2 | [Local Mode Active] (LOCAL) | Local mode is active
| 3 | [Channel 2 Active] (OVER) | Channel 2 Active
| 4 | [Manual Mode Active] (MANU) | Manual mode is active
| 5 | [PID Active] (AUTO) | PID Active
| 10 | [Boost In progress] (BOOST) | Boost is in progress
| 11 | [Sleep Active] (SLEEP) | Sleep mode is active
| 14 | [BL In Progress] (BQS) | Backlash in progress
APPT | 0 | [Generic Pump Control] (GPMP) | Generic Pump Control
| 3 | [Generic Fan Control] (FAN) | Generic fan control application
| 5 | [Conveyor] (CONV) | Conveyor
| 255 | [All Applications] (ALL) | All application functions available
ASA | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [Done] (DONE) | Done
AST | 3 | [IPM align.] (IPMA) | IPM alignment
| 4 | [SPM align.] (SPMA) | SPM alignment
| 7 | [Rotational Current Injection] (RCI) | Rotational Current Injection
| 254 | [No align.] (NO) | NO alignment
ASTS | 0 | [Not Done] (TAB) | Not done
| 1 | [Pending] (PEND) | Pending
| 2 | [In progress] (PROG) | In progress
| 3 | [Error] (FAIL) | Error detected
| 4 | [Done] (DONE) | Done
| 5 | [Custom Value] (CUS)
ATA | 0 | [No] (NO) | No
| 1 | [Power On] (PON) | Power On
| 2 | [Run Command] (AUTO) | Run command
AUT | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
BDCO | 38 | [50 kbps] (50K) | Baud rate 50kbps
| 52 | [125 kbps] (125K) | Baud rate 125kbps
| 60 | [250 kbps] (250K) | Baud rate 250kbps
| 68 | [500 kbps] (500K) | Baud rate 500kbps
| 76 | [1 Mbps] (1M) | Baud rate 1Mbps
BFR | 0 | [50Hz IEC] (50Hz) | 50Hz Motor frequency
| 1 | [60Hz NEMA] (60Hz) | 60Hz Motor frequency
BIP | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Brake impulse Fwd
| 2 | [2 IBR] (2IBR) | Brake impulse Fwd/Rev
BLC | 0 | [No] (NO) | No
| 2 | [R2] (R2) | Relay R2
| 3 | [R3] (R3) | Relay R3
| 4 | [R4] (R4) | Relay R4
| 5 | [R5] (R5) | Relay R5
| 6 | [R6] (R6) | Relay R6
| 64 | [DQ1 Digital Output] (DO1) | DQ1 Digital Output
| 66 | [DQ11 Digital Output ] (DO11) | DQ11 Digital Output
| 67 | [DQ12 Digital Output ] (DO12) | DQ12 Digital Output
| 75 | [R60] (R60) | Relay R60
| 68 | [R61] (R61) | Relay R61
| 69 | [R62] (R62) | Relay R62
| 70 | [R63] (R63) | Relay R63
| 71 | [R64] (R64) | Relay R64
| 72 | [R65] (R65) | Relay R65
| 73 | [R66] (R66) | Relay R66
| 74 | [R67] (R67) | Relay R67
BMP | 0 | [Stop] (STOP) | Cmd/ref clear on c/over
| 1 | [Bumpless] (BUMP) | Cmd/ref copied on c/over
| 2 | [Disabled] (DIS) | Disabled
BOA | 0 | [Inactive] (NO) | Inactive
| 1 | [Dynamic] (DYNA) | Dynamic
| 2 | [Static] (STAT) | Static
| 3 | [Constant] (CSTE) | Constant
BQM | 0 | [Not Configured] (NO) | Not configured
| 1 | [On Start] (START) | On start
| 2 | [On Start + Dir Change] (CHGDIR) | On Start + direction change
| 3 | [On Master Request] (MS) | On Master request
BQMM | 0 | [Sequential] (SEQ) | Sequential
| 1 | [Simultaneous] (SIMUL) | Simultaneous
BRA | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [High Torque] (DYNA) | High torque
BSP | 0 | [Standard] (BSD) | Standard ref template
| 1 | [Pedestal] (BLS) | Pedestal at LSP
| 2 | [Deadband] (BNS) | Deadband at LSP
| 4 | [Deadband at 0%] (BNS0) | Deadband at 0 speed
BST | 0 | [Traveling] (HOR) | Cross traverse motion
BYC0 | 0 | [Not configured] (NO) | Bypass drive not configured
| 1 | [Monitor] (MON) | Bypass drive monitor
| 2 | [Control DOL] (DOL) | Bypass drive control DOL
| 3 | [Control Synchronized] (SYNC) | Bypass drive control synchronized
BYC2 | 0 | [Terminal] (TER) | Terminal
| 1 | [Modbus] (MDB) | Modbus
| 2 | [Com. Module] (OPT) | Communication module
| 3 | [Embedded Ethernet] (ETH) | Embedded Ethernet
| 4 | [CANOpen] (CAN) | CANOpen
BYP0 | 0 | [Not Configured] (NO) | Not configured
| 1 | [Mode 1] (MODE1) | Mode 1
BYP2 | 0 | [Never] (NEVER) | Never
| 1 | [Manual] (MANU) | Manual
BYS0 | 0 | [Not Configured] (NO) | Not Configured
| 1 | [Undefined] (UND) | Undefined
| 2 | [Drive] (DRV) | Drive
| 3 | [DOL] (DOL) | DOL
| 4 | [DOL On Error] (DOLF) | DOL on error
BYS1 | 0 | [Not configured] (NO) | Not configured
| 1 | [QF2=0 - QF3=0] (BYS1) | QF2=0 - QF3=0
| 2 | [QF2=0 - QF3=1] (BYS2) | QF2=0 - QF3=1
| 3 | [QF2=1 - QF3=0] (BYS3) | QF2=1 - QF3=0
| 4 | [QF2=1 - QF3=1] (BYS4) | QF2=1 - QF3=1
| 5 | [QF11=0 - QF2=0 - QF3=0] (BYS5) | QF11=0 - QF2=0 - QF3=0
| 6 | [QF11=0 - QF2=0 - QF3=1] (BYS6) | QF11=0 - QF2=0 - QF3=1
| 7 | [QF11=0 - QF2=1 - QF3=0] (BYS7) | QF11=0 - QF2=1 - QF3=0
| 8 | [QF11=0 - QF2=1 - QF3=1] (BYS8) | QF11=0 - QF2=1 - QF3=1
| 9 | [QF11=1 - QF2=0 - QF3=0] (BYSA) | QF11=1 - QF2=0 - QF3=0
| 10 | [QF11=1 - QF2=0 - QF3=1] (BYSB) | QF11=1 - QF2=0 - QF3=1
| 11 | [QF11=1 - QF2=1 - QF3=0] (BYSC) | QF11=1 - QF2=1 - QF3=0
| 12 | [QF11=1 - QF2=1 - QF3=1] (BYSD) | QF11=1 - QF2=1 - QF3=1
CAR | 0 | [No Warning Clearing] (NO) | No Warning clearing
| 1 | [Clear Event 1 Warning] (RA1) | Clear Event 1 Warning
| 2 | [Clear Event 2 Warning] (RA2) | Clear Event 2 Warning
| 3 | [Clear Event 3 Warning] (RA3) | Clear Event 3 Warning
| 4 | [Clear Event 4 Warning] (RA4) | Clear Event 4 Warning
| 5 | [Clear Event 5 Warning] (RA5) | Clear Event 5 Warning
CCA | 0 | [Not Configured] (NO) | Not Configured
| 1 | [Counter] (CPT) | Counter
| 2 | [Date and Time] (DT) | Date and Time
CCS | 0 | [Mains/Control ON] (0) | Mains or Control Supply ON
| 1 | [Mains Supply ON] (1) | Mains Supply ON
| 2 | [Drive is Running] (2) | Drive in Running State
CDX | 1 | [Terminals] (TER) | Terminal block
| 3 | [HMI] (LCC) | Local HMI
| 10 | [Modbus] (MDB) | Modbus communication
| 20 | [CANopen] (CAN) | CANopen communication
| 30 | [Com. Module] (NET) | Ext. communication Module
| 40 | [Ethernet] (ETH) | Ethernet
| 50 | [Modbus 2] (MDB2) | Modbus 2
| 51 | [HMI Panel] (HMIP) | HMI Panel
| 52 | [Ctrl Inside] (PLCI) | Ctrl Inside
CFPS | 0 | [None] (NO) | Not Assigned
| 1 | [Set No.1] (CFP1) | Parameter set 1
| 2 | [Set No.2] (CFP2) | Parameter set 2
| 3 | [Set No.3] (CFP3) | Parameter set 3
CHCF | 1 | [Not separ.] (SIM) | Combined channel mode
| 2 | [Separate] (SEP) | Separated channel mode
| 3 | [I/O profile] (IO) | I/O mode
CINR | 20 | [0.001] (0001) | 0.001
| 30 | [0.01] (001) | 0.01
| 40 | [0.1] (01) | 0.1
| 50 | [1] (1) | 1
| 60 | [10] (10) | 10
| 70 | [100] (100) | 100
CIOA | 0 | [20/70] (20) | 20/70
| 1 | [21/71] (21) | 21/71
| 2 | [100/101] (100) | 100/101
| 3 | [Unconfig.] (UNCG) | Unconfigured
CMDS | 0 | [No] (NO) | No
| 1 | [Remote] (REM) | Remote
| 2 | [Local] (LOC) | Local
| 3 | [Panel] (PAN) | Panel
CNFS | 0 | [In progress] (NO) | In progress
| 1 | [Config. No.0] (CNF0) | Configuration set 1
| 2 | [Config. No.1] (CNF1) | Configuration set 2
| 3 | [Config. No.2] (CNF2) | Configuration set 3
| 4 | [Config 3 active] (CNF3) | Config 3 active
CNL | 0 | [Terminals] (TER) | Terminal block
| 2 | [HMI] (LCC) | Local HMI
| 3 | [Modbus] (MDB) | Modbus communication 1
| 4 | [Modbus 2] (MDB2) | Modbus 2
| 5 | [HMI Panel] (HMIP) | HMI Panel
| 6 | [CANopen] (CAN) | CANopen communication
| 7 | [None] (TUD)
| 9 | [Com. Module] (NET) | Ext. communication Module
| 11 | [Ethernet Module] (ETH) | Ethernet option module
| 12 | [Ctrl Inside] (PLCI) | Ctrl Inside
| 15 | [PC tool] (PWS) | PC tool
COFM | 0 | [Measured] (HWCOF) | Measured
| 1 | [Computed] (SWCOF) | Computed
COM1 | 0 | [R0T0] (R0T0)
| 1 | [R0T1] (R0T1)
| 2 | [R1T0] (R1T0)
| 3 | [R1T1] (R1T1)
COP | 0 | [No] (NO) | No copy
| 1 | [Reference Frequency] (SP) | Copy reference frequency
| 2 | [Command] (CD) | Copy command
| 3 | [Cmd + Ref Frequency] (ALL) | Copy command & reference frequency
CSA | 0 | [No] (NO) | Not assigned
| 1 | [AQ1 assignment] (AO1) | AQ1 assignment
| 2 | [AQ2 assignment] (AO2) | AQ2 assignment
| 32 | [PTO] (PTO) | PTO
| 129 | [Ref Frequency 1] (AIFR1) | Reference frequency 1
| 130 | [Ref Frequency 2] (AIFR2) | Reference frequency 2
| 131 | [Ref Frequency 2 Summing] (AISA2) | Reference frequency 2 Summing
| 132 | [PID feedback] (AIPIF) | PI controller feedback
| 136 | [Torque limitation] (AITAA) | Torque limitation
| 137 | [Subtract Ref Freq 2] (AIDA2) | Subtract Reference Frequency 2
| 138 | [Manual PID ref.] (AIPIM) | Manual PID reference
| 139 | [PID Ref Frequency] (AIFPI) | PID reference frequency
| 160 | [Ref Frequency 3 Summing] (AISA3) | Reference frequency 3 Summing
| 161 | [Ref Frequency 1B] (AIFR1B) | Reference frequency 1B
| 162 | [Subtract Ref Freq 3] (AIDA3) | Subtract Reference Frequency 3
| 163 | [Forced local] (AIFLOC) | Forced loc mode channel
| 164 | [Ref Frequency 2 multiplier] (AIMA2) | Reference frequency 2 multiplier
| 165 | [Ref Frequency 3 multiplier] (AIMA3) | Reference frequency 3 multiplier
| 166 | [Torque reference] (AITR1) | Torque reference 1
| 168 | [Virtual AI1 Channel ] (AIAIC1) | Virtual AI1 channel
| 200 | [Torque Ref Offset ] (AITQO) | Torque reference offset
| 201 | [Torque Ref Ratio] (AITQR) | Torque ref ratio
| 202 | [Torque limitation 2] (AITAA2) | Torque limitation 2
| 203 | [Torque reference 2] (AITR2) | Torque reference 2
| 204 | [Frequency Meter] (FQF) | Frequency meter
| 205 | [External Feed Forward] (AITEFF) | External feed forward
| 345 | [M/S Speed Ref In] (MSSI) | M/S Master speed reference input
| 346 | [M/S Trq Ref In] (MSTI) | M/S Master torque reference input
CTT | 0 | [SVC V] (VVC) | Sensorless flux vector V
| 2 | [FVC] (FVC) | Full flux vector
| 3 | [U/F VC Standard] (STD) | U/F VC Standard motor law
| 4 | [U/F VC 5pts] (UF5) | U/F VC 5 point voltage/frequency
| 5 | [Sync. mot.] (SYN) | Synchronous motor
| 6 | [U/F VC Quad.] (UFQ) | U/F VC Quadratic
| 7 | [Energy Sav.] (NLD) | Energy Saving
| 9 | [Sync.CL] (FSY) | Sync.CL
| 11 | [U/F VC Energy Sav.] (ECO) | U/F VC Energy Sav.
DLR | 0 | [Locked drv] (DLR0) | Drive Locked
| 1 | [Unlock. drv] (DLR1) | Drive unlocked
| 2 | [Not allowed] (DLR2) | Download not allowed
| 3 | [Lock/unlock] (DLR3) | Combined Lock/Unlock
DOTD | 0 | [Freewheel stop] (NST) | Drive freewheel stop
| 1 | [Ramp stop] (RMP) | Ramp stop
DPMA | 1 | [Master 1] (1) | Master 1
| 2 | [Master 2] (2) | Master 2
DRYM | 0 | [No] (NO) | No
| 1 | [Switch] (SWT) | Switch
| 2 | [Power] (PWR) | Power
DUR | 0 | [5 minutes] (5) | 5 minutes
| 1 | [10 minutes] (10) | 10 minutes
| 2 | [30 minutes] (30) | 30 minutes
| 3 | [1 hour] (1H) | 1 hour
| 4 | [2 hours] (2H) | 2 hours
| 5 | [3 hours] (3H) | 3 hours
| 6 | [Unlimited] (CT) | Unlimited
ECFG | 0 | [Ignore] (NO) | Ignore
| 1 | [Freewheel Stop] (YES) | Freewheel stop
| 2 | [Per STT] (STT) | Per STT
| 4 | [Fallback Speed] (LFF) | Fallback speed
| 5 | [Speed maintained] (RLS) | Speed maintained
| 6 | [Ramp stop] (RMP) | Ramp stop
EFAP | 0 | [Linear Flux 1] (LINF1) | Linear flux 1
| 1 | [Linear Flux 2] (LINF2) | Linear flux 2
| 2 | [Saturation Flux] (SATF) | Saturation flux
EFDR | 0 | [No Error] (NO) | No error
| 1 | [Server Timeout] (TOUT) | Server timeout
| 2 | [Server No File] (SNF) | Server no file
| 3 | [Server Corrupt File] (CRPT) | Server corrupt file
| 4 | [Server Empty File] (EPTY) | Server empty file
| 5 | [Drive Invalid File] (HINV) | Drive invalid file
| 6 | [CRC Error] (CRC) | CRC error
| 7 | [Version Incompatibility] (VRM) | Version incompatibility
| 9 | [Drive No File] (HNF) | Drive no file
| 10 | [Server Reading Size] (SIZE) | Server reading Size
| 11 | [Drive Opening File] (OPEN) | Drive opening file
| 12 | [Drive Reading File] (READ) | Drive reading file
| 13 | [Incompatibility] (SCNT) | Incompatibility
| 14 | [Drive Invalid Name] (NINV) | Drive invalid name
| 15 | [Server Incorrect File Size] (FSIZ) | Server incorrect file size
| 16 | [Drive Writing File] (HWF) | Drive writing file
| 17 | [Server Writing File] (SWF) | Server writing file
EMDT | 0 | [KW Counter] (KWCT) | KW Counter
| 1 | [Instant. kW trend] (CVE) | Instantaneous kW trend
| 2 | [Daily kWh report] (HSD) | Daily kWh report
| 3 | [Weekly kWh report] (HSW) | Weekly kWh report
| 4 | [Monthly kWh report] (HSM) | Monthly kWh report
| 5 | [Yearly kWh report] (HSY) | Yearly kWh report
ENC | 0 | [Not done] (NO) | Encoder check not done
| 1 | [Yes] (YES) | Encoder check requested
| 2 | [Done] (DONE) | Encoder check completed
ENS | 1 | [AABB] (AABB) | For signals A/A-/B/B-
| 2 | [AB] (AB) | For signals A/B
| 3 | [A] (A) | For signal A
ENSP | 1 | [200 kHz] (200k) | 200 kHz
| 9 | [1 MHz] (1M) | 1 MHz
ENU | 0 | [No] (NO) | Inactive
| 1 | [Speed Monitoring] (SEC) | Speed feedback monitoring
| 2 | [Speed Regulation] (REG) | Speed feedback regulation
ERC | 0 | [Mains Voltage] (ULN) | Mains voltage
| 1 | [Mains Current] (ILN) | Mains current
| 2 | [Mains Frequency] (FAC) | Mains frequency
| 3 | [Active Input Power] (IPRW) | Instantaneous active input power
| 4 | [Input Reactive Power] (IQRW) | Input reactive power
| 5 | [Apparent Input Power] (ISRW) | Apparent input power
| 6 | [Input Power Factor] (PWF) | Input power factor
| 7 | [Mains Unbalance Ratio] (UMV) | Mains unbalance ratio
| 8 | [Pre-Ramp Ref Freq] (FRH) | Reference frequency before ramp
| 9 | [Ramp output frequency (signed)] (FRO) | Ramp output frequency (signed)
| 10 | [Motor Frequency] (RFR) | Motor frequency
| 11 | [Speed] (SPD) | Speed
| 12 | [Motor Power] (OPR) | Motor power
| 13 | [Motor Mech. Power] (OPRW) | Motor mechanical power
| 14 | [Motor Elec Power] (EPR) | Motor electrical power
| 15 | [Output Elec. Power] (EPRW) | Output Electrical Power
| 16 | [Motor Torque] (OTR) | Motor torque
| 17 | [Motor Torque (Nm)] (OTQN) | Motor Torque in Nm
| 18 | [Motor Current] (LCR) | Motor current
| 19 | [Motor Current Id] (IDM) | Motor current Id
| 20 | [Motor Current Iq] (IQM) | Motor current Iq
| 21 | [Motor Voltage] (UOP) | Motor voltage
| 22 | [Max Transfo thermal state ] (TTM) | Maximum transformer thermal state
| 23 | [Max Motor thermal state] (TMM) | Maximum motor thermal state
ETST | 1 | [Init] (INIT) | Init
| 2 | [PreOp] (PROP) | PreOp
| 3 | [Boot] (BOOT) | Boot
| 4 | [SafeOp] (SFOP) | SafeOp
| 8 | [Op] (OP) | Op
FCS | 0 | [No] (NO) | No
| 1 | [Recall customer parameter set 0] (REC0) | Recall customer parameter set 0
| 2 | [Recall customer parameter set 1] (REC1) | Recall customer parameter set 1
| 3 | [Recall customer parameter set 2] (REC2) | Recall customer parameter set 2
| 4 | [Recall customer parameter set 3] (REC3) | Recall customer parameter set 3
| 64 | [Recall default parameter set] (INI) | Recall default parameter set
| 71 | [Recall OEM default parameter set] (INI1) | Recall OEM default parameter set
FCSI | 0 | [Macro Config] (INI) | Macro configuration
| 2 | [Config 1] (CFG1) | Configuration 1
| 3 | [Config 2] (CFG2) | Configuration 2
| 4 | [Config 3] (CFG3) | Config 3
FDRA | 0 | [NOT ACTIVE] (IDLE) | NOT ACTIVE
| 1 | [SAVE] (SAVE) | SAVE
| 2 | [REST] (REST) | REST
FEM | 0 | [No] (NO) | Disable pump characteristics
| 2 | [PQ] (PQ) | Activate Power vs Flow curve
FLR | 0 | [Not Configured] (NO) | Not configured
| 1 | [Yes On Freewheel] (YES) | Yes on freewheel
| 2 | [None] (ALL)
FLU | 0 | [Not continuous] (FNC) | Not continuous
| 1 | [Continuous] (FCT) | Continuous
| 2 | [No] (FNO) | No
FOR | 2 | [8-O-1] (8O1) | 8bit odd parity 1stop bit
| 3 | [8-E-1] (8E1) | 8 bits even parity 1 stop bit
| 4 | [8-N-1] (8N1) | 8bit no parity 1stop bit
| 5 | [8-N-2] (8N2) | 8bit no parity 2stop bits
FWER | 0 | [No Error] (NO) | No error
| 1 | [Lock Error] (LOCK) | Lock error
| 2 | [Package Error] (MD5) | Package error
| 3 | [Package compatibility error] (COMP) | Package compatibility error
| 4 | [Ask error] (ASK) | Ask error
| 5 | [Reset Drive Error] (RESET) | Reset drive error
| 6 | [Conf Saving Warning] (SAVE) | Configuration saving warning
| 7 | [Conf Loading Warning] (LOAD) | Conf loading warning
| 8 | [Post Script Warning] (SCP) | Post Script warning
| 9 | [Package Description Error] (DES) | Package Description error
| 10 | [Package not found] (PKG) | Package not found
| 11 | [Power Supply error] (SPWR) | Power Supply error
| 12 | [Boot M3 error] (BTM3) | Boot M3 error
| 13 | [Boot C28 error] (BTC28) | Boot C28 error
| 14 | [M3 Error] (M3) | M3 error
| 15 | [C28 error] (C28) | C28 error
| 16 | [CPLD error] (CPLD) | CPLD error
| 17 | [Boot Power Error] (PWR) | Boot power error
| 18 | [Emb. Eth Boot Error] (EMBT) | Embedded ethernet boot error
| 19 | [Emb. Eth Error] (EMIL) | Embedded ethernet error
| 20 | [Emb. Eth Web Error] (EMWB) | Embedded ethernet WebServer error
| 21 | [Module Eth Boot Error] (OPTBT) | Module ethernet boot error
| 22 | [Module Eth Error] (OPTIL) | Module ethernet error
| 23 | [Module Eth Web Error] (OPTWB) | Module ethernet WebServer error
| 24 | [Password enabled] (PSWD) | Password enabled
| 25 | [Flash Error] (MEM) | Flash error
| 26 | [Package error] (IFO) | Package error
| 27 | [Wait] (WAIT) | Wait
FWST | 0 | [Inactive] (CHECK) | Firmware update inactive
| 1 | [PwrUpd in progress] (POWER) | Power update in progress
| 2 | [PwrUpd Pending] (PEND) | Power update pending
| 3 | [Ready] (RDY) | Firmware update ready
| 4 | [Inactive] (NO) | Firmware update inactive
| 5 | [Succeeded] (SUCCD) | Firmware update succeded
| 6 | [Update Error] (FAILED) | Update Error
| 7 | [In Progress] (PROG) | Firmware update in progress
| 8 | [Requested] (RQSTD) | Firmware update requested
| 9 | [Transfer In Progress] (TRLD) | Transfer In Progress
| 10 | [Transfer Done] (TROK) | Transfer Done
| 11 | [Package cleared] (CLEAR) | Package cleared
| 12 | [Warning] (SUCWR) | Firmware update succeded with warnings
| 13 | [Drive State Error] (FLSTA) | Drive State Error
| 14 | [Package Error] (FLPKG) | Package Error
| 15 | [Saving conf] (SAVE) | Saving current configuration
| 16 | [Post Script] (POST) | Post Script
| 17 | [Reseting Product] (RESET) | Reseting product
GOVB | 0 | [Ground Warn] (ALRM) | Ground warning
| 1 | [Ground Error] (FLT) | Ground error
| 2 | [None] (ALFL)
HMIS | 0 | [Autotuning] (TUN) | Drive automatic tuning
| 2 | [Ready] (RDY) | Ready
| 3 | [Freewheel] (NST) | Freewheel stop
| 4 | [Running] (RUN) | Running
| 5 | [Accelerating] (ACC) | Accelerating
| 6 | [Decelerating] (DEC) | Decelerating
| 7 | [Current limitation] (CLI) | In current limitation
| 9 | [Mot. fluxing] (FLU) | Motor fluxing
| 11 | [No Mains Voltage] (NLP) | No Mains voltage
| 13 | [control.stop] (CTL) | Control stopping
| 14 | [Dec. adapt.] (OBR) | Dec ramp adaptation
| 17 | [Undervoltage Warning] (USA) | Undervoltage Warning
| 18 | [TC Mode Active] (TC) | TC Mode active
| 19 | [In autotest] (ST) | In autotest
| 20 | [Autotest error] (FA) | Autotest error
| 21 | [Autotest OK] (OK) | Autotest OK
| 22 | [EEprom test] (EP) | EEprom test
| 23 | [Operating State "Fault" ] (FLT) | Operating state "Fault"
| 25 | [DCP Flashing Mode] (DCP) | DCP Flashing Mode
| 36 | [Firmware Update] (FWUP) | Firmware Update
| 38 | [Angle test] (ASA) | Angle test
| 50 | [ON Lock active] (ONLK) | ON Lock active
| 51 | [POE active] (POD) | Power Output Disable active
| 52 | [Torque Limitation] (TLI) | Torque limitation
| 53 | [Power Limitation] (PLI) | Power limitation
| 54 | [Init] (INI) | Initializing
| 55 | [Reset] (RST) | Reset
| 56 | [Synchro. To Mains] (SYTM) | Synchro to mains
| 57 | [Rdy Transfer To Mains] (RTTM) | Ready to transfer to mains
| 58 | [Transfer In Progress] (TTMI) | Transfer in progress
| 59 | [Synchro. To Drive] (SYTD) | Synchro to drive
| 60 | [SD Transfer Ready] (RTTD) | Ready to transfer to drive
| 61 | [Transfer To Drive In Progress] (TTDI) | Transfer to drive in progress
| 62 | [None] (RDIP)
IFM | 0 | [Always Active] (ALL) | Always active
| 1 | [Ready & Run State] (RRY) | Ready and Run state
| 2 | [Run State] (RUN) | Run state
INCPER | 0 | [0.01%] (001) | 0.01%
| 1 | [0.1%] (01) | 0.1%
| 2 | [1%] (1) | 1%
INHS | 0 | [Disabled] (NO) | Disabled
| 1 | [Forced Run FW] (FRD) | Forced Run in forward direction
| 2 | [Forced Run RV] (RRS) | Forced Run in reverse direction
INR | 0 | [0.01] (001) | hundredths of seconds
| 1 | [0.1] (01) | Tenths of seconds
| 2 | [1] (1) | seconds
IPAE | 0 | [Idle State] (IDLE) | Idle State
| 1 | [Init] (INIT) | Init
| 2 | [Configuration] (CONF) | Configuration
| 3 | [Ready] (RDY) | Ready
| 4 | [Operational] (OPE) | Operational
| 5 | [Not Configured] (UCFG) | Not Configured
| 6 | [Unrecoverable Error] (UREC) | Unrecoverable error
IPM | 0 | [Fixed] (MANU) | Fixed address
| 1 | [BOOTP] (BOOTP) | BOOTP
| 2 | [DHCP] (DHCP) | DHCP
| 3 | [DCP] (DCP) | DCP
JMUL | 0 | [0.1] (10em1) | 0.1
| 1 | [1] (10e0) | 1
| 2 | [10] (10e1) | 10
| 3 | [100] (10e2) | 100
| 4 | [1000] (10e3) | 1000
| 5 | [10000] (10e4) | 10000
| 6 | [100000] (10e5) | 100000
LAC | 0 | [Basic] (BAS) | Basic access
| 1 | [Standard] (STD) | Standard access
| 3 | [Expert] (EPR) | Expert access
LDD | 0 | [Distrib. Log. DISABLE] (NO) | Distribution logging disable
| 1 | [Motor Frequency] (RFR) | Motor frequency
| 2 | [Motor Current] (LCR) | Motor current
| 3 | [Motor Speed] (SPD) | Motor Speed
| 4 | [Motor Voltage] (UOP) | Motor voltage
| 5 | [Motor Mech. Power] (OPRW) | Motor mechanical power
| 6 | [Input Elec. Power] (IPRW) | Input Electrical Power
| 7 | [Output Elec. Power] (EPRW) | Output Electrical Power
| 8 | [Motor Torque] (OTR) | Motor torque
| 9 | [Mains Voltage] (ULN) | Mains Voltage
| 10 | [DC BUS Voltage] (VBUS) | DC BUS Voltage
| 11 | [PID feedback] (RPF) | PID Feedback
| 12 | [AI2 Th Value] (TH2V) | AI2 thermal value
| 13 | [AI3 Th Value] (TH3V) | AI3 thermal value
| 14 | [AI4 Th Value] (TH4V) | AI4 thermal value
| 15 | [AI5 Th Value] (TH5V) | AI5 thermal value
| 16 | [Drive Thermal State] (THD) | Drive Thermal State
| 17 | [Motor Thermal State] (THR) | Motor Thermal State
| 18 | [Installation Flow] (FS1V) | Installation Flow
| 19 | [Pump Flow] (FS2V) | Pump Flow
| 20 | [Inlet Pressure] (PS1V) | Inlet Pressure
| 21 | [Outlet Pressure] (PS2V) | Outlet Pressure
| 22 | [Energy Consum. Ind.] (ECI) | Energy consumption indicator
| 23 | [Pump efficiency] (EFY) | Pump efficiency
| 24 | [Energy Perf. Ind.] (EPI) | Energy Performance Indicator
| 25 | [Mains Current] (ILN) | Mains Current
| 26 | [Input Reactive Power] (IQRW) | Input reactive power
| 27 | [Input Power Factor] (PWF) | Input power factor
| 28 | [AI1 Th Value] (TH1V) | AI1 thermal value
| 29 | [DBR Thermal State] (THB) | DBR thermal state
LDEN | 0 | [Stop] (STOP) | Stop
| 1 | [Start] (START) | Start
| 2 | [Always] (ALWAYS) | Always
| 3 | [Reset] (RESET) | Reset
| 4 | [Clear] (CLEAR) | Clear
| 5 | [Error] (ERROR) | Error
LDST | 2 | [200 ms] (200MS) | 200 ms
| 10 | [1 second] (1S) | 1 second
| 20 | [2 seconds] (2S) | 2 seconds
| 50 | [5 seconds] (5S) | 5 seconds
LFT | 0 | [No Error] (NOF) | No error detected
| 2 | [EEPROM Control] (EEF1) | EEPROM control
| 3 | [Incorrect Configuration] (CFF) | Incorrect configuration
| 4 | [Invalid Configuration] (CFI) | Invalid configuration
| 5 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 6 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 7 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 8 | [External Error] (EPF1) | External detected error
| 9 | [Overcurrent] (OCF) | Overcurrent
| 10 | [Precharge Capacitor] (CRF1) | Precharge capacitor
| 11 | [Encoder Feedback Loss] (SPF) | Encoder feedback loss
| 12 | [Load slipping] (ANF) | Load slipping
| 16 | [Drive Overheating] (OHF) | Drive overheating
| 17 | [Motor Overload] (OLF) | Motor overload
| 18 | [DC Bus Overvoltage] (OBF) | DC bus overvoltage
| 19 | [Supply Mains Overvoltage] (OSF) | Supply mains overvoltage
| 20 | [Single output phase loss] (OPF1) | Single output phase loss
| 21 | [Input phase loss] (PHF) | Input phase loss
| 22 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 23 | [Motor short circuit] (SCF1) | Motor short circuit
| 24 | [Motor Overspeed] (SOF) | Motor overspeed
| 25 | [Autotuning Error] (TNF) | Autotuning detected error
| 26 | [Internal Error 1] (INF1) | Internal Error 1 (Rating)
| 27 | [Internal Error 2] (INF2) | Internal Error 2 (Soft)
| 28 | [Internal Error 3] (INF3) | Internal Error 3 (Intern Comm)
| 29 | [Internal Error 4] (INF4) | Internal Error 4 (Manufacturing)
| 30 | [EEPROM Power] (EEF2) | EEPROM power
| 32 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 33 | [Output Phase Loss] (OPF2) | Output phase loss
| 34 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 35 | [Brake Control] (BLF) | Brake control
| 37 | [Internal Error 7] (INF7) | Internal Error 7 (Init)
| 38 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 40 | [Internal Error 8] (INF8) | Internal error 8 (Switching Supply)
| 41 | [Brake Feedback] (BRF) | Brake feedback
| 42 | [PC Com Interruption] (SLF2) | PC communication interruption
| 43 | [Encoder Coupling] (ECF) | Encoder coupling
| 44 | [Torque Limitation Error] (SSF) | Torque limitation error
| 45 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 51 | [Internal Error 9] (INF9) | Internal Error 9 (Measure)
| 52 | [Internal Error 10] (INFA) | Internal Error 10 (Mains)
| 53 | [Internal Error 11] (INFB) | Internal Error 11 (Temperature)
| 55 | [IGBT Short Circuit] (SCF4) | IGBT short circuit
| 56 | [Motor Short Circuit] (SCF5) | Motor short circuit
| 57 | [Torque timeout] (SRF) | Torque timeout
| 60 | [Internal Error 12] (INFC) | Internal Error 12 (Internal current supply)
| 62 | [Encoder] (ENF) | Encoder
| 64 | [Input Contactor] (LCF) | input contactor
| 68 | [Internal Error 6] (INF6) | Internal Error 6 (Option)
| 69 | [Internal Error 14] (INFE) | Internal Error 14 (CPU)
| 71 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 72 | [AI4 4-20mA loss] (LFF4) | AI4 4-20mA loss
| 73 | [Boards Compatibility] (HCF) | Boards compatibility
| 77 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 79 | [AI5 4-20 mA loss] (LFF5) | AI5 4-20 mA loss
| 99 | [Channel Switch Error] (CSF) | Channel switching detected error
| 100 | [Process Underload] (ULF) | Process Underload
| 101 | [Process Overload] (OLC) | Process overload
| 105 | [Angle error] (ASF) | Angle error
| 106 | [AI1 4-20 mA loss] (LFF1) | AI1 4-20 mA loss
| 107 | [Safety Function Error] (SAFF) | Safety function detected error
| 112 | [AI3 Th Level Error] (TH3F) | AI3 thermal level error
| 113 | [AI3 Thermal Sensor Error] (T3CF) | Thermal sensor error on AI3
| 114 | [PumpCycle start Error ] (PCPF) | Pump Cycle start error
| 120 | [AI4 Th Level Error] (TH4F) | AI4 thermal level error
| 121 | [AI4 Thermal Sensor Error] (T4CF) | Thermal sensor error on AI4
| 122 | [AI5 Th Level Error] (TH5F) | AI5 thermal level error
| 123 | [AI5 Thermal Sensor Error] (T5CF) | Thermal sensor error on AI5
| 126 | [Dry Run Error] (DRYF) | Dry run detected error
| 127 | [PID Feedback Error] (PFMF) | PID Feedback detected error
| 128 | [Program Loading Error] (PGLF) | Program loading detected error
| 129 | [Program Running Error] (PGRF) | Program running detected error
| 133 | [None] (CF27)
| 134 | [None] (CF28)
| 136 | [HMI Comm Interrupt] (SLF4) | HMI communication interruption
| 137 | [Mains Overcurrent] (PWF1) | Mains overcurrent
| 138 | [Mains Ground Error] (PWF2) | Mains ground error
| 139 | [Motor Ground Error] (PWF3) | Motor ground error
| 140 | [PoC Fiber Error] (PWF4) | Power Cells Fiber communication error
| 141 | [PoC Supply Error] (PWF5) | Power Cells supply error
| 142 | [Internal Error 16] (INFG) | Internal Error 16 (IO Module - Relay)
| 143 | [Internal Error 17] (INFH) | Internal Error 17 (IO Module - Standard)
| 144 | [Internal Error 0] (INF0) | Internal Error 0 (IPC)
| 145 | [Compatibility Error] (INFO) | Device option interface error
| 146 | [Internal Error 13] (INFD) | Internal Error 13 (Diff Current)
| 148 | [Motor Stall Error] (STF) | Motor stall detected error
| 149 | [Internal Error 21] (INFL) | Internal Error 21 (RTC)
| 150 | [Embd Eth Com Interrupt] (ETHF) | Embedded Ethernet communication interruption
| 151 | [Internal Error 15] (INFF) | Internal Error 15 (Flash)
| 152 | [Firmware Update Error] (FWER) | Firmware Update Error
| 153 | [Internal Error 22] (INFM) | Internal Error 22 (Embedded Ethernet)
| 154 | [Internal Error 25] (INFP) | Internal Error 25 (Incompatibility CB & SW)
| 155 | [Internal Error 20] (INFK) | Internal Error 20 (option interface PCBA)
| 156 | [Internal Error 19] (INFJ) | Internal Error 19 (Encoder module)
| 157 | [Internal Error 27] (INFR) | Internal Error 27 (Diagnostics CPLD)
| 159 | [AFE ShortCircuit error] (SCF6) | AFE ShortCircuit error
| 162 | [MonitorCircuit A Error] (IFA) | Monitoring circuit A error
| 163 | [MonitorCircuit B Error] (IFB) | Monitoring circuit B error
| 164 | [MonitorCircuit C Error] (IFC) | Monitoring circuit C error
| 165 | [MonitorCircuit D Error] (IFD) | Monitoring circuit D error
| 166 | [CabinetCircuit A Error] (CFA) | Cabinet circuit A error
| 167 | [CabinetCircuit B Error] (CFB) | Cabinet circuit B error
| 168 | [CabinetCircuit C Error] (CFC) | Cabinet circuit C error
| 169 | [MotorWinding A Error] (TFA) | Motor winding A error
| 170 | [MotorWinding B Error] (TFB) | Motor winding B error
| 171 | [MotorBearing A Error] (TFC) | Motor bearing A error
| 172 | [MotorBearing B Error] (TFD) | Motor bearing B error
| 173 | [Cabinet Overheat Error] (CHF) | Cabinet overheat error
| 175 | [Internal Error 31] (INFV) | Internal Error 31 (Missing brick)
| 176 | [PoC Fiber DOF Error] (PWF8) | Power Cells Fiber DOF communication error
| 181 | [Pre-settings Transfer Error] (CFI3) | Pre-settings transfer error
| 182 | [Circuit Breaker Error] (CBF) | Circuit breaker error
| 185 | [Drive Overload] (TLOF) | Drive overload
| 186 | [MultiDrive Link Error] (MDLF) | MultiDrive Link Error
| 187 | [AI1 Th Level Error] (TH1F) | AI1 thermal level error
| 188 | [AI1 Thermal Sensor Error] (T1CF) | Thermal sensor error on AI1
| 189 | [Backlash Error] (BSQF) | Backlash error
| 190 | [M/S Device Error] (MSDF) | M/S device error
| 194 | [Encoder Th Level Error] (THEF) | Encoder module thermal level error
| 195 | [Encoder Th Sensor Error] (TECF) | Thermal sensor error on encoder module
| 196 | [Empty Configuration] (CFI4) | Empty configuration
| 197 | [SD Error] (SDFT) | Synchro to drive error
| 200 | [FDR 1 Error] (FDR1) | FDR Eth embedded error
| 201 | [FDR 2 Error] (FDR2) | FDR Eth module error
| 205 | [Opt 3 Comm Interrupt] (CNF3) | 3rd option module communication interruption
| 206 | [Opt 3 Intern Link Error] (ILF3) | 3rd option module internal link error
| 207 | [Opt 3 External Error] (EPF3) | 3rd option module external error
| 208 | [FPGA Internal Error] (PWF6) | FPGA internal error
| 209 | [PoC Gate Driver Error] (PWF7) | PoC gate driver error
| 210 | [Transformer 1 Overheat] (CF01) | Transformer 1 Overheat
| 211 | [Transformer 2 Overheat] (CF02) | Transformer 2 Overheat
| 212 | [PLC Internal Error] (CF03) | PLC internal error
| 213 | [Mains Off Button] (CF04) | Mains Off Button
| 214 | [Door interlock] (CF05) | Door interlock
| 215 | [Cooling Fan error] (CF06) | Cooling fan error
| 216 | [Cabinet Overheat] (CF07) | Cabinet overheat
| 217 | [QF1 Tripped] (CF08) | QF1 circuit breaker tripped
| 218 | [Fan Supply Error] (CF09) | Power supply for cooling fans not ready
| 219 | [Auxiliary Supply Error] (CF10) | Auxiliary supply error
| 220 | [QF1 Grounded Contact Error] (CF11) | QF1 MV Mains circuit breaker grounded contact error
| 221 | [QF1 isolated Contact Error] (CF12) | QF1 MV Mains circuit breaker isolated contact error
| 222 | [QF2 Feedback Error] (CF13) | QF2 feedback error
| 223 | [QF3 Feedback Error] (CF14) | QF3 feedback error
| 224 | [QF91 Feedback Error] (CF15) | QF91 feedback error
| 225 | [QF11 Feedback Error] (CF16) | QF11 feedback error
| 226 | [LV Surge Arrestor Error] (CF17) | LV surge arrestor error
| 227 | [Bypass Drive Error Sequence] (CF18) | Bypass drive error sequence
| 228 | [MotorWinding 1 Error] (CF19) | Motor winding 1 error
| 229 | [MotorWinding 2 Error] (CF20) | Motor winding 2 error
| 230 | [MotorBearing 1 Error] (CF21) | Motor bearing 1 error
| 231 | [MotorBearing 2 Error] (CF22) | Motor bearing 2 error
| 232 | [PT100 Winding Error] (CF23) | PT100 motor winding OC / SC error
| 233 | [PT100 Bearing Error] (CF24) | PT100 motor bearing OC / SC error
| 234 | [Thermal Choke Error] (CF25) | Thermal choke error
| 235 | [QF5 Feedback Error] (CF26) | QF5 feedback error
| 236 | [App Error 1] (AF01) | Application error 1
| 237 | [App Erorr 2] (AF02) | Application error 2
| 238 | [App Error 3] (AF03) | Application error 3
| 239 | [App Error 4] (AF04) | Application error 4
| 240 | [App Error 5] (AF05) | Application error 5
| 241 | [App Error 6] (AF06) | Application error 6
| 242 | [App Error 7] (AF07) | Application error 7
| 243 | [App Fct Error 8] (AF08) | Application function error 8
| 244 | [Mains Voltage Dip Error] (3PF) | Mains Voltage dip error
| 245 | [POE Error] (PODF) | Power Output error
| 246 | [Bypass Poc Error] (BYPF) | Bypass Poc Error
| 247 | [SM Error] (SMFT) | Synchro to mains error
MDT | 0 | [Digital] (DEC) | Digital values
| 1 | [Bar graph] (BAR) | Bar graph
| 2 | [List] (LIST) | List of values
| 3 | [Vu Meter] (VUMET) | Vu Meter
MPC | 0 | [Mot Power] (NPR) | Nominal motor Power
| 1 | [Mot Cosinus] (COS) | Nominal motor cosinus Phi
MRJ | 0 | [Modbus 1] (MDB) | Modbus 1
| 1 | [Modbus 2] (MDB2) | Modbus 2
| 2 | [HMI Panel] (HMIP) | HMI Panel
| 3 | [Vscope tools] (VSCP) | Vscope tools
| 4 | [MATLAB tools] (MAT) | MATLAB tools
| 5 | [SHELL tools] (SHELL) | SHELL tools
| 6 | [Printf tools] (PRINTF) | Printf tools
MSCM | 0 | [No] (NO) | Inactive
| 1 | [MultiDrive Link] (MDL) | MultiDrive link
| 2 | [Analog] (ANA) | Analog
MSCT | 1 | [Torque Direct] (TRQD) | Direct torque control
| 2 | [Torque Reverse] (TRQR) | Reverse torque control
| 3 | [Torque Custom] (TRQC) | Custom torque control
| 4 | [Speed Direct] (SPDD) | Direct speed control
| 5 | [Speed Reverse] (SPDR) | Reverse speed control
MSDT | 0 | [Master] (MSTER) | Master
| 1 | [Slave] (SLAVE) | Slave
MSID | 1 | [Master] (MSTER) | Master
| 2 | [Slave 1] (SLV1) | Slave 1
| 3 | [Slave 2] (SLV2) | Slave 2
| 4 | [Slave 3] (SLV3) | Slave 3
| 5 | [Slave 4] (SLV4) | Slave 4
| 6 | [Slave 5] (SLV5) | Slave 5
| 7 | [Slave 6] (SLV6) | Slave 6
| 8 | [Slave 7] (SLV7) | Slave 7
| 9 | [Slave 8] (SLV8) | Slave 8
| 10 | [Slave 9] (SLV9) | Slave 9
| 11 | [Slave 10] (SLV10) | Slave 10
MSMC | 1 | [Rigid] (RIGID) | Rigid coupling
| 2 | [Elastic] (ELAST) | Elastic coupling
MSS | 0 | [None] (NONE) | Not configured
| 1 | [M/S Local Control] (NACT) | M/S local control
| 2 | [M/S Not Ready] (NRDY) | M/S not ready
| 3 | [M/S Ready] (READY) | M/S ready
| 4 | [M/S Running] (RUN) | M/S running
| 5 | [M/S Warning] (ALARM) | M/S warning
MSSS | 0 | [Not Applied] (NO) | Not applied
| 1 | [Before Ramp] (BRMP) | Before Ramp
| 2 | [After Ramp] (ARMP) | After Ramp
| 3 | [Before Control Loop] (BCTRL) | Before speed control loop
MSTS | 0 | [Not Applied] (NO) | Not applied
| 1 | [Before Advanced Filter] (BFILT) | Before advanced filter
| 2 | [After Advanced Filter] (AFILT) | After advanced filter
MVCB | 0 | [QF1 Not Available] (NO) | QF1 Not Available
| 1 | [QF1 Locked] (LOCK) | QF1 Locked
| 2 | [QF1 Enable To Close] (RDY) | QF1 Enable To Close
| 3 | [QF1 Tripped] (TRIP) | QF1 Tripped
| 4 | [QF1 Closed] (MVCS) | QF1 Closed
NCV | 0 | [Unknown rating] (NO) | Unknown rating
| 1 | [0.12kW] (U010) | 0.10kW - 0.2HP
| 2 | [0.18kW / 0.25Hp] (U018) | 0.18 kW / 0.25 Hp
| 3 | [0.25kW] (U025) | 0.25kW - 0.37HP
| 4 | [0.37 kW / 0.5 Hp] (U037) | 0.37 kW / 0.5 Hp
| 5 | [0.55 kW /0.75 Hp] (U055) | 0.55 kW / 0.75 Hp
| 6 | [0.75 kW / 1 Hp] (U075) | 0.75 kW / 1 Hp
| 7 | [5.5kW / 7.5HP] (U090) | 5.5kW - 7.5HP
| 8 | [1.1 kW / 1.5 Hp] (U110) | 1.1 kW / 1.5 Hp
| 9 | [1.5 kW / 2 Hp] (U150) | 1.5 kW / 2 Hp
| 10 | [1.85kW] (U185) | 1.85kW - 3HP
| 11 | [2.2 kW / 3 Hp] (U220) | 2.2 kW / 3 Hp
| 12 | [3 kW / 4HP] (U300) | 3 kW / 4HP
| 13 | [4kW / 5HP] (U370) | 3.7kW - 5HP
| 14 | [4kW / 5HP] (U400) | 4kW - 5HP
| 15 | [5.5 kW / 7.5 Hp] (U550) | 5.5 kW / 7.5 Hp
| 16 | [7.5 kW / 10 Hp] (U750) | 7.5 kW / 10 Hp
| 17 | [9kW] (U900) | 9kW - 11HP
| 18 | [11 kW / 15 Hp] (D110) | 11 kW / 15 HP
| 19 | [15 kW / 20 Hp] (D150) | 15 kW / 20 HP
| 20 | [18,5kW / 25HP] (D185) | 18.5kW - 25HP
| 21 | [22kW / 30HP] (D220) | 22kW - 30HP
| 22 | [30kW / 40HP] (D300) | 30kW - 40HP
| 23 | [37kW / 50HP] (D370) | 37kW - 50HP
| 24 | [45kW / 60HP] (D450) | 45kW - 60HP
| 25 | [55kW / 75HP] (D550) | 55kW - 75HP
| 26 | [75kW / 100HP] (D750) | 75kW - 100HP
| 27 | [90kW / 125HP] (D900) | 90kW - 125HP
| 28 | [110 kW / 150HP] (C110) | 110kW - 150HP
| 29 | [132kW / 200 HP] (C132) | 132kW - 200HP
| 30 | [160kW / 250HP] (C160) | 160kW - 250HP
| 31 | [200kW / 300HP] (C200) | 200kW - 300HP
| 32 | [220kW / 350HP] (C220) | 220kW - 350HP
| 33 | [250kW / 400HP] (C250) | 250kW - 400HP
| 34 | [280kW / 450HP] (C280) | 280kW - 450HP
| 35 | [315kW / 500HP] (C315) | 315kW - 500HP
| 36 | [355 kW / 450HP] (C355) | 355kW - 450HP
| 37 | [400kW / 600HP] (C400) | 400kW - 600HP
| 38 | [450kW / 750HP] (C450) | 450kW - 750HP
| 39 | [500kW / 800HP] (C500) | 500kW - 800HP
| 40 | [560kW / 850HP] (C560) | 560kW - 850HP
| 41 | [630kW / 900HP] (C630) | 630kW -900HP
| 42 | [710kW / 950HP] (C710) | 710kW -950HP
| 43 | [800kW / 1000HP] (C800) | 800kW - 1000HP
| 44 | [900kW / 900HP] (C900) | 900kW - 900HP
| 45 | [1000kW / 1000HP] (M100) | 1000kW - 1000HP
| 46 | [1100kW / 1100HP] (M110) | 1100kW - 1100HP
| 47 | [1200kW / 1200HP] (M120) | 1200kW - 1200HP
| 48 | [1300kW / 1300HP] (M130) | 1300kW - 1300HP
| 49 | [1400kW / 1400HP] (M140) | 1400kW - 1400HP
| 50 | [1500kW / 1500HP] (M150) | 1500kW - 1500HP
| 51 | [1600kW / 1600HP] (M160) | 1600kW - 1600HP
| 52 | [1700kW / 1700HP] (M170) | 1700kW - 1700HP
| 53 | [1800kW / 1800HP] (M180) | 1800kW - 1800HP
| 54 | [1900kW / 1900HP] (M190) | 1900kW - 1900HP
| 55 | [2000kW / 2000HP] (M200) | 2000kW - 2000HP
| 56 | [2100kW / 2100HP] (M210) | 2100kW - 2100HP
| 57 | [2200kW / 2200HP] (M220) | 2200kW - 2200HP
| 58 | [2300kW / 2300HP] (M230) | 2300kW - 2300HP
| 59 | [2400kW / 2400HP] (M240) | 2400kW - 2400HP
| 60 | [2500 kW / 3333 Hp] (M250) | 2500 kW / 3333 Hp
| 61 | [2600 kW / 3467 Hp] (M260) | 2600 kW / 3467 Hp
| 62 | [2700 kW / 3600 Hp] (M270) | 2700 kW / 3600 Hp
| 63 | [2800 kW / 3733 Hp] (M280) | 2800 kW / 3733 Hp
| 64 | [2900 kW / 3867 Hp] (M290) | 2900 kW / 3867 Hp
| 65 | [3000 kW / 4000 Hp] (M300) | 3000 kW / 4000 Hp
| 66 | [3100 kW / 4133 Hp] (M310) | 3100 kW / 4133 Hp
| 67 | [3200 kW / 4267 Hp] (M320) | 3200 kW / 4267 Hp
| 68 | [3300 kW / 4400 Hp] (M330) | 3300 kW / 4400 Hp
| 69 | [3400 kW / 4533 Hp] (M340) | 3400 kW / 4533 Hp
| 70 | [3500 kW / 4667 Hp] (M350) | 3500 kW / 4667 Hp
| 71 | [3600 kW / 4800 Hp] (M360) | 3600 kW / 4800 Hp
| 72 | [3700 kW / 4933 Hp] (M370) | 3700 kW / 4933 Hp
| 73 | [3800 kW / 5067 Hp] (M380) | 3800 kW / 5067 Hp
| 74 | [3900 kW / 5200 Hp] (M390) | 3900 kW / 5200 Hp
| 75 | [4000 kW / 5333 Hp] (M400) | 4000 kW / 5333 Hp
| 76 | [4100 kW / 5467 Hp] (M410) | 4100 kW / 5467 Hp
| 77 | [4200 kW / 5600 Hp] (M420) | 4200 kW / 5600 Hp
| 78 | [4300 kW / 5733 Hp] (M430) | 4300 kW / 5733 Hp
| 79 | [4400 kW / 5867 Hp] (M440) | 4400 kW / 5867 Hp
| 80 | [4500 kW / 6000 Hp] (M450) | 4500 kW / 6000 Hp
| 81 | [4600 kW / 6133 Hp] (M460) | 4600 kW / 6133 Hp
| 82 | [4700 kW / 6267 Hp] (M470) | 4700 kW / 6267 Hp
| 83 | [4800 kW / 6400 Hp] (M480) | 4800 kW / 6400 Hp
| 84 | [4900 kW / 6533 Hp] (M490) | 4900 kW / 6533 Hp
| 85 | [5000 kW / 6667 Hp] (M500) | 5000 kW / 6667 Hp
| 86 | [5100 kW / 6800 Hp] (M510) | 5100 kW / 6800 Hp
| 87 | [5200 kW / 6933 Hp] (M520) | 5200 kW / 6933 Hp
| 88 | [5300 kW / 7067 Hp] (M530) | 5300 kW / 7067 Hp
| 89 | [5400 kW / 7200 Hp] (M540) | 5400 kW / 7200 Hp
| 90 | [5500 kW / 7333 Hp] (M550) | 5500 kW / 7333 Hp
| 91 | [5600 kW / 7467 Hp] (M560) | 5600 kW / 7467 Hp
| 92 | [5700 kW / 7600 Hp] (M570) | 5700 kW / 7600 Hp
| 93 | [5800 kW / 7733 Hp] (M580) | 5800 kW / 7733 Hp
| 94 | [5900 kW / 7867 Hp] (M590) | 5900 kW / 7867 Hp
| 95 | [6000 kW / 8000 Hp] (M600) | 6000 kW / 8000 Hp
| 96 | [6100 kW / 8133 Hp] (M610) | 6100 kW / 8133 Hp
| 97 | [6200 kW / 8267 Hp] (M620) | 6200 kW / 8267 Hp
| 98 | [6300 kW / 8400 Hp] (M630) | 6300 kW / 8400 Hp
| 99 | [6400 kW / 8533 Hp] (M640) | 6400 kW / 8533 Hp
| 100 | [6500 kW / 8667 Hp] (M650) | 6500 kW / 8667 Hp
| 101 | [6600 kW / 8800 Hp] (M660) | 6600 kW / 8800 Hp
| 102 | [6700 kW / 8933 Hp] (M670) | 6700 kW / 8933 Hp
| 103 | [6800 kW / 9067 Hp] (M680) | 6800 kW / 9067 Hp
| 104 | [6900 kW / 9200 Hp] (M690) | 6900 kW / 9200 Hp
| 105 | [7000 kW / 9333 Hp] (M700) | 7000 kW / 9333 Hp
| 106 | [7100 kW / 9467 Hp] (M710) | 7100 kW / 9467 Hp
| 107 | [7200 kW / 9600 Hp] (M720) | 7200 kW / 9600 Hp
| 108 | [7300 kW / 9733 Hp] (M730) | 7300 kW / 9733 Hp
| 109 | [7400 kW / 9867 Hp] (M740) | 7400 kW / 9867 Hp
| 110 | [7500 kW / 10000 Hp] (M750) | 7500 kW / 10000 Hp
| 111 | [7600 kW / 10133 Hp] (M760) | 7600 kW / 10133 Hp
| 112 | [7700 kW / 10267 Hp] (M770) | 7700 kW / 10267 Hp
| 113 | [7800 kW / 10400 Hp] (M780) | 7800 kW / 10400 Hp
| 114 | [7900 kW / 10533 Hp] (M790) | 7900 kW / 10533 Hp
| 115 | [8000 kW / 10667 Hp] (M800) | 8000 kW / 10667 Hp
| 116 | [8100 kW / 10800 Hp] (M810) | 8100 kW / 10800 Hp
| 117 | [8200 kW / 10933 Hp] (M820) | 8200 kW / 10933 Hp
| 118 | [8300 kW / 11067 Hp] (M830) | 8300 kW / 11067 Hp
| 119 | [8400 kW / 11200 Hp] (M840) | 8400 kW / 11200 Hp
| 120 | [8500 kW / 11333 Hp] (M850) | 8500 kW / 11333 Hp
| 121 | [8600 kW / 11467 Hp] (M860) | 8600 kW / 11467 Hp
| 122 | [8700 kW / 11600 Hp] (M870) | 8700 kW / 11600 Hp
| 123 | [8800 kW / 11733 Hp] (M880) | 8800 kW / 11733 Hp
| 124 | [8900 kW / 11867 Hp] (M890) | 8900 kW / 11867 Hp
| 125 | [9000 kW / 12000 Hp] (M900) | 9000 kW / 12000 Hp
| 126 | [9100 kW / 12133 Hp] (M910) | 9100 kW / 12133 Hp
| 127 | [9200 kW / 12267 Hp] (M920) | 9200 kW / 12267 Hp
| 128 | [9300 kW / 12400 Hp] (M930) | 9300 kW / 12400 Hp
| 129 | [9400 kW / 12533 Hp] (M940) | 9400 kW / 12533 Hp
| 130 | [9500 kW / 12667 Hp] (M950) | 9500 kW / 12667 Hp
| 131 | [9600 kW / 12800 Hp] (M960) | 9600 kW / 12800 Hp
| 132 | [9700 kW / 12933 Hp] (M970) | 9700 kW / 12933 Hp
| 133 | [9800 kW / 13067 Hp] (M980) | 9800 kW / 13067 Hp
| 134 | [9900 kW / 13200 Hp] (M990) | 9900 kW / 13200 Hp
| 135 | [10000 kW / 13333 Hp] (T100) | 10000 kW / 13333 Hp
| 136 | [10100 kW / 13467 Hp] (T101) | 10100 kW / 13467 Hp
| 137 | [10200 kW / 13600 Hp] (T102) | 10200 kW / 13600 Hp
| 138 | [10300 kW / 13733 Hp] (T103) | 10300 kW / 13733 Hp
| 139 | [10400 kW / 13867 Hp] (T104) | 10400 kW / 13867 Hp
| 140 | [10500 kW / 14000 Hp] (T105) | 10500 kW / 14000 Hp
| 141 | [10600 kW / 14133 Hp] (T106) | 10600 kW / 14133 Hp
| 142 | [10700 kW / 14267 Hp] (T107) | 10700 kW / 14267 Hp
| 143 | [10800 kW / 14400 Hp] (T108) | 10800 kW / 14400 Hp
| 144 | [10900 kW / 14533 Hp] (T109) | 10900 kW / 14533 Hp
| 145 | [11000 kW / 14667 Hp] (T110) | 11000 kW / 14667 Hp
| 146 | [11100 kW / 14800 Hp] (T111) | 11100 kW / 14800 Hp
| 147 | [11200 kW / 14933 Hp] (T112) | 11200 kW / 14933 Hp
| 148 | [11300 kW / 15067 Hp] (T113) | 11300 kW / 15067 Hp
| 149 | [11400 kW / 15200 Hp] (T114) | 11400 kW / 15200 Hp
| 150 | [11500 kW / 15333 Hp] (T115) | 11500 kW / 15333 Hp
| 151 | [11600 kW / 15467 Hp] (T116) | 11600 kW / 15467 Hp
| 152 | [11700 kW / 15600 Hp] (T117) | 11700 kW / 15600 Hp
| 153 | [11800 kW / 15733 Hp] (T118) | 11800 kW / 15733 Hp
| 154 | [11900 kW / 15867 Hp] (T119) | 11900 kW / 15867 Hp
| 155 | [12000 kW / 16000 Hp] (T120) | 12000 kW / 16000 Hp
| 156 | [12100 kW / 16133 Hp] (T121) | 12100 kW / 16133 Hp
| 157 | [12200 kW / 16267 Hp] (T122) | 12200 kW / 16267 Hp
| 158 | [12300 kW / 16400 Hp] (T123) | 12300 kW / 16400 Hp
| 159 | [12400 kW / 16533 Hp] (T124) | 12400 kW / 16533 Hp
| 160 | [12500 kW / 16667 Hp] (T125) | 12500 kW / 16667 Hp
| 161 | [12600 kW / 16800 Hp] (T126) | 12600 kW / 16800 Hp
| 162 | [12700 kW / 16933 Hp] (T127) | 12700 kW / 16933 Hp
| 163 | [12800 kW / 17067 Hp] (T128) | 12800 kW / 17067 Hp
| 164 | [12900 kW / 17200 Hp] (T129) | 12900 kW / 17200 Hp
| 165 | [13000 kW / 17333 Hp] (T130) | 13000 kW / 17333 Hp
| 166 | [13100 kW / 17467 Hp] (T131) | 13100 kW / 17467 Hp
| 167 | [13200 kW / 17600 Hp] (T132) | 13200 kW / 17600 Hp
| 168 | [13300 kW / 17733 Hp] (T133) | 13300 kW / 17733 Hp
| 169 | [13400 kW / 17867 Hp] (T134) | 13400 kW / 17867 Hp
| 170 | [13500 kW / 18000 Hp] (T135) | 13500 kW / 18000 Hp
| 171 | [13600 kW / 18133 Hp] (T136) | 13600 kW / 18133 Hp
| 172 | [13700 kW / 18267 Hp] (T137) | 13700 kW / 18267 Hp
| 173 | [13800 kW / 18400 Hp] (T138) | 13800 kW / 18400 Hp
| 174 | [13900 kW / 18533 Hp] (T139) | 13900 kW / 18533 Hp
| 175 | [14000 kW / 18667 Hp] (T140) | 14000 kW / 18667 Hp
| 176 | [14100 kW / 18800 Hp] (T141) | 14100 kW / 18800 Hp
| 177 | [14200 kW / 18933 Hp] (T142) | 14200 kW / 18933 Hp
| 178 | [14300 kW / 19067 Hp] (T143) | 14300 kW / 19067 Hp
| 179 | [14400 kW / 19200 Hp] (T144) | 14400 kW / 19200 Hp
| 180 | [14500 kW / 19333 Hp] (T145) | 14500 kW / 19333 Hp
| 181 | [14600 kW / 19467 Hp] (T146) | 14600 kW / 19467 Hp
| 182 | [14700 kW / 19600 Hp] (T147) | 14700 kW / 19600 Hp
| 183 | [14800 kW / 19733 Hp] (T148) | 14800 kW / 19733 Hp
| 184 | [14900 kW / 19867 Hp] (T149) | 14900 kW / 19867 Hp
| 185 | [15000 kW / 20000 Hp] (T150) | 15000 kW / 20000 Hp
| 186 | [15100 kW / 20133 Hp] (T151) | 15100 kW / 20133 Hp
| 187 | [15200 kW / 20267 Hp] (T152) | 15200 kW / 20267 Hp
| 188 | [15300 kW / 20400 Hp] (T153) | 15300 kW / 20400 Hp
| 189 | [15400 kW / 20533 Hp] (T154) | 15400 kW / 20533 Hp
| 190 | [15500 kW / 20667 Hp] (T155) | 15500 kW / 20667 Hp
| 191 | [15600 kW / 20800 Hp] (T156) | 15600 kW / 20800 Hp
| 192 | [15700 kW / 20933 Hp] (T157) | 15700 kW / 20933 Hp
| 193 | [15800 kW / 21067 Hp] (T158) | 15800 kW / 21067 Hp
| 194 | [15900 kW / 21200 Hp] (T159) | 15900 kW / 21200 Hp
| 195 | [16000 kW / 21333 Hp] (T160) | 16000 kW / 21333 Hp
| 196 | [16100 kW / 21467 Hp] (T161) | 16100 kW / 21467 Hp
| 197 | [16200 kW / 21600 Hp] (T162) | 16200 kW / 21600 Hp
| 198 | [16300 kW / 21733 Hp] (T163) | 16300 kW / 21733 Hp
| 199 | [16400 kW / 21867 Hp] (T164) | 16400 kW / 21867 Hp
| 200 | [16500 kW / 22000 Hp] (T165) | 16500 kW / 22000 Hp
| 201 | [16600 kW / 22133 Hp] (T166) | 16600 kW / 22133 Hp
| 202 | [16700 kW / 22267 Hp] (T167) | 16700 kW / 22267 Hp
| 203 | [16800 kW / 22400 Hp] (T168) | 16800 kW / 22400 Hp
| 204 | [16900 kW / 22533 Hp] (T169) | 16900 kW / 22533 Hp
| 205 | [17000 kW / 22667 Hp] (T170) | 17000 kW / 22667 Hp
| 206 | [17100 kW / 22800 Hp] (T171) | 17100 kW / 22800 Hp
| 207 | [17200 kW / 22933 Hp] (T172) | 17200 kW / 22933 Hp
| 208 | [17300 kW / 23067 Hp] (T173) | 17300 kW / 23067 Hp
| 209 | [17400 kW / 23200 Hp] (T174) | 17400 kW / 23200 Hp
| 210 | [17500 kW / 23333 Hp] (T175) | 17500 kW / 23333 Hp
| 211 | [17600 kW / 23467 Hp] (T176) | 17600 kW / 23467 Hp
| 212 | [17700 kW / 23600 Hp] (T177) | 17700 kW / 23600 Hp
| 213 | [17800 kW / 23733 Hp] (T178) | 17800 kW / 23733 Hp
| 214 | [17900 kW / 23867 Hp] (T179) | 17900 kW / 23867 Hp
| 215 | [18000 kW / 24000 Hp] (T180) | 18000 kW / 24000 Hp
| 216 | [18100 kW / 24133 Hp] (T181) | 18100 kW / 24133 Hp
| 217 | [18200 kW / 24267 Hp] (T182) | 18200 kW / 24267 Hp
| 218 | [18300 kW / 24400 Hp] (T183) | 18300 kW / 24400 Hp
| 219 | [18400 kW / 24533 Hp] (T184) | 18400 kW / 24533 Hp
| 220 | [18500 kW / 24667 Hp] (T185) | 18500 kW / 24667 Hp
| 221 | [18600 kW / 24800 Hp] (T186) | 18600 kW / 24800 Hp
| 222 | [18700 kW / 24933 Hp] (T187) | 18700 kW / 24933 Hp
| 223 | [18800 kW / 25067 Hp] (T188) | 18800 kW / 25067 Hp
| 224 | [18900 kW / 25200 Hp] (T189) | 18900 kW / 25200 Hp
| 225 | [19000 kW / 25333 Hp] (T190) | 19000 kW / 25333 Hp
| 226 | [19100 kW / 25467 Hp] (T191) | 19100 kW / 25467 Hp
| 227 | [19200 kW / 25600 Hp] (T192) | 19200 kW / 25600 Hp
| 228 | [19300 kW / 25733 Hp] (T193) | 19300 kW / 25733 Hp
| 229 | [19400 kW / 25867 Hp] (T194) | 19400 kW / 25867 Hp
| 230 | [19500 kW / 26000 Hp] (T195) | 19500 kW / 26000 Hp
| 231 | [19600 kW / 26133 Hp] (T196) | 19600 kW / 26133 Hp
| 232 | [19700 kW / 26267 Hp] (T197) | 19700 kW / 26267 Hp
| 233 | [19800 kW / 26400 Hp] (T198) | 19800 kW / 26400 Hp
| 234 | [19900 kW / 26533 Hp] (T199) | 19900 kW / 26533 Hp
| 235 | [20000 kW / 26667 Hp] (T200) | 20000 kW / 26667 Hp
NFL | 0 | [No] (NO) | No
| 1 | [First] (1ST) | First
| 2 | [Second] (2ND) | Second
| 3 | [All] (ALL) | All
NMTS | 0 | [Boot] (BOOT) | On boot up
| 2 | [Stopped] (STOP) | Stopped
| 1 | [Operation] (OPE) | Operational
| 4 | [Pre-op] (POPE) | Pre operation
NPL | 0 | [1] (POS) | 1
| 1 | [0] (NEG) | 0
N_Y | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
OPL | 0 | [Function Inactive] (NO) | Function inactive
| 1 | [OPF Error Triggered] (YES) | OPF error Triggered
OVMA | 0 | [Default] (DEFAULT) | Default
| 255 | [Full] (FULL) | Full
PCM | 0 | [No] (NO) | Disable pump characteristics
| 3 | [PHQ] (PHQ) | Enable Head vs Flow and Power vs Flow curves
PCM0 | 0 | [PoC not configured] (NO) | Power cell not configured
| 1 | [PoC Invalid Config] (TOPO) | Power cell invalid configuration
| 2 | [PoC not supplied] (NLP) | Power cell not supply
| 3 | [PoC ready] (RDY) | Power cell ready
| 4 | [PoC running] (RUN) | Power cell running
| 5 | [PoC fault] (FLT) | Power cell fault
| 6 | [PoC By-passed] (BYP) | PoC By-passed
| 7 | [Power Output Disabled] (POD) | Power Output Disabled
| 8 | [Damaged PoC By-passed ] (BYPF) | Damaged PoC By-passed
PCPM | 0 | [No] (NO) | Pump Cycle monitoring disabled
| 1 | [Mode 1] (NORM) | Pump Cycle monitoring mode 1
| 2 | [Mode 2] (RTC) | Pump Cycle monitoring mode 2
PCS | 0 | [None] (NONE) | None
| 1 | [Inactive] (NACT) | Inactive
| 2 | [Active] (ACTIVE) | Active
| 3 | [Failed] (FAILED) | Failed
PHR | 0 | [ABC] (ABC) | A - B - C phase rotation
| 1 | [ACB] (ACB) | A - C - B phase rotation
PKTP | 0 | [Product] (PRD) | Product package
| 1 | [Module] (OPT) | Module package
| 2 | [Spare parts] (SPR) | Spare parts package
| 3 | [Customized] (CUS) | Customized package
| 4 | [Indus] (IND) | Indus package
PL00 | 0 | [Error] (FLT) | Error
| 1 | [Warning] (WARN) | Warning
PLS0 | 0 | [No] (NO) | No
| 1 | [4 positions (O-L-R-P)] (OLRP) | 4 position switch (Off - Local - Remote - Panel)
| 2 | [3 positions (L-R-P)] (LRP) | 3 position switch (Local - Remote - Panel)
| 3 | [3 positions (O-R-P)] (ORP) | 3 position switch (Off - Remote - Panel)
| 4 | [3 positions (O-L-R)] (OLR) | 3 position switch (Off - Local - Remote)
| 5 | [2 positions (L-R)] (LR) | 2 position switch (Local - Remote)
| 6 | [2 positions (R-P)] (RP) | 2 position switch (Remote - Panel)
PMDT | 0 | [Parameters List] (NO) | Parameters List
| 1 | [Operating Time] (HOT) | Operating Time Histogram
| 2 | [Nb of Starts] (HNS) | Nb of Starts Histogram
| 3 | [Efficiency] (EFF) | Efficiency Trend view
| 4 | [Power vs Flow] (CPQ) | Power vs Flow curve
| 5 | [Head vs Flow] (CHQ) | Head vs Flow curve
| 6 | [Efficiency vs Flow] (CEQ) | Efficiency vs Flow curve
POES | 0 | [Not active] (IDLE) | Not active
| 1 | [Active] (POD) | Active
| 2 | [Error] (FLT) | Error
PRFL | 0 | [Not Configured] (UNCG) | Not configured
| 1 | [1] (1) | 1
| 100 | [100] (100) | 100
| 101 | [101] (101) | 101
| 102 | [102] (102) | 102
| 106 | [106] (106) | 106
| 107 | [107] (107) | 107
PSA | 0 | [Not Configured] (NO) | Not configured
| 1 | [AI1] (AI1) | AI1 Analog input
| 2 | [AI2] (AI2) | AI2 Analog input
| 3 | [AI3] (AI3) | AI3 Analog input
| 4 | [AI4] (AI4) | AI4 Analog input
| 5 | [AI5] (AI5) | AI5 Analog input
| 129 | [Motor Current] (OCR) | Motor current
| 130 | [Motor Frequency] (OFR) | Motor frequency
| 131 | [Ramp out.] (ORP) | Ramp output
| 132 | [Motor torq.] (TRQ) | Motor torque
| 133 | [Sign. torque] (STQ) | Signed torque
| 134 | [sign ramp] (ORS) | Signed ramp
| 135 | [PID ref.] (OPS) | PID reference
| 136 | [PID feedbk] (OPF) | PID feedback
| 137 | [PID error] (OPE) | PID error
| 138 | [PID output] (OPI) | PID output
| 139 | [Motor Power] (OPR) | Motor power
| 140 | [Mot thermal] (THR) | Motor thermal state
| 141 | [Drv thermal] (THD) | Drive thermal state
| 142 | [Torque 4Q] (TR4Q) | Torque 4Q
| 143 | [Measured Motor Freq] (OFRR) | Measured motor frequency
| 160 | [Ref Frequency via DI] (UPDT) | Reference frequency via DI
| 163 | [Ref.Freq-Rmt.Term] (LCC) | Reference Frequency via remote terminal
| 164 | [Ref. Freq-Modbus] (MDB) | Reference Frequency via Modbus
| 165 | [Modbus 2] (MDB2) | Modbus 2
| 167 | [Ref. Freq-CANopen] (CAN) | Reference Frequency via CANopen
| 169 | [Ref. Freq-Com. Module] (NET) | Reference Frequency via Com Module
| 171 | [Embedded Ethernet] (ETH) | Embedded Ethernet
| 173 | [Sig. o/p frq.] (OFS) | Signed output frequency
| 174 | [Mot therm2] (THR2) | Motor thermal 2 state
| 175 | [Mot therm3] (THR3) | Motor thermal 3 state
| 176 | [Mot therm4] (THR4) | Motor thermal 4 state
| 177 | [Unsigned Trq Ref] (UTR) | Unsigned torque reference
| 178 | [Signed Trq Ref] (STR) | Signed torque reference
| 179 | [Torque lim.] (TQL) | Torque limit
| 180 | [Motor volt.] (UOP) | Motor voltage
| 183 | [AI Virtual 1] (AIV1) | AI Virtual 1
| 184 | [DQ1] (DO1) | Digital output 1
| 188 | [DI7 PulseInput] (PI7) | DI7 PulseInput
| 189 | [DI8 PulseInput ] (PI8) | DI8 PulseInput
| 191 | [Mains Voltage] (ULN) | Mains voltage
| 192 | [Mains Current] (ILN) | Mains current
| 193 | [Input Elec. Power] (IPR) | Input Electrical Power
| 194 | [Input Reactive Power] (IQR) | Input reactive power
| 195 | [Input Power Factor] (PWF) | Input power factor
| 198 | [HMI Panel] (HMIP) | HMI Panel
| 199 | [Ctrl Inside] (PLCI) | Ctrl Inside
| 340 | [Est. Pump Flow] (SLPF) | Estimated pump flow
| 344 | [M/S Out Speed Reference] (MSSO) | M/S output speed reference
| 345 | [M/S Out Torque Reference] (MSTO) | M/S output torque reference
PSL | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Drive in operating state "Fault"
| 2 | [Drive Running] (RUN) | Drive running
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 5 | [High Speed Reached] (FLA) | High speed reached
| 6 | [Current Thd Reached] (CTA) | Current threshold reached
| 7 | [Ref Freq Reached] (SRA) | Reference frequency reached
| 8 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 9 | [Brake Sequence] (BLC) | Brake sequence
| 10 | [PID error Warning] (PEE) | PID error Warning
| 11 | [PID Feedback Warn] (PFA) | PID feedback Warning
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 14 | [Drv Therm Thd reached] (TAD) | Drive thermal threshold reached
| 16 | [Ref Freq High Thd reached] (RTAH) | Reference frequency high threshold reached
| 17 | [Ref Freq Low Thd reached] (RTAL) | Reference frequency low threshold reached
| 18 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 19 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 20 | [Low Current Reached] (CTAL) | Low Current Threshold Reached
| 21 | [Process Undld Warning] (ULA) | Process underload Warning
| 22 | [Process Overload Warning] (OLA) | Process Overload Warning
| 23 | [PID High Fdbck Warn] (PFAH) | PID High Feedback Warning
| 24 | [PID Low Fdbck Warn] (PFAL) | PID Low Feedback Warning
| 25 | [Regulation Warning] (PISH) | Regulation Warning
| 26 | [Forced Run] (ERN) | Forced Run
| 28 | [High Torque Warning] (TTHA) | High torque Warning
| 29 | [Low Torque Warning] (TTLA) | Low torque Warning
| 30 | [Forward] (MFRD) | Run forward
| 31 | [Reverse] (MRRS) | Run reverse
| 34 | [Ramp switching] (RP2) | Ramp switching
| 37 | [Mot2 Therm Thd reached] (TS2) | Motor 2 thermal threshold reached
| 38 | [Mot3 Therm Thd reached] (TS3) | Motor 3 thermal threshold reached
| 39 | [Mot4 Therm Thd reached] (TS4) | Motor 4 thermal threshold reached
| 42 | [HMI cmd] (BMP) | HMI command
| 47 | [Neg Torque] (ATS) | Negative torque
| 48 | [Cnfg.0 act.] (CNF0) | Configuration 0 active
| 49 | [Cnfg.1 act.] (CNF1) | Configuration 1 active
| 50 | [Cnfg.2 act.] (CNF2) | Configuration 2 active
| 51 | [Configuration 3 Active] (CNF3) | Configuration 3 active
| 52 | [set 1 active] (CFP1) | Parameter set 1 active
| 53 | [set 2 active] (CFP2) | Parameter set 2 active
| 54 | [set 3 active] (CFP3) | Parameter set 3 active
| 64 | [DC charged] (DBL) | DC bus charged
| 72 | [Pulse Warn Thd Reached] (FQLA) | Pulse warning threshold reached
| 77 | [I present] (MCP) | I present
| 80 | [Warning Grp 1] (AG1) | Warning group 1
| 81 | [Warning Grp 2] (AG2) | Warning group 2
| 82 | [Warning Grp 3] (AG3) | Warning group 3
| 87 | [External Error Warning] (EFA) | External error warning
| 88 | [Undervoltage Warning ] (USA) | Undervoltage Warning
| 89 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 90 | [Slipping warn] (ANA) | Slipping warning
| 91 | [Drive Thermal Warning] (THA) | Drive thermal state Warning
| 93 | [Load Mvt Warn] (BSA) | Load movement warning
| 94 | [Brake Contact Warn] (BCA) | Brake contact warning
| 95 | [Lim T/I Reached] (SSA) | Limit torque / I reached
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 1
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 103 | [Trq ctrl Warning] (RTA) | Torque control timeout warning
| 107 | [AI3 4-20 Loss Warning] (AP3) | AI3 4-20 Loss Warning
| 108 | [AI4 4-20 Loss Warn] (AP4) | AI4 4-20 Loss Warning
| 123 | [AI1 4-20 Loss Warning] (AP1) | AI1 4-20 loss Warning
| 127 | [Ready] (RDY) | Ready
| 128 | [Yes] (YES) | Yes
| 129 | [DI1] (LI1) | Digital Input 1
| 130 | [DI2] (LI2) | Digital Input 2
| 131 | [DI3] (LI3) | Digital Input 3
| 132 | [DI4] (LI4) | Digital Input 4
| 133 | [DI5] (LI5) | Digital Input 5
| 134 | [DI6] (LI6) | Digital Input 6
| 135 | [DI7] (LI7) | Digital input 7
| 136 | [DI8] (LI8) | Digital input 8
| 139 | [DI11] (LI11) | Digital Input 11
| 140 | [DI12] (LI12) | Digital Input 12
| 141 | [DI13] (LI13) | Digital Input 13
| 142 | [DI14] (LI14) | Digital Input 14
| 143 | [DI15] (LI15) | Digital Input 15
| 144 | [DI16] (LI16) | Digital Input 16
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 176 | [C100] (C100) | Bit 0 Modbus ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 192 | [C200] (C200) | Bit 0 CANopen ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 208 | [C300] (C300) | Bit 0 Com Module ctrl word
| 209 | [C301] (C301) | Bit 1 Com Module ctrl word
| 210 | [C302] (C302) | Bit 2 Com Module ctrl word
| 211 | [C303] (C303) | Bit 3 Com Module ctrl word
| 212 | [C304] (C304) | Bit 4 Com Module ctrl word
| 213 | [C305] (C305) | Bit 5 Com Module ctrl word
| 214 | [C306] (C306) | Bit 6 Com Module ctrl word
| 215 | [C307] (C307) | Bit 7 Com Module ctrl word
| 216 | [C308] (C308) | Bit 8 Com Module ctrl word
| 217 | [C309] (C309) | Bit 9 Com Module ctrl word
| 218 | [C310] (C310) | Bit 10 Com Module ctrl word
| 219 | [C311] (C311) | Bit 11 Com Module ctrl word
| 220 | [C312] (C312) | Bit 12 Com Module ctrl word
| 221 | [C313] (C313) | Bit 13 Com Module ctrl word
| 222 | [C314] (C314) | Bit 14 Com Module ctrl word
| 223 | [C315] (C315) | Bit 15 Com Module ctrl word
| 240 | [C500] (C500) | C500
| 241 | [C501] (C501) | C501
| 242 | [C502] (C502) | C502
| 243 | [C503] (C503) | C503
| 244 | [C504] (C504) | C504
| 245 | [C505] (C505) | C505
| 246 | [C506] (C506) | C506
| 247 | [C507] (C507) | C507
| 248 | [C508] (C508) | C508
| 249 | [C509] (C509) | C509
| 250 | [C510] (C510) | C510
| 251 | [C511] (C511) | C511
| 252 | [C512] (C512) | C512
| 253 | [C513] (C513) | C513
| 254 | [C514] (C514) | C514
| 255 | [C515] (C515) | C515
| 256 | [C600] (C600) | C600
| 257 | [C601] (C601) | C601
| 258 | [C602] (C602) | C602
| 259 | [C603] (C603) | C603
| 260 | [C604] (C604) | C604
| 261 | [C605] (C605) | C605
| 262 | [C606] (C606) | C606
| 263 | [C607] (C607) | C607
| 264 | [C608] (C608) | C608
| 265 | [C609] (C609) | C609
| 266 | [C610] (C610) | C610
| 267 | [C611] (C611) | C611
| 268 | [C612] (C612) | C612
| 269 | [C613] (C613) | C613
| 270 | [C614] (C614) | C614
| 271 | [C615] (C615) | C615
| 272 | [DI1 (Low level)] (L1L) | Digital input DI1 (low level)
| 273 | [DI2 (Low level)] (L2L) | Digital input DI2 (low level)
| 274 | [DI3 (Low level)] (L3L) | Digital input DI3 (low level)
| 275 | [DI4 (Low level)] (L4L) | Digital input DI4 (low level)
| 276 | [DI5 (Low level)] (L5L) | Digital input DI5 (low level)
| 277 | [DI6 (Low level)] (L6L) | Digital input DI6 (low level)
| 278 | [DI7 (Low level)] (L7L) | Digital input DI7 (low level)
| 279 | [DI8 (Low level)] (L8L) | Digital input DI8 (low level)
| 282 | [DI11 (Low level)] (L11L) | Digital input DI1 (low level)
| 283 | [DI12 (Low level)] (L12L) | Digital input DI12 (low level)
| 284 | [DI13 (Low level)] (L13L) | Digital input DI13 (low level)
| 285 | [DI14 (Low level)] (L14L) | Digital input DI14 (low level)
| 286 | [DI15 (Low level)] (L15L) | Digital input DI15 (low level)
| 287 | [DI16 (Low level)] (L16L) | Digital input DI16 (low level)
| 302 | [DI50 (High Level)] (D50H) | Digital Input DI50 (High level)
| 303 | [DI51 (High Level)] (D51H) | Digital Input DI51 (High level)
| 304 | [DI52 (High Level)] (D52H) | Digital Input DI52 (High level)
| 305 | [DI53 (High Level)] (D53H) | Digital Input DI53 (High level)
| 306 | [DI54 (High Level)] (D54H) | Digital Input DI54 (High level)
| 307 | [DI55 (High Level)] (D55H) | Digital Input DI55 (High level)
| 308 | [DI56 (High Level)] (D56H) | Digital Input DI56 (High level)
| 309 | [DI57 (High Level)] (D57H) | Digital Input DI57 (High level)
| 310 | [DI58 (High Level)] (D58H) | Digital Input DI58 (High level)
| 311 | [DI59 (High Level)] (D59H) | Digital Input DI59 (High level)
| 312 | [DI50 (Low level)] (D50L) | Digital input DI50 (low level)
| 313 | [DI51 (Low level)] (D51L) | Digital input DI51 (low level)
| 314 | [DI52 (Low level)] (D52L) | Digital input DI52 (low level)
| 315 | [DI53 (Low level)] (D53L) | Digital input DI53 (low level)
| 316 | [DI54 (Low level)] (D54L) | Digital input DI54 (low level)
| 317 | [DI55 (Low level)] (D55L) | Digital input DI55 (low level)
| 318 | [DI56 (Low level)] (D56L) | Digital input DI56 (low level)
| 319 | [DI57 (Low level)] (D57L) | Digital input DI57 (low level)
| 320 | [DI58 (Low level)] (D58L) | Digital input DI58 (low level)
| 321 | [DI59 (Low level)] (D59L) | Digital input DI59 (low level)
| 322 | [DI60 (High Level)] (D60H) | Digital Input DI60 (High level)
| 323 | [DI60 (Low level)] (D60L) | Digital input DI60 (low level)
| 324 | [DI61 (High Level)] (D61H) | Digital Input DI61 (High level)
| 325 | [DI61 (Low level)] (D61L) | Digital input DI61 (low level)
| 326 | [DI62 High Assignment] (D62H) | DI62 High Assignment
| 327 | [DI63 High Assignment] (D63H) | DI63 High Assignment
| 328 | [DI64 High Assignment] (D64H) | DI64 High Assignment
| 329 | [DI62 Low Assignment] (D62L) | DI62 Low Assignment
| 330 | [DI63 Low Assignment] (D63L) | DI63 Low Assignment
| 331 | [DI64 Low Assignment] (D64L) | DI64 Low Assignment
| 332 | [C712] (C712) | C712
| 333 | [C713] (C713) | C713
| 334 | [C714] (C714) | C714
| 335 | [C715] (C715) | C715
| 346 | [Dry Run Warning] (DRYA) | Dry run warning
| 352 | [Pump Cycle Warning] (PCPA) | Pump Cycle warning
| 369 | [M/S Device Warn] (MSDA) | M/S device warning
| 371 | [Local] (LOCC) | Local
| 372 | [QF1 Start Command ] (QF0C) | Circuit breaker QF1 start command
| 373 | [QF1 Stop Command ] (QF0O) | Circuit breaker QF1 stop command
| 374 | [QF91 Start Command] (QF4C) | Circuit breaker QF91 start command
| 375 | [QF91 Stop Command] (QF4O) | Circuit breaker QF91 stop command
| 376 | [QF1 Closed] (CBCL) | Circuit breaker QF1 Closed
| 377 | [POE State] (POE) | POE state
| 378 | [Transfer To Drive In Progress] (TTDI) | Transfer to drive in progress
| 379 | [SD Ready To Transfer] (RTTD) | Ready to transfer to drive
| 380 | [Transfer To Mains In Progress] (TTMI) | Transfer to mains in progress
| 381 | [SM Ready To Transfer] (RTTM) | Ready to transfer to mains
| 383 | [None] (CFRS)
| 474 | [Temp Sens AI1 Warn] (TS1A) | Temperature sensor AI1 warning
| 476 | [Temp Sens AI3 Warn] (TS3A) | Temperature sensor AI3 warning
| 477 | [Temp Sens AI4 Warn] (TS4A) | Temperature sensor AI4 warning
| 478 | [Temp Sens AI5 Warn] (TS5A) | Temperature sensor AI5 warning
| 479 | [QF2 Start Command ] (QF2C) | Circuit breaker QF2 start command
| 480 | [QF2 Stop Command ] (QF2O) | Circuit breaker QF2 stop command
| 484 | [Cust Warning 5] (CAS5) | Customer Warning 5
| 485 | [AI1 Th Warning] (TP1A) | AI1 thermal sensor warning
| 486 | [Torque ref. channel] (TR1) | Torque reference channel
| 487 | [Torque ref. 2 channel] (TR2) | Torque reference channel 2
| 491 | [Power Cons Warning] (POWD) | Power Consumption Warning
| 492 | [Warning Grp 4] (AG4) | Warning group 4
| 493 | [Warning Grp 5] (AG5) | Warning group 5
| 494 | [Fallback speed] (FRF) | Fallback speed
| 495 | [Speed Maintained] (RLS) | Speed maintained
| 496 | [Per Type of Stop] (STT) | Per type of stop
| 497 | [Life Cycle Warn 1] (LCA1) | Life Cycle Warning 1
| 498 | [Life Cycle Warn 2] (LCA2) | Life Cycle Warning 2
| 500 | [AI3 Th Warning] (TP3A) | AI3 thermal sensor warning
| 501 | [AI4 Th Warning] (TP4A) | AI4 thermal sensor warning
| 502 | [AI5 Th Warning] (TP5A) | AI5 thermal sensor warning
| 503 | [AI5 4-20 Loss Warn] (AP5) | AI5 4-20 Loss Warning
| 504 | [Fan Counter Warning] (FCTA) | Fan Counter Warning
| 505 | [Fan Feedback Warn] (FFDA) | Fan Feedback Warning
| 506 | [Power High Threshold] (PTHA) | Power High Threshold
| 507 | [Power Low Threshold] (PTHL) | Power Low Threshold
| 508 | [Cust Warning 1] (CAS1) | Customer Warning 1
| 509 | [Cust Warning 2] (CAS2) | Customer Warning 2
| 510 | [Cust Warning 3] (CAS3) | Customer Warning 3
| 511 | [Cust Warning 4] (CAS4) | Customer Warning 4
PSLIN | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Drive in operating state "Fault"
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 486 | [Torque ref. channel] (TR1) | Torque reference channel
| 487 | [Torque ref. 2 channel] (TR2) | Torque reference channel 2
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 1
| 128 | [Yes] (YES) | Yes
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 18 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 19 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 129 | [DI1] (LI1) | Digital Input 1
| 130 | [DI2] (LI2) | Digital Input 2
| 131 | [DI3] (LI3) | Digital Input 3
| 132 | [DI4] (LI4) | Digital Input 4
| 133 | [DI5] (LI5) | Digital Input 5
| 134 | [DI6] (LI6) | Digital Input 6
| 135 | [DI7] (LI7) | Digital input 7
| 136 | [DI8] (LI8) | Digital input 8
| 139 | [DI11] (LI11) | Digital Input 11
| 140 | [DI12] (LI12) | Digital Input 12
| 141 | [DI13] (LI13) | Digital Input 13
| 142 | [DI14] (LI14) | Digital Input 14
| 143 | [DI15] (LI15) | Digital Input 15
| 144 | [DI16] (LI16) | Digital Input 16
| 272 | [DI1 (Low level)] (L1L) | Digital input DI1 (low level)
| 273 | [DI2 (Low level)] (L2L) | Digital input DI2 (low level)
| 274 | [DI3 (Low level)] (L3L) | Digital input DI3 (low level)
| 275 | [DI4 (Low level)] (L4L) | Digital input DI4 (low level)
| 276 | [DI5 (Low level)] (L5L) | Digital input DI5 (low level)
| 277 | [DI6 (Low level)] (L6L) | Digital input DI6 (low level)
| 278 | [DI7 (Low level)] (L7L) | Digital input DI7 (low level)
| 279 | [DI8 (Low level)] (L8L) | Digital input DI8 (low level)
| 282 | [DI11 (Low level)] (L11L) | Digital input DI1 (low level)
| 283 | [DI12 (Low level)] (L12L) | Digital input DI12 (low level)
| 284 | [DI13 (Low level)] (L13L) | Digital input DI13 (low level)
| 285 | [DI14 (Low level)] (L14L) | Digital input DI14 (low level)
| 286 | [DI15 (Low level)] (L15L) | Digital input DI15 (low level)
| 287 | [DI16 (Low level)] (L16L) | Digital input DI16 (low level)
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 209 | [C301] (C301) | Bit 1 Com Module ctrl word
| 210 | [C302] (C302) | Bit 2 Com Module ctrl word
| 211 | [C303] (C303) | Bit 3 Com Module ctrl word
| 212 | [C304] (C304) | Bit 4 Com Module ctrl word
| 213 | [C305] (C305) | Bit 5 Com Module ctrl word
| 214 | [C306] (C306) | Bit 6 Com Module ctrl word
| 215 | [C307] (C307) | Bit 7 Com Module ctrl word
| 216 | [C308] (C308) | Bit 8 Com Module ctrl word
| 217 | [C309] (C309) | Bit 9 Com Module ctrl word
| 218 | [C310] (C310) | Bit 10 Com Module ctrl word
| 219 | [C311] (C311) | Bit 11 Com Module ctrl word
| 220 | [C312] (C312) | Bit 12 Com Module ctrl word
| 221 | [C313] (C313) | Bit 13 Com Module ctrl word
| 222 | [C314] (C314) | Bit 14 Com Module ctrl word
| 223 | [C315] (C315) | Bit 15 Com Module ctrl word
| 241 | [C501] (C501) | C501
| 242 | [C502] (C502) | C502
| 243 | [C503] (C503) | C503
| 244 | [C504] (C504) | C504
| 245 | [C505] (C505) | C505
| 246 | [C506] (C506) | C506
| 247 | [C507] (C507) | C507
| 248 | [C508] (C508) | C508
| 249 | [C509] (C509) | C509
| 250 | [C510] (C510) | C510
| 251 | [C511] (C511) | C511
| 252 | [C512] (C512) | C512
| 253 | [C513] (C513) | C513
| 254 | [C514] (C514) | C514
| 255 | [C515] (C515) | C515
| 257 | [C601] (C601) | C601
| 258 | [C602] (C602) | C602
| 259 | [C603] (C603) | C603
| 260 | [C604] (C604) | C604
| 261 | [C605] (C605) | C605
| 262 | [C606] (C606) | C606
| 263 | [C607] (C607) | C607
| 264 | [C608] (C608) | C608
| 265 | [C609] (C609) | C609
| 266 | [C610] (C610) | C610
| 267 | [C611] (C611) | C611
| 268 | [C612] (C612) | C612
| 269 | [C613] (C613) | C613
| 270 | [C614] (C614) | C614
| 271 | [C615] (C615) | C615
| 332 | [C712] (C712) | C712
| 333 | [C713] (C713) | C713
| 334 | [C714] (C714) | C714
| 335 | [C715] (C715) | C715
| 302 | [DI50 (High Level)] (D50H) | Digital Input DI50 (High level)
| 303 | [DI51 (High Level)] (D51H) | Digital Input DI51 (High level)
| 304 | [DI52 (High Level)] (D52H) | Digital Input DI52 (High level)
| 305 | [DI53 (High Level)] (D53H) | Digital Input DI53 (High level)
| 306 | [DI54 (High Level)] (D54H) | Digital Input DI54 (High level)
| 307 | [DI55 (High Level)] (D55H) | Digital Input DI55 (High level)
| 308 | [DI56 (High Level)] (D56H) | Digital Input DI56 (High level)
| 309 | [DI57 (High Level)] (D57H) | Digital Input DI57 (High level)
| 310 | [DI58 (High Level)] (D58H) | Digital Input DI58 (High level)
| 311 | [DI59 (High Level)] (D59H) | Digital Input DI59 (High level)
| 322 | [DI60 (High Level)] (D60H) | Digital Input DI60 (High level)
| 324 | [DI61 (High Level)] (D61H) | Digital Input DI61 (High level)
| 326 | [DI62 High Assignment] (D62H) | DI62 High Assignment
| 327 | [DI63 High Assignment] (D63H) | DI63 High Assignment
| 328 | [DI64 High Assignment] (D64H) | DI64 High Assignment
| 312 | [DI50 (Low level)] (D50L) | Digital input DI50 (low level)
| 313 | [DI51 (Low level)] (D51L) | Digital input DI51 (low level)
| 314 | [DI52 (Low level)] (D52L) | Digital input DI52 (low level)
| 315 | [DI53 (Low level)] (D53L) | Digital input DI53 (low level)
| 316 | [DI54 (Low level)] (D54L) | Digital input DI54 (low level)
| 317 | [DI55 (Low level)] (D55L) | Digital input DI55 (low level)
| 318 | [DI56 (Low level)] (D56L) | Digital input DI56 (low level)
| 319 | [DI57 (Low level)] (D57L) | Digital input DI57 (low level)
| 320 | [DI58 (Low level)] (D58L) | Digital input DI58 (low level)
| 321 | [DI59 (Low level)] (D59L) | Digital input DI59 (low level)
| 323 | [DI60 (Low level)] (D60L) | Digital input DI60 (low level)
| 325 | [DI61 (Low level)] (D61L) | Digital input DI61 (low level)
| 329 | [DI62 Low Assignment] (D62L) | DI62 Low Assignment
| 330 | [DI63 Low Assignment] (D63L) | DI63 Low Assignment
| 331 | [DI64 Low Assignment] (D64L) | DI64 Low Assignment
PSS | 0 | [Not locked] (NACT) | Pre-settings not locked
| 1 | [Locked] (ACT) | Pre-settings locked
PSST | 0 | [No password defined] (NO) | No password defined
| 1 | [Password is unlocked] (ULK) | Password is unlocked
| 2 | [Password is locked] (LOCK) | Password is locked
PST | 0 | [Stop Key No Priority] (NO) | Stop key no priority
| 1 | [Stop Key Priority] (YES) | Stop key priority
PVIS | 0 | [Active] (ACT) | Active parameters
| 1 | [All] (ALL) | All parameters
QF0S | 0 | [Not Configured] (NO) | Circuit Breaker Not Configured
| 1 | [In Start Pulse] (CBST) | Circuit Breaker In Start Pulse
| 2 | [Not Closed] (CBNC) | Circuit Breaker Not Closed
| 3 | [Closed] (CBCS) | Circuit Breaker Closed
| 4 | [In Stop Pulse] (CBSP) | Circuit Breaker In Stop Pulse
| 5 | [Not Open] (CBNO) | Circuit Breaker Not Open
| 6 | [Open] (CBOS) | Circuit Breaker Open
QSTD | 2 | [Fast stop then disable voltage] (FST2) | Fast stop then disable voltage
| 6 | [Fast stop then stay in quick stop state] (FST6) | Fast stop then stay in quick stop state
RDS | 0 | [Auto] (AUTO) | Auto detected
| 1 | [10M. full] (10F) | 10Mbps full duplex
| 2 | [10M. half] (10H) | 10Mbps half duplex
| 3 | [100M. full] (100F) | 100Mbps full duplex
| 4 | [100M. half] (100H) | 100Mbps half duplex
REFQ | 3 | [3 kHz] (3K) | 3 kHz
| 4 | [4 kHz] (4K) | 4 kHz
| 5 | [5 kHz] (5K) | 5 kHz
| 6 | [6 kHz] (6K) | 6 kHz
| 7 | [7 kHz] (7K) | 7 kHz
| 8 | [8 kHz] (8K) | 8 kHz
| 9 | [9 kHz] (9K) | 9 kHz
| 10 | [10 kHz] (10K) | 10 kHz
| 11 | [11 kHz] (11K) | 11 kHz
| 12 | [12 kHz] (12K) | 12 kHz
RPPN | 0 | [2 poles] (2P) | 2 poles
| 1 | [4 poles] (4P) | 4 poles
| 2 | [6 poles] (6P) | 6 poles
| 3 | [8 poles] (8P) | 8 poles
RPR | 0 | [No] (NO) | No
| 2 | [Run Time Reset] (RTH) | Run time reset
| 3 | [Internal Run Time Reset] (RTHI) | Internal runtime reset
| 4 | [Power ON Time Reset] (PTH) | Power ON time reset
| 7 | [Reset Fan Counter] (FTH) | Reset fan counter
| 8 | [In Power ON Time Reset] (PTHI) | Internal Power ON Time Reset
| 9 | [Clear GTHI] (GTHI) | Clear GTHI
| 10 | [Clear LTHI] (LTHI) | Clear LTHI
| 11 | [Clear NSM] (NSM) | Clear NSM
| 12 | [Clear NSMI] (NSMI) | Clear NSMI
| 45 | [Clear QF1] (QFP0) | Clear QF1
| 46 | [Clear QF3] (QFP3) | Clear QF3
| 47 | [ClearQF91] (QFP4) | ClearQF91
| 48 | [Clear NSV] (NSV) | Clear NSV
| 49 | [Clear NSVI] (NSVI) | Clear NSVI
| 64 | [Reset all ] (ALL) | Reset all counters
RPT | 0 | [Linear] (LIN) | Linear ramp
| 1 | [S-Ramp] (S) | S-Ramp
| 2 | [U-Ramp] (U) | U-Ramp
| 3 | [Customized] (CUS) | Ramp customized
SCS | 0 | [No] (NO) | No
| 1 | [Config 0] (STR0) | Save configuration 0
| 2 | [Config 1] (STR1) | Save configuration 1
| 3 | [Config 2] (STR2) | Save configuration 2
| 4 | [Config 3] (STR3) | Config 3
SFDR | 0 | [Initialization] (INIT) | Initialization
| 1 | [Not Active] (IDLE) | Not active
| 2 | [Operational] (OPE) | Operational
| 4 | [Ready] (RDY) | Ready
| 5 | [IP Configuration] (IPC) | IP configuration
| 7 | [Not Configured] (UNCF) | Not configured
| 8 | [Reading Configuration] (GET) | Reading configuration
| 9 | [Writing Configuration] (SET) | Writing Configuration
| 10 | [Applying Configuration] (APP) | Applying configuration
SIMM | 0 | [No] (NO) | No
| 1 | [Simulation 1] (SIM1) | Simulation 1
| 2 | [Simulation 2] (SIM2) | Simulation 2
SLPM | 0 | [No] (NO) | No
| 1 | [Switch] (SW) | Switch
| 3 | [Speed] (SPD) | Speed
| 4 | [Power] (PWR) | Power
| 6 | [Multiple] (OR) | Multiple
SMOT | 0 | [No info.] (NO) | No information
| 1 | [Low salient] (LLS) | Low saliency
| 2 | [Med salient] (MLS) | Medium saliency
| 3 | [High salient] (HLS) | High saliency
SSCD | 0 | [Undefined] (UND) | Undefined
| 1 | [Binary code] (BIN) | Binary code
| 2 | [Gray code] (GRAY) | Gray code
SSCP | 0 | [Undefined] (UND) | Undefined
| 1 | [No parity] (NO) | No parity
| 3 | [Even parity] (EVEN) | Even parity
SSL | 0 | [Standard] (STD) | Standard
| 1 | [High Perf] (HPF) | High performance
STM | 0 | [No Synchronization] (NO) | No synchronization
| 1 | [Synchro Pending] (PEND) | Synchronization pending
| 2 | [Acc To Mains] (ACC) | Acceleration to mains frequency
| 3 | [Stabilization To Mains] (STAB) | Stabilization to mains frequency
| 4 | [Synchronization] (SYNC) | Synchronization
| 5 | [Synchro Stabilization] (SYST) | Synchronization stabilization
| 6 | [Ready To Transfer] (RTT) | Ready to transfer
| 7 | [Transfer In Progress] (TTI) | Transfer in progress
| 8 | [Synchronization Error] (STF) | Synchronization error
STP | 0 | [Inactive] (NO) | Inactive
| 4 | [Freewheel Stop] (LNF) | Locked in freewheel stop without error
STR | 0 | [No Save] (NO) | No save
| 1 | [Save to RAM] (RAM) | Save to RAM
| 2 | [Save to EEPROM] (EEP) | Save to EEPROM
STT | 0 | [On Ramp] (RMP) | On ramp
| 2 | [Freewheel Stop] (NST) | Freewheel stop
STUN | 0 | [Default] (TAB) | Default
| 1 | [Measure] (MEAS) | Measure
| 2 | [Custom] (CUS) | Custom
SUCU | 0 | [Euro] (EURO) | Euro
| 1 | [$] (DOLLAR) | $
| 2 | [£] (POUND) | £
| 3 | [Krone] (KR) | Krone
| 4 | [Renminbi] (RMB) | Renminbi
| 5 | [Other] (OTHER) | Other
SUFR | 0 | [1 L/s] (1LS) | 1 L/s
| 1 | [0.1 l/s] (01LS) | 0.1 l/s
| 2 | [1 L/mn] (1LM) | 1 L/mn
| 3 | [1 L/h] (1LH) | 1 L/h
| 4 | [1 dm3/mn] (1DM3M) | 1 dm3/mn
| 5 | [1 m3/s] (1M3S) | 1 m3/s
| 6 | [0.1 m3/s] (01M3S) | 0.1 m3/s
| 7 | [1 m3/mn] (1M3MN) | 1 m3/mn
| 8 | [0.1 m3/mn] (01M3MN) | 0.1 m3/mn
| 9 | [1 m3/h] (1M3H) | 1 m3/h
| 10 | [0.1 m3/h] (01M3H) | 0.1 m3/h
| 11 | [1 gal/s] (1GPS) | 1 gal/s
| 12 | [1 GPM] (1GPM) | 1 GPM
| 13 | [1 gal/h] (1GPH) | 1 gal/h
| 14 | [1 ft3/s] (1CFS) | 1 ft3/s
| 15 | [1 CFM] (1CFM) | 1 CFM
| 16 | [1 SCFM] (1SCFM) | 1 SCFM
| 17 | [1 ft3/h] (1CFH) | 1 ft3/h
| 18 | [1 Kg/s] (1KGS) | 1 Kg/s
| 19 | [1 Kg/mn] (1KGM) | 1 Kg/mn
| 20 | [1 Kg/h] (1KGH) | 1 Kg/h
| 21 | [1 Lb/s] (1LBS) | 1 Lb/s
| 22 | [1 Lb/mn] (1LBM) | 1 Lb/mn
| 23 | [1 Lb/h] (1LBH) | 1 Lb/h
| 24 | [0.1 %] (01PC) | 0.1 %
| 25 | [0.1] (01WO) | 0.1
| 26 | [0.1 dam3/h] (01DA3H) | 0.1 dam3/h
| 27 | [0.01 dam3/h] (10M3H) | 0.01 dam3/h
| 28 | [0.1 kilo-GPM] (01KGPM) | 0.1 kilo-GPM
| 29 | [0.01 kilo-GPM] (10GPM) | 0.01 kilo-GPM
| 30 | [1 ton/h] (1TONH) | 1 ton/h
| 31 | [0.1 ton/h] (01TONH) | 0.1 ton/h
| 32 | [0.01 ton/h] (10KGH) | 0.01 ton/h
| 33 | [1 kilo-lb/h] (1KLBH) | 1 kilo-lb/h
| 34 | [0.1 kilo-lb/h] (01KLBH) | 0.1 kilo-lb/h
| 35 | [0.01 kilo-lb/h] (10LBH) | 0.01 kilo-lb/h
SUPR | 0 | [1 Kpa] (1KPA) | 1 Kpa
| 1 | [1 mbar] (1MBAR) | 1 mbar
| 2 | [1 Bar] (1BAR) | 1 Bar
| 3 | [0.1 Bar] (01BAR) | 0.1 Bar
| 4 | [0.01 Bar] (001BAR) | 0.01 Bar
| 5 | [1 Psi] (1PSI) | 1 Psi
| 6 | [0.1 Psi] (01PSI) | 0.1 Psi
| 7 | [1 Psig] (1PSIG) | 1 Psig
| 8 | [0.1 Psig] (01PSIG) | 0.1 Psig
| 9 | [1 inH2O] (1INH20) | 1 inH2O
| 10 | [1 inWg] (1INWG) | 1 inWg
| 11 | [1 inWC] (1INWC) | 1 inWC
| 12 | [1 ftWg] (1FTWG) | 1 ftWg
| 13 | [1 ftWc] (1FTWC) | 1 ftWc
| 14 | [1 ft] (1FT) | 1 ft
| 15 | [1 mWg] (1MWG) | 1 mWg
| 16 | [0.1 mWg] (01MWG) | 0.1 mWg
| 17 | [1 mWC] (1MWC) | 1 mWC
| 18 | [0.1 mWc] (01MWC) | 0.1 mWc
| 19 | [1 m] (1M) | 1 m
| 20 | [0.1 m ] (01M) | 0.1 m
| 21 | [1 inHg] (1INHG) | 1 inHg
| 22 | [0.1 %] (01PC) | 0.1 %
| 23 | [0.1] (01WO) | 0.1
SUTP | 0 | [0.1°C] (01C) | 0.1°C
| 1 | [0.1°F] (01F) | 0.1°F
TBR | 4 | [Automatic] (AUTO) | Automatic
| 8 | [300 bps] (300) | 300 bps
| 12 | [600 bps] (600) | 600 bps
| 16 | [1.2 Kbps] (1200) | 1.2 Kbps
| 20 | [2.4 Kbps] (2400) | 2.4 Kbps
| 24 | [4800 bps] (4800) | 4800 bps
| 28 | [9600 bps] (9600) | 9600 bps
| 30 | [10 Kbps] (10000) | 10 Kbps
| 32 | [19200 bps] (19200) | 19200 bps
| 34 | [20 Kbps] (20000) | 20 Kbps
| 35 | [28.8 Kbps] (28800) | 28.8 Kbps
| 36 | [38.4 Kbps] (38400) | 38.4 Kbps
| 37 | [45.45 Kbps] (45450) | 45.45 Kbps
| 38 | [50 Kbps] (50000) | 50 Kbps
| 40 | [57.6 Kbps] (57600) | 57.6 Kbps
| 41 | [76.8 Kbps] (76800)
| 42 | [93.75 Kbps] (93750) | 93.75 Kbps
| 44 | [100 Kbps] (100K) | 100 Kbps
| 48 | [115.2 Kbps] (115K2) | 115.2 Kbps
| 52 | [125 Kbps] (125K) | 125 Kbps
| 53 | [156 Kbps] (156K) | 156 Kbps
| 54 | [187.5 Kbps] (187K5) | 187.5 Kbps
| 56 | [230.4 Kbps] (230K4) | 230.4 Kbps
| 60 | [250 Kbps] (250K) | 250 Kbps
| 64 | [460.8 Kbps] (460K8) | 460.8 Kbps
| 68 | [500 Kbps] (500K) | 500 Kbps
| 69 | [625 Kbps] (625K) | 625 Kbps
| 70 | [800 Kbps] (800K) | 800 Kbps
| 72 | [921.6 Kbps] (921K6) | 921.6 Kbps
| 76 | [1 Mbps] (1M) | 1 Mbps
| 80 | [1.5 Mbps] (1M5) | 1.5 Mbps
| 81 | [2.5 Mbps] (2M5) | 2.5 Mbps
| 82 | [3 Mbps] (3M) | 3 Mbps
| 83 | [6 Mbps] (6M) | 6 Mbps
| 84 | [10 Mbps] (10M) | 10 Mbps
| 86 | [5 Mbps] (5M) | 5 Mbps
| 88 | [12 Mbps] (12M) | 12 Mbps
| 92 | [100 Mbps] (100M) | 100 Mbps
TCC | 0 | [2-Wire Control] (2C) | 2-wire control
| 1 | [3-Wire Control] (3C) | 3-wire control
TCT | 0 | [Level] (LEL) | Level
| 1 | [Transition] (TRN) | Transition
| 2 | [Level With Fwd Priority] (PFO) | Level with Forward priority
THET | 0 | [None] (NONE) | None
| 1 | [PTC] (PTC) | PTC
| 2 | [PT100] (1PT2) | PT100
| 3 | [PT1000] (1PT3) | PT1000
| 4 | [KTY] (KTY) | KTY
| 5 | [Klixon] (KLIX) | Klixon
THT | 0 | [No] (NO) | No thermal monitoring
| 1 | [Self cooled] (ACL) | Self cooled motor
| 2 | [Force-cool] (FCL) | Force cooled motor
TLOL | 0 | [Disabled] (DIS) | Disabled
| 1 | [Error Triggered] (TRIP) | Error triggered
| 2 | [Reduce to I Nom Drive] (LIM) | Reduce to drive nominal current
TOB | 0 | [Warning] (ALRM) | Warning
| 1 | [Error] (FLT) | Error
TOCT | 0 | [NA] (NA) | NA
| 1 | [PRESSURE] (PRESS) | PRESSURE
| 2 | [FLOW] (FLOW) | FLOW
| 3 | [OTHER] (OTHER) | OTHER
TRES | 0 | [0.3] (03) | 0.3
| 1 | [0.5] (05) | 0.5
| 2 | [0.8] (08) | 0.8
| 3 | [1.0] (10) | 1.0
TST | 0 | [Speed] (SPD) | Speed
| 1 | [Freewheel] (NST) | Freewheel stop
| 2 | [Spin] (SPN) | Spin
TUNU | 0 | [No] (NO) | No
| 1 | [Therm mot] (TM) | Use the motor thermal evolution
TWO | 0 | [OFF] (LOW) | ModBus Word Order OFF
| 1 | [ON] (HIGH) | Modbus Word Order ON
UECP | 0 | [Undefined] (UND) | Undefined
| 2 | [Hiperface] (SCHP) | SinCos Hiperface
| 3 | [SinCos] (SC) | SinCos
| 4 | [SSI] (SSI) | SSI
| 8 | [AB] (AB) | AB
| 9 | [Resolver] (RES) | Resolver
| 10 | [BiSS] (BISS) | BiSS
| 11 | [EnDat 2.2] (EN22) | EnDat 2.2
| 12 | [HTL] (HTL) | HTL encoder
UECV | 0 | [Undefined] (UND) | Undefined
| 5 | [5 Vdc] (5V) | 5 Vdc
| 12 | [12 Vdc] (12V) | 12 Vdc
| 15 | [15 Vdc] (15V) | 15 Vdc
| 24 | [24 Vdc] (24V) | 24 Vdc
ULR | 0 | [Permitted] (ULR0) | Upload access allowed
| 1 | [Not allowed] (ULR1) | Upload access not allow
USB | 0 | [Error Triggered] (0) | Error triggered
| 1 | [Error Triggered w/o Relay] (1) | Error triggered w/o relay
| 2 | [Warning Triggered] (2) | Warning Triggered
VCAL | 0 | [Unknown Voltage] (NO) | Unkown voltage
| 1 | [100-120(1)] (110M) | 100-120 V single phase
| 2 | [100-120(3)] (110T) | 100-120 V three phase
| 3 | [200-240 V single] (220M) | 200-240 V single
| 4 | [200-240 V Three] (220T) | 200-240 V three phase
| 5 | [380-500(1)] (480M) | 380-500 V single phase
| 6 | [380-500 V Three] (480T) | 380-500 V three phase
| 7 | [500-690(1)] (690M) | 500-690 V single phase
| 8 | [500-690 V Three] (690T) | 500-690 V three phase
| 9 | [600(1)] (600M) | 600 V single phase
| 10 | [600 V Three] (600T) | 600 V three phase
| 11 | [1.0KV Three Phase] (1K0T) | 1.0KV three phase
| 12 | [2.4KV Three Phase] (2K4T) | 2.4KV three phase
| 13 | [3.0KV Three Phase] (3K0T) | 3.0KV three phase
| 14 | [3.3KV Three Phase] (3K3T) | 3.3KV three phase
| 15 | [4.16KV Three Phase] (4K2T) | 4.16KV three phase
| 16 | [5.0KV Three Phase] (5K0T) | 5.0KV three phase
| 17 | [5.5KV Three Phase] (5K5T) | 5.5KV three phase
| 18 | [6.0KV Three Phase] (6K0T) | 6.0KV three phase
| 19 | [6.3KV Three Phase] (6K3T) | 6.3KV three phase
| 20 | [6.6KV Three Phase] (6K6T) | 6.6KV three phase
| 21 | [6.9KV Three Phase] (6K9T) | 6.9KV three phase
| 22 | [10KV Three Phase] (10KT) | 10KV three phase
| 23 | [11KV Three Phase] (11KT) | 11KV three phase
| 24 | [13.8KV Three Phase] (14KT) | 13.8KV three phase
WUPM | 0 | [Feedback] (FBK) | Feedback
| 1 | [Error] (ERR) | Error

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2 | Reserved (= 0).
|  | Bit 3 | Reserved (= 0).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CMD | Possible values in CiA402 profile, separate or not separate mode:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
CMP2 |  | Bit 2 | Quick stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
CMP8 |  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
CMP9 |  | Bit 9 | Reserved (set to 0).
CMPA |  | Bit 10 | Reserved (set to 0).
CMPB |  | Bit 11 to 15 | Can be assigned to commands.
CMPC | Possible values in the IO profile on state command [2 wire] (2C).
CMPD |  | Bit 0 | Forward (on state) command
CMPE
CMPF
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
|  | Bit 1 to 15 | Can be assigned to commands.
Possible values in the IO profile on edge command [3 wire] (3C).
|  | Bit 0 | Stop (run authorization).
|  | Bit 1 | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
|  | Bit 2 to 15 | can be assigned to commands.
ETA | Possible values in CiA402 profile, separate or not separate mode:
EP0 |  | Bit 0
EP1 |  | Bit 1
EP2 |  | Bit 2
EP3 |  | Bit 3
EP4 |  | Bit 4 | "Voltage enabled", power part connected to supply mains
EP5
EP6
EP7 |  |  | When the drive is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop
EP9 |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
EPA |  | Bit 7 | Bit 7: Warning
EPB
EPC
EPD |  | Bit 8 | Bit 8: Reserved (= 0)
EPE |  | Bit 9 | Bit 9: Remote: command or reference via fieldbus
EPF
ETAD
|  | Bit 10 | Bit 10: Target reference reached
When the drive is in speed mode, this is the reference frequency.
|  | Bit 11 | Bit 11: "Internal limit active", reference outside limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
|  | Bit 15 | Bit 15: "Direction", direction of rotation
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (refer to fieldbus manuals).
ETI |  | Bit 0
IP0 |  | Bit 1
IP1
IP2 |  | Bit 2
IP3
IP4 |  | Bit 3 | Bit 3: Reserved (= 0).
IP5 |  | Bit 4
IP6 |  | Bit 5
IP7 |  | Bit 6
IP8
IP9 |  | Bit 7
IPA |  | Bit 8
IPB |  | Bit 9
IPC |  | Bit 10
IPD |  | Bit 11
IPE |  | Bit 12
IPF |  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Drive controled by terminal
bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
Bit 15
CRC |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
|  | Bit 10 | Reserved
Bit 11
Bit 12
|  | Bit 13 | Reserved
Bit 14
Bit 15
CCC |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
|  | Bit 10 | Reserved
Bit 11
Bit 12
|  | Bit 13 | Reserved
Bit 14
Bit 15
IL1R |  | Bit 0 | "LI1" logic inputs real image
|  | Bit 1 | "LI2" logic inputs real image
|  | Bit 2 | "LI3" logic inputs real image
|  | Bit 3 | "LI4" logic inputs real image
|  | Bit 4 | "LI5" logic inputs real image
|  | Bit 5 | "LI6" logic inputs real image
|  | Bit 6 | "LI7" logic inputs real image
|  | Bit 7 | "LI8" logic inputs real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs real image
|  | Bit 11 | "LI12" logic inputs real image
|  | Bit 12 | "LI13" logic inputs real image
|  | Bit 13 | "LI14" logic inputs real image
|  | Bit 14 | "LI15" logic inputs real image
|  | Bit 15 | "LI16" logic inputs real image
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | "R3" relay real image
|  | Bit 3 | "R4" relay real image
|  | Bit 4 | "R5" relay real image
|  | Bit 5 | "R6" relay real image
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | "DO1" logic outputs real image
|  | Bit 9 | "DO2" logic outputs real image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | "DO11" logic outputs real image
|  | Bit 13 | "DO12" logic outputs real image
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
|  | Bit 5 | Reserved (=0).
|  | Bit 6 | Reserved (=0).
|  | Bit 7 | Reserved (=0).
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
If one of these events occurs, the drive will trigger an error [Invalid configiguration] (CFI) and then automatically restore the factory settings.
CNF3 |  | Bit 0 | CNF3 - Modbus timeout
|  | Bit 1 | CNF3 - Network overload
|  | Bit 2 | CNF3 - EIP timeoout
|  | Bit 3 | CNF3 - EIP idle pool
|  | Bit 4 | CNF3 - EIP force trip
|  | Bit 5 | CNF3 - Fast Data lost
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
INFO |  | Bit 0 | PLC Inside compatibility error
|  | Bit 1 | HMI Panel compatibility error
|  | Bit 2 | IO Module configuration error
|  | Bit 3 | PLC Inside not identified
|  | Bit 4 | IO Scanner not running
|  | Bit 5 | IO Scanner not configured
|  | Bit 6 | PLC Inside Run delay timeout
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CRP0 | Bit 0 to Bit 7: Active command channels
CRP1
CRP2
CRP3
CRP4
CRP5
CRP6
CRP7
CRP8
CRP9
CRPA
CRPB
CRPC
CRPD
CRPE
CRPF
Bit 8 to Bit 15: Active reference channels
FRY |  | Bit 0
Bit 1
|  | Bit 2 | Reserved
Bit 3
Bit 4
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
Bit 7
Bit 8
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
Bit 15
EWE |  | Bit 0
Bit 1
IL1I |  | Bit 0 | "LI1" logic inputs physical image
|  | Bit 1 | "LI2" logic inputs physical image
|  | Bit 2 | "LI3" logic inputs physical image
|  | Bit 3 | "LI4" logic inputs physical image
|  | Bit 4 | "LI5" logic inputs physical image
|  | Bit 5 | "LI6" logic inputs physical image
|  | Bit 6 | "LI7" logic inputs physical image
|  | Bit 7 | "LI8" logic inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs physical image
|  | Bit 11 | "LI12" logic inputs physical image
|  | Bit 12 | "LI13" logic inputs physical image
|  | Bit 13 | "LI14" logic inputs physical image
|  | Bit 14 | "LI15" logic inputs physical image
|  | Bit 15 | "LI16" logic inputs physical image
PEV1 |  | Bit 0
Bit 1
Bit 2
Bit 3
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV2 |  | Bit 0
Bit 1
Bit 2
Bit 3
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV3 |  | Bit 0
Bit 1
Bit 2
Bit 3
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV4 |  | Bit 0
Bit 1
Bit 2
Bit 3
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST00 |  | Bit 4 | (SLM) : Stop asked by a "sleeping" function
|  | Bit 8 | (SLPP) : Sleep is pending
|  | Bit 9 | (SLPB) : Sleep Boost phase is running
|  | Bit 10 | (SLP) : Application Sleeping
ST02 |  | Bit 0 | (CNF0) : Configuration 1 is used
|  | Bit 1 | (CNF1) : Configuration 2 is used
|  | Bit 2 | (CNF2) : Configuration 3 is used
|  | Bit 3 | (CNF3) : Configuration 4 is used
|  | Bit 8 | (CFP1) : Parameter set 1 is used
|  | Bit 9 | (CFP2) : Parameter set 2 is used
|  | Bit 10 | (CFP3) : Parameter set 3 is used
ST03 |  | Bit 0 | (FLO) : Drive in forced local mode
|  | Bit 1 | (FR2) : Reference channel is channel 2
|  | Bit 2 | (FR1B) : Reference channel is channel 1, and FR1B is used
|  | Bit 3 | (FR1) : Reference channel is channel 1 (FR1 or FR1B is used)
|  | Bit 4 | (CD1) : Command channel is channel 1
|  | Bit 5 | (CD2) : Command channel is channel 2
|  | Bit 6 | (RFC) : Reference channel : 0-> channel1, 1-> channel 2
|  | Bit 7 | (RCB) : 0: FR1, FR1B ?
|  | Bit 8 | (CCS) : Command channel : 0-> channel 1, 1-> channel 2
|  | Bit 9 | (BMP) : Bump Less Channel
|  | Bit 10 | (RTTM) : Synchronization to main status
|  | Bit 11 | (TTMI) : Transfer to main in progress
|  | Bit 12 | (RTTD) : Synchronization to drive status
|  | Bit 13 | (TTDI) : Transfer to drive in progress
ST04 |  | Bit 0 | (FLT) : Drive is in fault state
|  | Bit 1 | (AUTO) : Automatic restart attempts in progress
|  | Bit 2 | (RDY) : Drive is in ready state
|  | Bit 3 | (RUN) : A gating order is set (there is potentially current in the motor)
|  | Bit 4 | (DBL) : Powerstage is supply (DC bus charged)
|  | Bit 5 | (CTL) : Controlled stop on power loss in progress
|  | Bit 8 | (FRF) : Reaction on event / fallback speed
|  | Bit 9 | (RLS) : Reaction on event / maintain speed
|  | Bit 10 | (STT) : Reaction on event / Stop on STT without tripping in fault
|  | Bit 12 | (ICC) : Drive is locked when encoder configuration is not complete
|  | Bit 13 | (INI) : Drive is initializing
ST05 |  | Bit 3 | (BLC) : The drive asks to close the brake
|  | Bit 8 | (BSA) : Brake speed alarm
|  | Bit 9 | (BCA) : Brake contact alarm
ST06 |  | Bit 0 | (ACC) : Drive in acceleration
|  | Bit 1 | (DEC) : Drive in deceleration
|  | Bit 2 | (SRA) : Frequency reference reached
|  | Bit 3 | (MFRD) : Motor running in Forward
|  | Bit 4 | (MRRS) : Motor running in Reverse
|  | Bit 5 | (ATS) : Torque on the motor is negative
|  | Bit 7 | (FLU) : Motor fluxing in progress
|  | Bit 8 | (FLX) : Motor fluxed
|  | Bit 9 | (TUN) : Autotune in progress
|  | Bit 10 | (MCP) : Motor current present
|  | Bit 11 | (RP2) : Ramp switching state : 0-> ramp 1, 1-> ramp 2
|  | Bit 12 | (CL2) : Current switching state : 0-> current limit 1, 1-> current limit 2
|  | Bit 13 | (TL2) : Torque switching state : 0-> Torque limit 1, 1-> Torque limit 2
ST07 |  | Bit 0 | (AG1) : One of the alarm of alarm group 1 is active
|  | Bit 1 | (AG2) : One of the alarm of alarm group 2 is active
|  | Bit 2 | (AG3) : One of the alarm of alarm group 3 is active
|  | Bit 3 | (AG4) : One of the alarm of alarm group 4 is active
|  | Bit 4 | (AG5) : One of the alarm of alarm group 5 is active
|  | Bit 8 | (LCA1) : Life Cycle Alarm 1 alarm
|  | Bit 9 | (LCA2) : Life Cycle Alarm 2 alarm
ST08 |  | Bit 0 | (DRYA) : Dry Running Alarm
|  | Bit 6 | (PCPA) : Cyclic Start Protection Alarm
ST09 |  | Bit 0 | (PFA) : alarm on PID Feedback
|  | Bit 1 | (PFAH) : PID feedback high threshold reached
|  | Bit 2 | (PFAL) : PID feedback low threshold reached
|  | Bit 3 | (PISH) : PI feedback monitoring alarm is raised
|  | Bit 11 | (PEE) : alarm on PID error
ST11 |  | Bit 1 | (TP3A) : Temperature Protection AI3 Alarm
|  | Bit 2 | (TP4A) : Temperature Protection AI4 Alarm
|  | Bit 3 | (TP5A) : Temperature Protection AI5 Alarm
|  | Bit 4 | (TP1A) : Temperature Protection AI1 Alarm
|  | Bit 7 | (TPEA) : Temperature Protection Encoder board Alarm
|  | Bit 8 | (TS1A) : Temperature Sensor AI1 Alarm
|  | Bit 10 | (TS3A) : Temperature Sensor AI3 Alarm
|  | Bit 11 | (TS4A) : Temperature Sensor AI4 Alarm
|  | Bit 12 | (TS5A) : Temperature Sensor AI5 Alarm
ST12 |  | Bit 0 | (AP1) : 4-20 loss alarm on AI1
|  | Bit 2 | (AP3) : 4-20 loss alarm on AI3
|  | Bit 3 | (AP4) : 4-20 loss alarm on AI4
|  | Bit 4 | (AP5) : 4-20 loss alarm on AI5
ST13 |  | Bit 0 | (THA) : drive overheating alarm is raised
|  | Bit 2 | (FCTA) : Fan Counter Speed alarm
|  | Bit 3 | (FFDA) : Fan feedback alarm is raised
|  | Bit 5 | (EFA) : external alarm is raised
|  | Bit 6 | (USA) : undervoltage alarm is raised
|  | Bit 7 | (UPA) : controlled stop on power loss threshold id reached
|  | Bit 8 | (OBR) : Impossible to follow the customer ramp during deceleration
|  | Bit 10 | (ERN) : Emergency
ST14 |  | Bit 0 | (FTA) : Motor frequency high threshold 1 reached
|  | Bit 1 | (FTAL) : Motor frequency low threshold 1 reached
|  | Bit 2 | (FQLA) : Frequency level reached (frequency meter)
|  | Bit 3 | (F2AL) : Motor frequency low threshold 2 reached
|  | Bit 4 | (FLA) : HighSpeedReached function result
|  | Bit 5 | (RTAH) : Reference frequency high threshold reached
|  | Bit 6 | (RTAL) : Reference frequency low threshold reached
|  | Bit 7 | (F2A) : Motor frequency high threshold 2 reached
|  | Bit 14 | (MOTW) : Motor parameter scaling Warning
ST15 |  | Bit 0 | (CTA) : Motor current high threshold reached
|  | Bit 1 | (CTAL) : Motor current low threshold reached
|  | Bit 2 | (TTHA) : Motor torque high threshold reached
|  | Bit 3 | (TTLA) : Motor torque low threshold reached
|  | Bit 4 | (ULA) : Underload is detected
|  | Bit 5 | (OLA) : Overload is detected
|  | Bit 6 | (CLI) : current or torque limitation is running
|  | Bit 7 | (SSA) : Timeout on current or torque limitation is reached
|  | Bit 8 | (RTA) : Torque regulation alarm
|  | Bit 9 | (POWD) : Electrical Power Drift alarm
|  | Bit 10 | (PTHA) : Power high threshold reached
|  | Bit 11 | (PTHL) : Power Low threshold reached
|  | Bit 12 | (ANA) : Anti-veering alarm
|  | Bit 14 | (TLI) : torque limitation is running
|  | Bit 15 | (PLI) : power limitation is running
ST16 |  | Bit 1 | (TAD) : DriveThermalThresholdReached function result
|  | Bit 2 | (TSA) : MotorThermalThresholdReached function result (motor 1)
|  | Bit 3 | (TS2) : MotorThermalThresholdReached function result (motor 2)
|  | Bit 4 | (TS3) : MotorThermalThresholdReached function result (motor 3)
|  | Bit 5 | (TS4) : MotorThermalThresholdReached function result (motor 4)
ST17 |  | Bit 0 | (CAS1) : Customer Alarm 1 active
|  | Bit 1 | (CAS2) : Customer Alarm 2 active
|  | Bit 2 | (CAS3) : Customer Alarm 3 active
|  | Bit 3 | (CAS4) : Customer Alarm 4 active
|  | Bit 4 | (CAS5) : Customer Alarm 5 active
ST18 |  | Bit 8 | (CHA) : Cabinet over-heating alarm
ST19 |  | Bit 0 | (IWA) : IO function : Digital warning A
|  | Bit 1 | (IWB) : IO function : Digital warning B
|  | Bit 2 | (IWC) : IO function : Digital warning C
|  | Bit 3 | (IWD) : IO function : Digital warning D
|  | Bit 4 | (CWA) : IO function : Cabinet warning A
|  | Bit 5 | (CWB) : IO function : Cabinet warning B
|  | Bit 6 | (CWC) : IO function : Cabinet warning C
|  | Bit 7 | (TWA) : IO function : Thermal input warning A
|  | Bit 8 | (TWB) : IO function : Thermal input warning B
|  | Bit 9 | (TWC) : IO function : Thermal input warning C
|  | Bit 10 | (TWD) : IO function : Thermal input warning D
ST20 |  | Bit 1 | (MSDA) : Master Slave : Device loss
|  | Bit 2 | (BSQA) : Backlash Sequence : Alarm
|  | Bit 8 | (OBW) : Power Cells Over-braking Light overvoltage warning
|  | Bit 9 | (IGW) : Mains input ground voltage warning
|  | Bit 10 | (OGW) : Motor output ground voltage warning
|  | Bit 11 | (POE) : POE function activated
|  | Bit 12 | (BYW1) : Bypass Poc Warning 1
|  | Bit 13 | (BYW2) : Bypass Poc Warning 2
ST22 |  | Bit 0 | (CW01) : RTC Battery warning
|  | Bit 1 | (CW02) : Cooling Fans not ready warning
|  | Bit 2 | (CW03) : Cabinet over-heat warning
|  | Bit 3 | (CW04) : MVCB Status not OK warning
|  | Bit 4 | (CW05) : Cooling Fan power supply warning
|  | Bit 5 | (CW06) : Auxiliary power supply warning
|  | Bit 6 | (CW07) : LV Surge Arrestor warning
|  | Bit 7 | (CW08) : Fan redundant cooling degraded warning(reserved)
|  | Bit 8 | (CW09) : Shutter incoherent state warning(reserved)
|  | Bit 9 | (CW10) : PLC Cabinet Warning 10 (reserved)
|  | Bit 10 | (CW11) : CB QF2 feedback warning
|  | Bit 11 | (CW12) : CB QF3 feedback warning
|  | Bit 12 | (CW13) : CB QF91 feedback warning
|  | Bit 13 | (CW14) : CB QF11 feedback warning
|  | Bit 14 | (CW15) : Bypass drive switch sequence warning
|  | Bit 15 | (CW16) : PLC Cabinet warning (reserved)
ST23 |  | Bit 0 | (CW17) : Motor thermal winding warning 1
|  | Bit 1 | (CW18) : Motor thermal winding warning 2
|  | Bit 2 | (CW19) : Motor thermal bearing warning 1
|  | Bit 3 | (CW20) : Motor thermal bearing warning 2
|  | Bit 4 | (CW21) : Transformer 1 thermal warning
|  | Bit 5 | (CW22) : Transformer 2 thermal warning
|  | Bit 6 | (CW23) : Drive bypass choke warning (reserved)
|  | Bit 7 | (CW24) : PLC Cabinet Warning 24 (reserved)
|  | Bit 8 | (CW25) : PLC Cabinet Warning 25 (reserved)
|  | Bit 9 | (CW26) : PLC Cabinet Warning 26 (reserved)
|  | Bit 10 | (CW27) : PLC Cabinet Warning 27 (reserved)
|  | Bit 11 | (CW28) : PLC Cabinet Warning 28 (reserved)
|  | Bit 12 | (CW29) : PLC Cabinet Warning 29 (reserved)
|  | Bit 13 | (CW30) : PLC Cabinet Warning 30 (reserved)
|  | Bit 14 | (CW31) : PLC Cabinet Warning 31 (reserved)
|  | Bit 15 | (CW32) : PLC Cabinet Warning 32 (reserved)
ST24 |  | Bit 0 | (AW01) : PLC Application ETO Warning 1
|  | Bit 1 | (AW02) : PLC Application ETO Warning 2
|  | Bit 2 | (AW03) : PLC Application ETO Warning 3
|  | Bit 3 | (AW04) : PLC Application ETO Warning 4
|  | Bit 4 | (AW05) : PLC Application ETO Warning 5
|  | Bit 5 | (AW06) : PLC Application ETO Warning 6
|  | Bit 6 | (AW07) : PLC Application ETO Warning 7
|  | Bit 7 | (AW08) : PLC Application ETO Warning 8
|  | Bit 8 | (AW09) : PLC Application ETO Warning 9
|  | Bit 9 | (AW10) : PLC Application ETO Warning 10
|  | Bit 10 | (AW11) : PLC Application ETO Warning 11
|  | Bit 11 | (AW12) : PLC Application ETO Warning 12
|  | Bit 12 | (AW13) : PLC Application ETO Warning 13
|  | Bit 13 | (AW14) : PLC Application ETO Warning 14
|  | Bit 14 | (AW15) : PLC Application ETO Warning 15
|  | Bit 15 | (AW16) : PLC Application ETO Warning 16
ILCI |  | Bit 0 | "DI50" logic inputs physical image
|  | Bit 1 | "DI51" logic inputs physical image
|  | Bit 2 | "DI52" logic inputs physical image
|  | Bit 3 | "DI53" logic inputs physical image
|  | Bit 4 | "DI54" logic inputs physical image
|  | Bit 5 | "DI55" logic inputs physical image
|  | Bit 6 | "DI56" logic inputs physical image
|  | Bit 7 | "DI57" logic inputs physical image
|  | Bit 8 | "DI58" logic inputs physical image
|  | Bit 9 | "DI59" logic inputs physical image
|  | Bit 10 | "DI60" logic inputs physical image
|  | Bit 11 | "DI61" logic inputs physical image
|  | Bit 12 | "DI62" logic inputs physical image
|  | Bit 13 | "DI63" logic inputs physical image
|  | Bit 14 | "DI64" logic inputs physical image
|  | Bit 15 | Reserved
ILCR |  | Bit 0 | "DI50" logic inputs real image
|  | Bit 1 | "DI51" logic inputs real image
|  | Bit 2 | "DI52" logic inputs real image
|  | Bit 3 | "DI53" logic inputs real image
|  | Bit 4 | "DI54" logic inputs real image
|  | Bit 5 | "DI55" logic inputs real image
|  | Bit 6 | "DI56" logic inputs real image
|  | Bit 7 | "DI57" logic inputs real image
|  | Bit 8 | "DI58" logic inputs real image
|  | Bit 9 | "DI59" logic inputs real image
|  | Bit 10 | "DI60" logic inputs real image
|  | Bit 11 | "DI61" logic inputs real image
|  | Bit 12 | "DI62" logic inputs real image
|  | Bit 13 | "DI63" logic inputs real image
|  | Bit 14 | "DI64" logic inputs real image
|  | Bit 15 | Reserved
ILC2 |  | Bit 0 | "DI70" logic inputs physical image
|  | Bit 1 | "DI71" logic inputs physical image
|  | Bit 2 | "DI72" logic inputs physical image
|  | Bit 3 | "DI73" logic inputs physical image
|  | Bit 4 | "DI74" logic inputs physical image
|  | Bit 5 | "DI75" logic inputs physical image
|  | Bit 6 | "DI76" logic inputs physical image
|  | Bit 7 | "DI77" logic inputs physical image
|  | Bit 8 | "DI78" logic inputs physical image
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ILC3 |  | Bit 0 | "DI80" logic inputs physical image
|  | Bit 1 | "DI81" logic inputs physical image
|  | Bit 2 | "DI82" logic inputs physical image
|  | Bit 3 | "DI83" logic inputs physical image
|  | Bit 4 | "DI84" logic inputs physical image
|  | Bit 5 | "DI85" logic inputs physical image
|  | Bit 6 | "DI86" logic inputs physical image
|  | Bit 7 | "DI87" logic inputs physical image
|  | Bit 8 | "DI88" logic inputs physical image
|  | Bit 9 | "DI89" logic inputs physical image
|  | Bit 10 | "DI90" logic inputs physical image
|  | Bit 11 | "DI91" logic inputs physical image
|  | Bit 12 | "DI92" logic inputs physical image
|  | Bit 13 | "DI93" logic inputs physical image
|  | Bit 14 | "DI94" logic inputs physical image
|  | Bit 15 | "DI95" logic inputs physical image
OLCI |  | Bit 0 | "R60" relay physical image
|  | Bit 1 | "R61" relay physical image
|  | Bit 2 | "R62" relay physical image
|  | Bit 3 | "R63" relay physical image
|  | Bit 4 | "R64" relay physical image
|  | Bit 5 | "R65" relay physical image
|  | Bit 6 | "R66" relay physical image
|  | Bit 7 | "R67" relay physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCR |  | Bit 0 | "R60" relay real image
|  | Bit 1 | "R61" relay real image
|  | Bit 2 | "R62" relay real image
|  | Bit 3 | "R63" relay real image
|  | Bit 4 | "R64" relay real image
|  | Bit 5 | "R65" relay real image
|  | Bit 6 | "R66" relay real image
|  | Bit 7 | "R67" relay real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLC2 |  | Bit 0 | "R70" relay physical image
|  | Bit 1 | "R71" relay physical image
|  | Bit 2 | "R72" relay physical image
|  | Bit 3 | "R73" relay physical image
|  | Bit 4 | "R74" relay physical image
|  | Bit 5 | "R75" relay physical image
|  | Bit 6 | "R76" relay physical image
|  | Bit 7 | "R77" relay physical image
|  | Bit 8 | "R80" relay physical image
|  | Bit 9 | "R81" relay physical image
|  | Bit 10 | "R82" relay physical image
|  | Bit 11 | "R83" relay physical image
|  | Bit 12 | "R84" relay physical image
|  | Bit 13 | "R85" relay physical image
|  | Bit 14 | "R86" relay physical image
|  | Bit 15 | "R87" relay physical image
OLCP |  | Bit 0 | "R60" relay physical image
|  | Bit 1 | "R61" relay physical image
|  | Bit 2 | "R62" relay physical image
|  | Bit 3 | "R63" relay physical image
|  | Bit 4 | "R64" relay physical image
|  | Bit 5 | "R65" relay physical image
|  | Bit 6 | "R66" relay physical image
|  | Bit 7 | "R67" relay physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC2 |  |  | On power-up, read CIC :
If CIC and CIC2 = 0 -> Ok
If CIC or CIC2 not 0 -> malfunction
Write FCS = "INI" to return to factory setting
Bit 0
Bit 1
Bit 2
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PCM1 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 15
PLO1 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BWS0 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BWS1 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BWS2 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BWS3 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BWC1 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BWC2 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
ERRQ |  | Bit 0
|  | Bit 1 | Reserved
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ERDS |  | Bit 0
Bit 1
Bit 2
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ERHS |  | Bit 0 | Reserved
Bit 1
|  | Bit 2 | Reserved
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
POEF |  | Bit 0
Bit 1
CMD6 |  |  | _Same as CMD
CMD7 |  |  | _Same as CMD
BWS4 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
OCT6 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
OCT7 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
OCT5 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
OCT2 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12: (0) Thermal cabinet T1 measurement from adaptation board : (1) Thermal cabinet T1 measurement from PLC Inside
Bit 13: (0) Thermal winding T1 measurement from adaptation board : (1) Thermal winding T1 measurement from PLC Inside
Bit 14: (0) Thermal cabinet T2 measurement from adaptation board : (1) Thermal cabinet T2 measurement from PLC Inside
Bit 15: (0) Thermal winding T2 measurement from adaptation board : (1) Thermal winding T2 measurement from PLC Inside
OCT3 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
OCT1 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
Bit 6
Bit 7
Bit 8
Bit 9
Bit 10
Bit 11
Bit 12
Bit 13
Bit 14
Bit 15
BYC3 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 5
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
BYC1 |  | Bit 0
Bit 1
Bit 2
Bit 3
Bit 4
Bit 4
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved