## Instructions
EAV64332 | 06/2018 | ATV600 - Communication Parameters
/!\ WARNING
UNEXPECTED MOVEMENT
Drive systems may perform unexpected movements because of incorrect wiring, incorrect settings, incorrect data or other errors. • Only appropriately trained persons who are familiar with and understand the contents of all pertinent product documentation and who have received safety training to recognize and avoid hazards involved are authorized to work on and with this drive system. Installation, adjustment, repair and maintenance must be performed by qualified personnel. • Carefully install the wiring in accordance with the EMC requirements. • Do not operate the product with unknown or unsuitable settings or data. • Perform a comprehensive commissioning test.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
/!\ WARNING
LOSS OF CONTROL
• The designer of any control scheme must consider the potential failure modes of control paths and, for critical control functions, provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop, overtravel stop, power outage and restart. • Separate or redundant control paths must be provided for critical control functions. • System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. • Observe all accident prevention regulations and local safety guidelines (1). • Each implementation of the product must be individually and thoroughly tested for proper operation before being placed into service.
Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only. Refer to programming manual and communication protocols manuals for full information.
This Excel file can be used to carry out searches (example: parameter address and format) and sort operations.
The columns include the following criteria:
Code:
Language-independent, this allows a rapid search in the programming manual, which includes an index of parameter codes.
Additional information can be found in the Communication Manuals (Modbus, CANopen....etc.....)
Name:
Parameter designation
Logic address:
Addresses for Modbus, Profibus, Profinet and Ethernet TCP
Address for the messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
CANopen index:
Addresses for CANopen, PowerLink and EtherCAT.
CANopen index/subindex in hexadecimal format, to be used for variable assignment of PDOs and SDO messaging.
DeviceNet path:
Address for DeviceNet and Ethernet IP.
Class/instance/attribute in decimal and hexadecimal (preceded by 16#) format.
When two paths are given, for example:
- 16#29/01/0D = 41/1/13 (messaging): ODVA standard path. It can be used for explicit messaging. Do not use it for configuring an assembly.
- 16#8C/01/07 = 140/1/7 (assembly): Altivar-specific path. This is the path that must be used for configuring an assembly. Avoid using it for explicit messaging, to ensure better interchangeability.
Link:
- For WORD (listing), a dynamic link opens its description. Listings are common to several parameters; only one part is valid for a given parameter. Refer to programming manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
- For WORD (bit register), in the Type column, a dynamic link opens its description.
Category:
Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access:
Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units:
Physical unit and multiplier.
Factory setting:
Value of the parameter set at the factory.
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Range:
Possible values.
Display:
Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu:
Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order:
Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu
CMI | Extended control word | 16#2138 = 8504 | 16#2037/5 | 16#8B/01/69 = 139/01/105 |  | Control parameters | R/W | WORD (BitString16) | -
CMD | Command register | 16#2135 = 8501 | 16#2037/2 | 16#8B/01/66 = 139/01/102 |  | Control parameters | R/W | WORD (BitString16) | - |  |  | [Cmd Register] (CMD) | [Communication map] (CMM)
RPR | Time counter reset | 16#0C30 = 3120 | 16#2001/15 | 16#70/01/79 = 112/01/121 | RPR | Control parameters | R/W | WORD (Enumeration) | - | [No] NO |  | [Time Counter Reset] (RPR) | [Counter Management] (ELT) [Maintenance] (CSMA)
LFRD | Speed setpoint | 16#219A = 8602 | 16#2038/3 | 16#8C/01/03 = 140/01/03 |  | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 rpm | -32767 rpm ... 32767 rpm
LFR | Reference frequency | 16#2136 = 8502 | 16#2037/3 | 16#8B/01/67 = 139/01/103 |  | Setpoint parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | -5000 ... 5000 | [Ref Frequency] (LFR) | [Drive parameters] (MPI)
PISP | PIDSet Point | 16#2137 = 8503 | 16#2037/4 | 16#8B/01/68 = 139/01/104 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 1000
AIV1 | AIV1 Image input | 16#14A1 = 5281 | 16#2016/52 | 16#7B/01/52 = 123/01/82 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -10000 ... 10000 | [AIV1 Image input] (AIV1) | [Drive parameters] (MPI)
MFR | Multiplying coefficient | 16#2E37 = 11831 | 16#2058/20 | 16#9C/01/20 = 156/01/32 |  | Setpoint parameters | R/W | UINT (Unsigned16) | 1 % |  | 0 % ... 100 % | [Multiplying coeff.] (MFR) | [Drive parameters] (MPI) [Settings] (SET)
ETA | CIA402 State Register | 16#0C81 = 3201 | 16#2002/2 | 16#71/01/02 = 113/01/02 |  | Status parameters | R | WORD (BitString16) | - |  |  | [CIA402 State Reg] (ETA) | [Communication map] (CMM)
HMIS | Drive state | 16#0CA8 = 3240 | 16#2002/29 | 16#71/01/29 = 113/01/41 | HMIS | Status parameters | R | WORD (Enumeration) | - |  |  | [Drive State] (HMIS) | [Pump Dashboard] (PMT) [Fan Dashboard] (FAN)
ETI | Internal State Register | 16#0C86 = 3206 | 16#2002/7 | 16#71/01/07 = 113/01/07 |  | Status parameters | R | WORD (BitString16) | -
CRC | Channel for reference frequency | 16#20F9 = 8441 | 16#2036/2A | 16#8B/01/2A = 139/01/42 |  | Status parameters | R | WORD (BitString16) | -
CCC | Active command channel | 16#20FA = 8442 | 16#2036/2B | 16#8B/01/2B = 139/01/43 |  | Status parameters | R | WORD (BitString16) | -
CNFS | Active configuration | 16#1F54 = 8020 | 16#2032/15 | 16#89/01/15 = 137/01/21 | CNFS | Status parameters | R | WORD (Enumeration) | - |  |  | [Config. active] (CNFS) | [Drive parameters] (MPI)
STUN | Tune selection | 16#2591 = 9617 | 16#2042/12 | 16#91/01/12 = 145/01/18 | STUN | Status parameters | R | WORD (Enumeration) | - | [Default] TAB |  | [Tune selection] (STUN) | [Simply start] (SIM) [Motor tune] (MTU)
SMOT | Status of motor tune in term of saliency | 16#25AD = 9645 | 16#2042/2E | 16#91/01/2E = 145/01/46 | SMOT | Status parameters | R | WORD (Enumeration) | - |  |  | [Saliency mot. state] (SMOT) | [Motor tune] (MTU)
RFRD | Output velocity | 16#219C = 8604 | 16#2038/5 | 16#8C/01/05 = 140/01/05 |  | Actual values parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
RFR | Motor frequency | 16#0C82 = 3202 | 16#2002/3 | 16#71/01/03 = 113/01/03 |  | Actual values parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor Frequency] (RFR) | [Drive parameters] (MPI)
OTR | Motor torque | 16#0C85 = 3205 | 16#2002/6 | 16#71/01/06 = 113/01/06 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor torque] (OTR) | [Motor parameters] (MMO)
LCR | Motor current | 16#0C84 = 3204 | 16#2002/5 | 16#71/01/05 = 113/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Current] (LCR) | [Pump Dashboard] (PMT) [Fan Dashboard] (FAN) [Motor parameters] (MMO)
UOP | Motor voltage | 16#0C88 = 3208 | 16#2002/9 | 16#71/01/09 = 113/01/09 |  | Actual values parameters | R | UINT (Unsigned16) | 1 V |  | 0 V ... 65535 V | [Motor voltage] (UOP) | [Motor parameters] (MMO)
OPR | Motor power | 16#0C8B = 3211 | 16#2002/C | 16#71/01/0C = 113/01/12 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 % | [Motor Power] (OPR) | [Motor parameters] (MMO)
FRHD | Speed reference before ramp | 16#219D = 8605 | 16#2038/6 | 16#8C/01/06 = 140/01/06 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FROD | Speed reference after ramp | 16#21C1 = 8641 | 16#2038/2A | 16#8C/01/2A = 140/01/42 |  | Reference parameters | R | INT (Signed16) | 1 rpm |  | -32767 rpm ... 32767 rpm
FRH | Reference frequency before ramp | 16#0C83 = 3203 | 16#2002/4 | 16#71/01/04 = 113/01/04 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -500.0 Hz ... 500.0 Hz | [Pre-Ramp Ref Freq] (FRH) | [Pump Dashboard] (PMT) [Fan Dashboard] (FAN) [Drive parameters] (MPI) [Communication map] (CMM)
FRO | Frequency reference after ramp | 16#233D = 9021 | 16#203C/16 | 16#8E/01/16 = 142/01/22 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
RPC | PID reference | 16#2ECE = 11982 | 16#2059/53 | 16#9C/01/B7 = 156/01/183 |  | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [PID reference] (RPC) | [Control] (CTR) [Control] (FTR) [Application Parameters] (APR) [PID display] (PIC)
RPF | PID feedback | 16#2ECD = 11981 | 16#2059/52 | 16#9C/01/B6 = 156/01/182 |  | Reference parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [PID feedback] (RPF) | [Control] (CTR) [Control] (FTR) [Application Parameters] (APR) [PID display] (PIC) [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB)
RPE | PID Error | 16#2ECC = 11980 | 16#2059/51 | 16#9C/01/B5 = 156/01/181 |  | Reference parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [PID Error] (RPE) | [PID display] (PIC)
RPO | PID Output | 16#2ECF = 11983 | 16#2059/54 | 16#9C/01/B8 = 156/01/184 |  | Reference parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [PID Output] (RPO) | [PID display] (PIC)
ULN | Mains voltage | 16#0C87 = 3207 | 16#2002/8 | 16#71/01/08 = 113/01/08 |  | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [Mains Voltage] (ULN) | [Drive parameters] (MPI)
THD | Drive thermal state | 16#0C89 = 3209 | 16#2002/A | 16#71/01/0A = 113/01/10 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Drive Therm State] (THD) | [Drive parameters] (MPI)
THR | Motor thermal state | 16#259E = 9630 | 16#2042/1F | 16#91/01/1F = 145/01/31 |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 % | [Motor Therm State] (THR) | [Pump Dashboard] (PMT) [Fan Dashboard] (FAN) [Motor parameters] (MMO)
RTH | Motor run time | 16#0CAC = 3244 | 16#2002/2D | 16#71/01/2D = 113/01/45 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
PTH | Power-on time | 16#0CAE = 3246 | 16#2002/2F | 16#71/01/2F = 113/01/47 |  | Measurement parameters | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
IL1R | Logic inputs states | 16#1452 = 5202 | 16#2016/3 | 16#7B/01/03 = 123/01/03 |  | I/O parameters | R | WORD (BitString16) | -
OL1R | Logic outputs states | 16#145C = 5212 | 16#2016/D | 16#7B/01/0D = 123/01/13 |  | I/O parameters | R/W | WORD (BitString16) | -
AI1C | Physical value AI1 | 16#147A = 5242 | 16#2016/2B | 16#7B/01/2B = 123/01/43 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI1R | Analog input 1 standardized value | 16#1470 = 5232 | 16#2016/21 | 16#7B/01/21 = 123/01/33 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2C | Physical value AI2 | 16#147B = 5243 | 16#2016/2C | 16#7B/01/2C = 123/01/44 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI2R | Analog input 2 standardized value | 16#1471 = 5233 | 16#2016/22 | 16#7B/01/22 = 123/01/34 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI3C | Physical value AI3 | 16#147C = 5244 | 16#2016/2D | 16#7B/01/2D = 123/01/45 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI3R | Analog input 3 standardized value | 16#1472 = 5234 | 16#2016/23 | 16#7B/01/23 = 123/01/35 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO1C | AQ1 physical value | 16#1497 = 5271 | 16#2016/48 | 16#7B/01/48 = 123/01/72 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AO1R | Analog output 1 standardized value | 16#148D = 5261 | 16#2016/3E | 16#7B/01/3E = 123/01/62 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
ERRD | CiA402 fault code | 16#219E = 8606 | 16#2038/7 | 16#8C/01/07 = 140/01/07 |  | Fault parameters | R | WORD (BitString16) | -
LFT | Last Error occurred | 16#1BD1 = 7121 | 16#2029/16 | 16#84/01/7A = 132/01/122 | LFT | Fault parameters | R | WORD (Enumeration) | - |  |  | [Last Error] (LFT) | [Diag. data] (DDT)
CIC | Incorrect configuration | 16#1BDA = 7130 | 16#2029/1F | 16#84/01/83 = 132/01/131 |  | Fault parameters | R/WS | WORD (BitString16) | -
CNF | Fieldbus module Communication interruption | 16#1BDC = 7132 | 16#2029/21 | 16#84/01/85 = 132/01/133 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Fieldbus Com Interrupt] (CNF) | [DEVICENET DIAG] (DVN) [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN) [POWERLINK DIAG] (PWL)
ILF1 | Internal communication interruption 1 | 16#1BDE = 7134 | 16#2029/23 | 16#84/01/87 = 132/01/135 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [InternCom Error1] (ILF1) | [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN) [POWERLINK DIAG] (PWL)
FNB | Fault counter | 16#1CE1 = 7393 | 16#202B/5E | 16#85/01/C2 = 133/01/194 |  | Fault parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DP0 | Fault code on last fault | 16#1C20 = 7200 | 16#202A/1 | 16#85/01/01 = 133/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
ULP0 | DC bus voltage | 16#1C66 = 7270 | 16#202A/47 | 16#85/01/47 = 133/01/71 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
LCP0 | Motor current | 16#1C48 = 7240 | 16#202A/29 | 16#85/01/29 = 133/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
RFP0 | Output frequency | 16#1C52 = 7250 | 16#202A/33 | 16#85/01/33 = 133/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
THP0 | Motor thermal state | 16#1C70 = 7280 | 16#202A/51 | 16#85/01/51 = 133/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 %
EP0 | State word | 16#1C2A = 7210 | 16#202A/B | 16#85/01/0B = 133/01/11 |  | History parameters | R | WORD (BitString16) | -
IP0 | ETI state word | 16#1C34 = 7220 | 16#202A/15 | 16#85/01/15 = 133/01/21 |  | History parameters | R | WORD (BitString16) | -
CMP0 | Cmd word | 16#1C3E = 7230 | 16#202A/1F | 16#85/01/1F = 133/01/31 |  | History parameters | R | WORD (BitString16) | -
DCC0 | Command channel | 16#FB2C = 64300 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
DRC0 | Channel for reference frequency | 16#FB36 = 64310 |  |  | CNL | History parameters | R | WORD (Enumeration) | -
CRP0 | Channels active on last fault | 16#1C7A = 7290 | 16#202A/5B | 16#85/01/5B = 133/01/91 |  | History parameters | R | WORD (BitString16) | -
RTP0 | Elapsed time | 16#1C5C = 7260 | 16#202A/3D | 16#85/01/3D = 133/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h
OTP0 | Motor torque | 16#1CA2 = 7330 | 16#202B/1F | 16#85/01/83 = 133/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
TDP0 | Drive thermal state | 16#1CAC = 7340 | 16#202B/29 | 16#85/01/8D = 133/01/141 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 %
TJP0 | IGBT junction temp | 16#1CB6 = 7350 | 16#202B/33 | 16#85/01/97 = 133/01/151 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C
SFP0 | Switching frequency | 16#1CC0 = 7360 | 16#202B/3D | 16#85/01/A1 = 133/01/161 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz
DP1 | Fault code on fault n-1 | 16#1C21 = 7201 | 16#202A/2 | 16#85/01/02 = 133/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
ULP1 | DC bus voltage | 16#1C67 = 7271 | 16#202A/48 | 16#85/01/48 = 133/01/72 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP1) | [None] (DP1)
LCP1 | Motor current | 16#1C49 = 7241 | 16#202A/2A | 16#85/01/2A = 133/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP1) | [None] (DP1)
RFP1 | Output frequency | 16#1C53 = 7251 | 16#202A/34 | 16#85/01/34 = 133/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP1) | [None] (DP1)
THP1 | Motor thermal state | 16#1C71 = 7281 | 16#202A/52 | 16#85/01/52 = 133/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP1) | [None] (DP1)
EP1 | Status of last error 1 | 16#1C2B = 7211 | 16#202A/C | 16#85/01/0C = 133/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP1) | [None] (DP1)
IP1 | ETI state word | 16#1C35 = 7221 | 16#202A/16 | 16#85/01/16 = 133/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP1) | [None] (DP1)
CMP1 | Cmd word | 16#1C3F = 7231 | 16#202A/20 | 16#85/01/20 = 133/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP1) | [None] (DP1)
DCC1 | Command channel | 16#FB2D = 64301 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC1) | [None] (DP1)
DRC1 | Channel for reference frequency | 16#FB37 = 64311 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC1) | [None] (DP1)
CRP1 | Active channels on fault n-1 | 16#1C7B = 7291 | 16#202A/5C | 16#85/01/5C = 133/01/92 |  | History parameters | R | WORD (BitString16) | -
RTP1 | Elapsed time | 16#1C5D = 7261 | 16#202A/3E | 16#85/01/3E = 133/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP1) | [None] (DP1)
OTP1 | Motor torque | 16#1CA3 = 7331 | 16#202B/20 | 16#85/01/84 = 133/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP1) | [None] (DP1)
TDP1 | Drive thermal state | 16#1CAD = 7341 | 16#202B/2A | 16#85/01/8E = 133/01/142 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP1) | [None] (DP1)
TJP1 | IGBT junction temp | 16#1CB7 = 7351 | 16#202B/34 | 16#85/01/98 = 133/01/152 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP1) | [None] (DP1)
SFP1 | Switching frequency | 16#1CC1 = 7361 | 16#202B/3E | 16#85/01/A2 = 133/01/162 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP1) | [None] (DP1)
DP2 | Fault code on fault n-2 | 16#1C22 = 7202 | 16#202A/3 | 16#85/01/03 = 133/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
ULP2 | DC bus voltage | 16#1C68 = 7272 | 16#202A/49 | 16#85/01/49 = 133/01/73 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP2) | [None] (DP2)
LCP2 | Motor current | 16#1C4A = 7242 | 16#202A/2B | 16#85/01/2B = 133/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP2) | [None] (DP2)
RFP2 | Output frequency | 16#1C54 = 7252 | 16#202A/35 | 16#85/01/35 = 133/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP2) | [None] (DP2)
THP2 | Motor thermal state | 16#1C72 = 7282 | 16#202A/53 | 16#85/01/53 = 133/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP2) | [None] (DP2)
EP2 | Status of last error 2 | 16#1C2C = 7212 | 16#202A/D | 16#85/01/0D = 133/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EP2) | [None] (DP2)
IP2 | ETI state word | 16#1C36 = 7222 | 16#202A/17 | 16#85/01/17 = 133/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP2) | [None] (DP2)
CMP2 | Cmd word | 16#1C40 = 7232 | 16#202A/21 | 16#85/01/21 = 133/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP2) | [None] (DP2)
DCC2 | Command channel | 16#FB2E = 64302 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC2) | [None] (DP2)
DRC2 | Channel for reference frequency | 16#FB38 = 64312 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC2) | [None] (DP2)
CRP2 | Active channels on fault n-2 | 16#1C7C = 7292 | 16#202A/5D | 16#85/01/5D = 133/01/93 |  | History parameters | R | WORD (BitString16) | -
RTP2 | Elapsed time | 16#1C5E = 7262 | 16#202A/3F | 16#85/01/3F = 133/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP2) | [None] (DP2)
OTP2 | Motor torque | 16#1CA4 = 7332 | 16#202B/21 | 16#85/01/85 = 133/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP2) | [None] (DP2)
TDP2 | Drive thermal state | 16#1CAE = 7342 | 16#202B/2B | 16#85/01/8F = 133/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP2) | [None] (DP2)
TJP2 | IGBT junction temp | 16#1CB8 = 7352 | 16#202B/35 | 16#85/01/99 = 133/01/153 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP2) | [None] (DP2)
SFP2 | Switching frequency | 16#1CC2 = 7362 | 16#202B/3F | 16#85/01/A3 = 133/01/163 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP2) | [None] (DP2)
DP3 | Fault code on fault n-3 | 16#1C23 = 7203 | 16#202A/4 | 16#85/01/04 = 133/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
ULP3 | DC bus voltage | 16#1C69 = 7273 | 16#202A/4A | 16#85/01/4A = 133/01/74 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP3) | [None] (DP3)
LCP3 | Motor current | 16#1C4B = 7243 | 16#202A/2C | 16#85/01/2C = 133/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP3) | [None] (DP3)
RFP3 | Output frequency | 16#1C55 = 7253 | 16#202A/36 | 16#85/01/36 = 133/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP3) | [None] (DP3)
THP3 | Motor thermal state | 16#1C73 = 7283 | 16#202A/54 | 16#85/01/54 = 133/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP3) | [None] (DP3)
EP3 | Status of last error 3 | 16#1C2D = 7213 | 16#202A/E | 16#85/01/0E = 133/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EP3) | [None] (DP3)
IP3 | ETI state word | 16#1C37 = 7223 | 16#202A/18 | 16#85/01/18 = 133/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP3) | [None] (DP3)
CMP3 | Cmd word | 16#1C41 = 7233 | 16#202A/22 | 16#85/01/22 = 133/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP3) | [None] (DP3)
DCC3 | Command channel | 16#FB2F = 64303 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC3) | [None] (DP3)
DRC3 | Channel for reference frequency | 16#FB39 = 64313 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC3) | [None] (DP3)
CRP3 | Active channels on fault n-3 | 16#1C7D = 7293 | 16#202A/5E | 16#85/01/5E = 133/01/94 |  | History parameters | R | WORD (BitString16) | -
RTP3 | Elapsed time | 16#1C5F = 7263 | 16#202A/40 | 16#85/01/40 = 133/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP3) | [None] (DP3)
OTP3 | Motor torque | 16#1CA5 = 7333 | 16#202B/22 | 16#85/01/86 = 133/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP3) | [None] (DP3)
TDP3 | Drive thermal state | 16#1CAF = 7343 | 16#202B/2C | 16#85/01/90 = 133/01/144 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP3) | [None] (DP3)
TJP3 | IGBT junction temp | 16#1CB9 = 7353 | 16#202B/36 | 16#85/01/9A = 133/01/154 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP3) | [None] (DP3)
SFP3 | Switching frequency | 16#1CC3 = 7363 | 16#202B/40 | 16#85/01/A4 = 133/01/164 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP3) | [None] (DP3)
DP4 | Fault code on fault n-4 | 16#1C24 = 7204 | 16#202A/5 | 16#85/01/05 = 133/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
ULP4 | DC bus voltage | 16#1C6A = 7274 | 16#202A/4B | 16#85/01/4B = 133/01/75 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP4) | [None] (DP4)
LCP4 | Motor current | 16#1C4C = 7244 | 16#202A/2D | 16#85/01/2D = 133/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP4) | [None] (DP4)
RFP4 | Output frequency | 16#1C56 = 7254 | 16#202A/37 | 16#85/01/37 = 133/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP4) | [None] (DP4)
THP4 | Motor thermal state | 16#1C74 = 7284 | 16#202A/55 | 16#85/01/55 = 133/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP4) | [None] (DP4)
EP4 | Status of last error 4 | 16#1C2E = 7214 | 16#202A/F | 16#85/01/0F = 133/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EP4) | [None] (DP4)
IP4 | ETI state word | 16#1C38 = 7224 | 16#202A/19 | 16#85/01/19 = 133/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP4) | [None] (DP4)
CMP4 | Cmd word | 16#1C42 = 7234 | 16#202A/23 | 16#85/01/23 = 133/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP4) | [None] (DP4)
DCC4 | Command channel | 16#FB30 = 64304 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC4) | [None] (DP4)
DRC4 | Channel for reference frequency | 16#FB3A = 64314 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC4) | [None] (DP4)
CRP4 | Active channels on fault n-4 | 16#1C7E = 7294 | 16#202A/5F | 16#85/01/5F = 133/01/95 |  | History parameters | R | WORD (BitString16) | -
RTP4 | Elapsed time | 16#1C60 = 7264 | 16#202A/41 | 16#85/01/41 = 133/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP4) | [None] (DP4)
OTP4 | Motor torque | 16#1CA6 = 7334 | 16#202B/23 | 16#85/01/87 = 133/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP4) | [None] (DP4)
TDP4 | Drive thermal state | 16#1CB0 = 7344 | 16#202B/2D | 16#85/01/91 = 133/01/145 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP4) | [None] (DP4)
TJP4 | IGBT junction temp | 16#1CBA = 7354 | 16#202B/37 | 16#85/01/9B = 133/01/155 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP4) | [None] (DP4)
SFP4 | Switching frequency | 16#1CC4 = 7364 | 16#202B/41 | 16#85/01/A5 = 133/01/165 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP4) | [None] (DP4)
DP5 | Fault code on fault n-5 | 16#1C25 = 7205 | 16#202A/6 | 16#85/01/06 = 133/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
ULP5 | DC bus voltage | 16#1C6B = 7275 | 16#202A/4C | 16#85/01/4C = 133/01/76 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP5) | [None] (DP5)
LCP5 | Motor current | 16#1C4D = 7245 | 16#202A/2E | 16#85/01/2E = 133/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP5) | [None] (DP5)
RFP5 | Output frequency | 16#1C57 = 7255 | 16#202A/38 | 16#85/01/38 = 133/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP5) | [None] (DP5)
THP5 | Motor thermal state | 16#1C75 = 7285 | 16#202A/56 | 16#85/01/56 = 133/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP5) | [None] (DP5)
EP5 | State word | 16#1C2F = 7215 | 16#202A/10 | 16#85/01/10 = 133/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP5) | [None] (DP5)
IP5 | ETI state word | 16#1C39 = 7225 | 16#202A/1A | 16#85/01/1A = 133/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP5) | [None] (DP5)
CMP5 | Cmd word | 16#1C43 = 7235 | 16#202A/24 | 16#85/01/24 = 133/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP5) | [None] (DP5)
DCC5 | Command channel | 16#FB31 = 64305 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC5) | [None] (DP5)
DRC5 | Channel for reference frequency | 16#FB3B = 64315 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC5) | [None] (DP5)
CRP5 | Active channels on fault n-5 | 16#1C7F = 7295 | 16#202A/60 | 16#85/01/60 = 133/01/96 |  | History parameters | R | WORD (BitString16) | -
RTP5 | Elapsed time | 16#1C61 = 7265 | 16#202A/42 | 16#85/01/42 = 133/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP5) | [None] (DP5)
OTP5 | Motor torque | 16#1CA7 = 7335 | 16#202B/24 | 16#85/01/88 = 133/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP5) | [None] (DP5)
TDP5 | Drive thermal state | 16#1CB1 = 7345 | 16#202B/2E | 16#85/01/92 = 133/01/146 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP5) | [None] (DP5)
TJP5 | IGBT junction temp | 16#1CBB = 7355 | 16#202B/38 | 16#85/01/9C = 133/01/156 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP5) | [None] (DP5)
SFP5 | Switching frequency | 16#1CC5 = 7365 | 16#202B/42 | 16#85/01/A6 = 133/01/166 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP5) | [None] (DP5)
DP6 | Fault code on fault n-6 | 16#1C26 = 7206 | 16#202A/7 | 16#85/01/07 = 133/01/07 | LFT | History parameters | R | WORD (Enumeration) | -
ULP6 | DC bus voltage | 16#1C6C = 7276 | 16#202A/4D | 16#85/01/4D = 133/01/77 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP6) | [None] (DP6)
LCP6 | Motor current | 16#1C4E = 7246 | 16#202A/2F | 16#85/01/2F = 133/01/47 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP6) | [None] (DP6)
RFP6 | Output frequency | 16#1C58 = 7256 | 16#202A/39 | 16#85/01/39 = 133/01/57 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP6) | [None] (DP6)
THP6 | Motor thermal state | 16#1C76 = 7286 | 16#202A/57 | 16#85/01/57 = 133/01/87 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP6) | [None] (DP6)
EP6 | State word | 16#1C30 = 7216 | 16#202A/11 | 16#85/01/11 = 133/01/17 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP6) | [None] (DP6)
IP6 | ETI state word | 16#1C3A = 7226 | 16#202A/1B | 16#85/01/1B = 133/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP6) | [None] (DP6)
CMP6 | Cmd word | 16#1C44 = 7236 | 16#202A/25 | 16#85/01/25 = 133/01/37 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP6) | [None] (DP6)
DCC6 | Command channel | 16#FB32 = 64306 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC6) | [None] (DP6)
DRC6 | Channel for reference frequency | 16#FB3C = 64316 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC6) | [None] (DP6)
CRP6 | Active channels on fault n-6 | 16#1C80 = 7296 | 16#202A/61 | 16#85/01/61 = 133/01/97 |  | History parameters | R | WORD (BitString16) | -
RTP6 | Elapsed time | 16#1C62 = 7266 | 16#202A/43 | 16#85/01/43 = 133/01/67 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP6) | [None] (DP6)
OTP6 | Motor torque | 16#1CA8 = 7336 | 16#202B/25 | 16#85/01/89 = 133/01/137 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP6) | [None] (DP6)
TDP6 | Drive thermal state | 16#1CB2 = 7346 | 16#202B/2F | 16#85/01/93 = 133/01/147 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP6) | [None] (DP6)
TJP6 | IGBT junction temp | 16#1CBC = 7356 | 16#202B/39 | 16#85/01/9D = 133/01/157 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP6) | [None] (DP6)
SFP6 | Switching frequency | 16#1CC6 = 7366 | 16#202B/43 | 16#85/01/A7 = 133/01/167 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP6) | [None] (DP6)
DP7 | Fault code on fault n-7 | 16#1C27 = 7207 | 16#202A/8 | 16#85/01/08 = 133/01/08 | LFT | History parameters | R | WORD (Enumeration) | -
ULP7 | DC bus voltage | 16#1C6D = 7277 | 16#202A/4E | 16#85/01/4E = 133/01/78 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP7) | [None] (DP7)
LCP7 | Motor current | 16#1C4F = 7247 | 16#202A/30 | 16#85/01/30 = 133/01/48 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP7) | [None] (DP7)
RFP7 | Output frequency | 16#1C59 = 7257 | 16#202A/3A | 16#85/01/3A = 133/01/58 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP7) | [None] (DP7)
THP7 | Motor thermal state | 16#1C77 = 7287 | 16#202A/58 | 16#85/01/58 = 133/01/88 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP7) | [None] (DP7)
EP7 | State word | 16#1C31 = 7217 | 16#202A/12 | 16#85/01/12 = 133/01/18 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP7) | [None] (DP7)
IP7 | ETI state word | 16#1C3B = 7227 | 16#202A/1C | 16#85/01/1C = 133/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP7) | [None] (DP7)
CMP7 | Cmd word | 16#1C45 = 7237 | 16#202A/26 | 16#85/01/26 = 133/01/38 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP7) | [None] (DP7)
DCC7 | Command channel | 16#FB33 = 64307 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC7) | [None] (DP7)
DRC7 | Channel for reference frequency | 16#FB3D = 64317 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC7) | [None] (DP7)
CRP7 | Active channels on fault n-7 | 16#1C81 = 7297 | 16#202A/62 | 16#85/01/62 = 133/01/98 |  | History parameters | R | WORD (BitString16) | -
RTP7 | Elapsed time | 16#1C63 = 7267 | 16#202A/44 | 16#85/01/44 = 133/01/68 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP7) | [None] (DP7)
OTP7 | Motor torque | 16#1CA9 = 7337 | 16#202B/26 | 16#85/01/8A = 133/01/138 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP7) | [None] (DP7)
TDP7 | Drive thermal state | 16#1CB3 = 7347 | 16#202B/30 | 16#85/01/94 = 133/01/148 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP7) | [None] (DP7)
TJP7 | IGBT junction temp | 16#1CBD = 7357 | 16#202B/3A | 16#85/01/9E = 133/01/158 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP7) | [None] (DP7)
SFP7 | Switching frequency | 16#1CC7 = 7367 | 16#202B/44 | 16#85/01/A8 = 133/01/168 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP7) | [None] (DP7)
DP8 | Fault code on fault n-8 | 16#1C28 = 7208 | 16#202A/9 | 16#85/01/09 = 133/01/09 | LFT | History parameters | R | WORD (Enumeration) | -
ULP8 | DC bus voltage | 16#1C6E = 7278 | 16#202A/4F | 16#85/01/4F = 133/01/79 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP8) | [None] (DP8)
LCP8 | Motor current | 16#1C50 = 7248 | 16#202A/31 | 16#85/01/31 = 133/01/49 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP8) | [None] (DP8)
RFP8 | Output frequency | 16#1C5A = 7258 | 16#202A/3B | 16#85/01/3B = 133/01/59 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Output frequency] (RFP8) | [None] (DP8)
THP8 | Motor thermal state | 16#1C78 = 7288 | 16#202A/59 | 16#85/01/59 = 133/01/89 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP8) | [None] (DP8)
EP8 | State word | 16#1C32 = 7218 | 16#202A/13 | 16#85/01/13 = 133/01/19 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EP8) | [None] (DP8)
IP8 | ETI state word | 16#1C3C = 7228 | 16#202A/1D | 16#85/01/1D = 133/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP8) | [None] (DP8)
CMP8 | Cmd word | 16#1C46 = 7238 | 16#202A/27 | 16#85/01/27 = 133/01/39 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP8) | [None] (DP8)
DCC8 | Command channel | 16#FB34 = 64308 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC8) | [None] (DP8)
DRC8 | Channel for reference frequency | 16#FB3E = 64318 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC8) | [None] (DP8)
CRP8 | Active channels on fault n-8 | 16#1C82 = 7298 | 16#202A/63 | 16#85/01/63 = 133/01/99 |  | History parameters | R | WORD (BitString16) | -
RTP8 | Elapsed time | 16#1C64 = 7268 | 16#202A/45 | 16#85/01/45 = 133/01/69 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Elapsed time] (RTP8) | [None] (DP8)
OTP8 | Motor torque | 16#1CAA = 7338 | 16#202B/27 | 16#85/01/8B = 133/01/139 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP8) | [None] (DP8)
TDP8 | Drive thermal state | 16#1CB4 = 7348 | 16#202B/31 | 16#85/01/95 = 133/01/149 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP8) | [None] (DP8)
TJP8 | IGBT junction temp | 16#1CBE = 7358 | 16#202B/3B | 16#85/01/9F = 133/01/159 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP8) | [None] (DP8)
SFP8 | Switching frequency | 16#1CC8 = 7368 | 16#202B/45 | 16#85/01/A9 = 133/01/169 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP8) | [None] (DP8)
NCV | Drive nominal rating | 16#0BC3 = 3011 | 16#2000/C | 16#70/01/0C = 112/01/12 | NCV | Identification parameters | R | WORD (Enumeration) | - | [Unknown rating] NO
VCAL | Drive mains voltage | 16#0BC4 = 3012 | 16#2000/D | 16#70/01/0D = 112/01/13 | VCAL | Identification parameters | R | WORD (Enumeration) | - | [Unkown voltage] NO
INV | Nominal Drive Current | 16#0BC9 = 3017 | 16#2000/12 | 16#70/01/12 = 112/01/18 |  | Identification parameters | R | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535
VDP | Drive software version | 16#0CE6 = 3302 | 16#2003/3 | 16#71/01/67 = 113/01/103 |  | Identification parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
PAN0 | Device name (char 1 and 2) | 16#0D0C = 3340 | 16#2003/29 | 16#71/01/8D = 113/01/141 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN1 | Device name (char 3 and 4) | 16#0D0D = 3341 | 16#2003/2A | 16#71/01/8E = 113/01/142 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN2 | Device name (char 5 and 6) | 16#0D0E = 3342 | 16#2003/2B | 16#71/01/8F = 113/01/143 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN3 | Device name (char 7 and 8) | 16#0D0F = 3343 | 16#2003/2C | 16#71/01/90 = 113/01/144 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN4 | Device name (char 9 and 10) | 16#0D10 = 3344 | 16#2003/2D | 16#71/01/91 = 113/01/145 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN5 | Device name (char 11 and 12) | 16#0D11 = 3345 | 16#2003/2E | 16#71/01/92 = 113/01/146 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN6 | Device name (char 13 and 14) | 16#0D12 = 3346 | 16#2003/2F | 16#71/01/93 = 113/01/147 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
PAN7 | Device name (char 15 and 16) | 16#0D13 = 3347 | 16#2003/30 | 16#71/01/94 = 113/01/148 |  | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NC1 | Com scan output 1 value | 16#31D9 = 12761 | 16#2061/3E | 16#A0/01/A2 = 160/01/162 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out1 val.] (NC1) | [Com scan output map] (OSA)
NC2 | Com scan output 2 value | 16#31DA = 12762 | 16#2061/3F | 16#A0/01/A3 = 160/01/163 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out2 val.] (NC2) | [Com scan output map] (OSA)
NC3 | Com scan output 3 value | 16#31DB = 12763 | 16#2061/40 | 16#A0/01/A4 = 160/01/164 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out3 val.] (NC3) | [Com scan output map] (OSA)
NC4 | Com scan output 4 value | 16#31DC = 12764 | 16#2061/41 | 16#A0/01/A5 = 160/01/165 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out4 val.] (NC4) | [Com scan output map] (OSA)
NC5 | Com scan output 5 value | 16#31DD = 12765 | 16#2061/42 | 16#A0/01/A6 = 160/01/166 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out5 val.] (NC5) | [Com scan output map] (OSA)
NC6 | Com scan output 6 value | 16#31DE = 12766 | 16#2061/43 | 16#A0/01/A7 = 160/01/167 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out6 val.] (NC6) | [Com scan output map] (OSA)
NC7 | Com scan output 7 value | 16#31DF = 12767 | 16#2061/44 | 16#A0/01/A8 = 160/01/168 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out7 val.] (NC7) | [Com scan output map] (OSA)
NC8 | Com scan output 8 value | 16#31E0 = 12768 | 16#2061/45 | 16#A0/01/A9 = 160/01/169 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan Out8 val.] (NC8) | [Com scan output map] (OSA)
NM1 | Com scan input 1 value | 16#31C5 = 12741 | 16#2061/2A | 16#A0/01/8E = 160/01/142 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In1 val.] (NM1) | [Com. scanner input map] (ISA)
NM2 | Com scan input 2 value | 16#31C6 = 12742 | 16#2061/2B | 16#A0/01/8F = 160/01/143 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In2 val.] (NM2) | [Com. scanner input map] (ISA)
NM3 | Com scan input 3 value | 16#31C7 = 12743 | 16#2061/2C | 16#A0/01/90 = 160/01/144 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In3 val.] (NM3) | [Com. scanner input map] (ISA)
NM4 | Com scan input 4 value | 16#31C8 = 12744 | 16#2061/2D | 16#A0/01/91 = 160/01/145 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In4 val.] (NM4) | [Com. scanner input map] (ISA)
NM5 | Com scan input 5 value | 16#31C9 = 12745 | 16#2061/2E | 16#A0/01/92 = 160/01/146 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In5 val.] (NM5) | [Com. scanner input map] (ISA)
NM6 | Com scan input 6 value | 16#31CA = 12746 | 16#2061/2F | 16#A0/01/93 = 160/01/147 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In6 val.] (NM6) | [Com. scanner input map] (ISA)
NM7 | Com scan input 7 value | 16#31CB = 12747 | 16#2061/30 | 16#A0/01/94 = 160/01/148 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In7 val.] (NM7) | [Com. scanner input map] (ISA)
NM8 | Com scan input 8 value | 16#31CC = 12748 | 16#2061/31 | 16#A0/01/95 = 160/01/149 |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Com Scan In8 val.] (NM8) | [Com. scanner input map] (ISA)
SMAL | Velocity min amount | 16#21A1 = 8609 | 16#2038/A | 16#8C/01/0A = 140/01/10 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 0 rpm ... 65535 rpm
SMIL | Velocity max amount | 16#219F = 8607 | 16#2038/8 | 16#8C/01/08 = 140/01/08 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 0 rpm ... 65535 rpm
SPAL | Acceleration delta speed | 16#21A3 = 8611 | 16#2038/C | 16#8C/01/0C = 140/01/12 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 1 rpm ... 4294967295 rpm
SPAT | Acceleration delta time | 16#21A5 = 8613 | 16#2038/E | 16#8C/01/0E = 140/01/14 |  | CiA 402 settings | R/W | UINT (Unsigned16) | 1 s |  | 0 s ... 65535 s
SPDL | Deceleration delta speed | 16#21A6 = 8614 | 16#2038/F | 16#8C/01/0F = 140/01/15 |  | CiA 402 settings | R/W | UINT (Unsigned32) | 1 rpm |  | 1 rpm ... 4294967295 rpm
SPFN | Setpoint factor numerator | 16#21C2 = 8642 | 16#2038/2B | 16#8C/01/2B = 140/01/43 |  | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767
SPFD | Setpoint factor denominator | 16#21C3 = 8643 | 16#2038/2C | 16#8C/01/2C = 140/01/44 |  | CiA 402 settings | R/WS | INT (Signed16) | 1 | 1 | -32768 ... 32767
DOTD | Type of SwitchOn Disable Stop | 16#21CC = 8652 | 16#2038/35 | 16#8C/01/35 = 140/01/53 | DOTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [SwitchOnDisable Stp] (DOTD) | [Stop configuration] (STT)
QSTD | Quick stop option code | 16#21CB = 8651 | 16#2038/34 | 16#8C/01/34 = 140/01/52 | QSTD | CiA 402 settings | R/WS | WORD (Enumeration) | - | [Fast stop then disable voltage] FST2
SCS | Save configuration | 16#1F41 = 8001 | 16#2032/2 | 16#89/01/02 = 137/01/02 | SCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FCS | Restore configuration | 16#1F42 = 8002 | 16#2032/3 | 16#89/01/03 = 137/01/03 | FCS | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO
FRY | Factory setting group | 16#0BCE = 3022 | 16#2000/17 | 16#70/01/17 = 112/01/23 |  | Configuration management | R/WS | WORD (BitString16) | - | BIT1
CHA1 | Parameter set sel 1 | 16#3266 = 12902 | 16#2063/3 | 16#A1/01/67 = 161/01/103 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [2 Parameter sets] (CHA1) | [Parameters switching] (MLP)
CHA2 | Parameter set sel 2 | 16#3267 = 12903 | 16#2063/4 | 16#A1/01/68 = 161/01/104 | PSLIN | Parameter set switching | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [3 Parameter sets] (CHA2) | [Parameters switching] (MLP)
CFPS | Used parameter set | 16#3264 = 12900 | 16#2063/1 | 16#A1/01/65 = 161/01/101 | CFPS | Parameter set switching | R | WORD (Enumeration) | - |  |  | [Used param. set] (CFPS) | [Drive parameters] (MPI)
VAL | Load parameter set command | 16#3265 = 12901 | 16#2063/2 | 16#A1/01/66 = 161/01/102 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 1
AD01 | Parameter set address 1 | 16#326F = 12911 | 16#2063/C | 16#A1/01/70 = 161/01/112 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD02 | Parameter set address 2 | 16#3270 = 12912 | 16#2063/D | 16#A1/01/71 = 161/01/113 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD03 | Parameter set address 3 | 16#3271 = 12913 | 16#2063/E | 16#A1/01/72 = 161/01/114 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD04 | Parameter set address 4 | 16#3272 = 12914 | 16#2063/F | 16#A1/01/73 = 161/01/115 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD05 | Parameter set address 5 | 16#3273 = 12915 | 16#2063/10 | 16#A1/01/74 = 161/01/116 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD06 | Parameter set address 6 | 16#3274 = 12916 | 16#2063/11 | 16#A1/01/75 = 161/01/117 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD07 | Parameter set address 7 | 16#3275 = 12917 | 16#2063/12 | 16#A1/01/76 = 161/01/118 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD08 | Parameter set address 8 | 16#3276 = 12918 | 16#2063/13 | 16#A1/01/77 = 161/01/119 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD09 | Parameter set address 9 | 16#3277 = 12919 | 16#2063/14 | 16#A1/01/78 = 161/01/120 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD10 | Parameter set address 10 | 16#3278 = 12920 | 16#2063/15 | 16#A1/01/79 = 161/01/121 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD11 | Parameter set address 11 | 16#3279 = 12921 | 16#2063/16 | 16#A1/01/7A = 161/01/122 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD12 | Parameter set address 12 | 16#327A = 12922 | 16#2063/17 | 16#A1/01/7B = 161/01/123 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD13 | Parameter set address 13 | 16#327B = 12923 | 16#2063/18 | 16#A1/01/7C = 161/01/124 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD14 | Parameter set address 14 | 16#327C = 12924 | 16#2063/19 | 16#A1/01/7D = 161/01/125 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
AD15 | Parameter set address 15 | 16#327D = 12925 | 16#2063/1A | 16#A1/01/7E = 161/01/126 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
S101 | Parameter set 1 value 1 | 16#3283 = 12931 | 16#2063/20 | 16#A1/01/84 = 161/01/132 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S101) | [Set 1] (PS1)
S102 | Parameter set 1 value 2 | 16#3284 = 12932 | 16#2063/21 | 16#A1/01/85 = 161/01/133 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S102) | [Set 1] (PS1)
S103 | Parameter set 1 value 3 | 16#3285 = 12933 | 16#2063/22 | 16#A1/01/86 = 161/01/134 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S103) | [Set 1] (PS1)
S104 | Parameter set 1 value 4 | 16#3286 = 12934 | 16#2063/23 | 16#A1/01/87 = 161/01/135 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S104) | [Set 1] (PS1)
S105 | Parameter set 1 value 5 | 16#3287 = 12935 | 16#2063/24 | 16#A1/01/88 = 161/01/136 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S105) | [Set 1] (PS1)
S106 | Parameter set 1 value 6 | 16#3288 = 12936 | 16#2063/25 | 16#A1/01/89 = 161/01/137 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S106) | [Set 1] (PS1)
S107 | Parameter set 1 value 7 | 16#3289 = 12937 | 16#2063/26 | 16#A1/01/8A = 161/01/138 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S107) | [Set 1] (PS1)
S108 | Parameter set 1 value 8 | 16#328A = 12938 | 16#2063/27 | 16#A1/01/8B = 161/01/139 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S108) | [Set 1] (PS1)
S109 | Parameter set 1 value 9 | 16#328B = 12939 | 16#2063/28 | 16#A1/01/8C = 161/01/140 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S109) | [Set 1] (PS1)
S110 | Parameter set 1 value 10 | 16#328C = 12940 | 16#2063/29 | 16#A1/01/8D = 161/01/141 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S110) | [Set 1] (PS1)
S111 | Parameter set 1 value 11 | 16#328D = 12941 | 16#2063/2A | 16#A1/01/8E = 161/01/142 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S111) | [Set 1] (PS1)
S112 | Parameter set 1 value 12 | 16#328E = 12942 | 16#2063/2B | 16#A1/01/8F = 161/01/143 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S112) | [Set 1] (PS1)
S113 | Parameter set 1 value 13 | 16#328F = 12943 | 16#2063/2C | 16#A1/01/90 = 161/01/144 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S113) | [Set 1] (PS1)
S114 | Parameter set 1 value 14 | 16#3290 = 12944 | 16#2063/2D | 16#A1/01/91 = 161/01/145 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S114) | [Set 1] (PS1)
S115 | Parameter set 1 value 15 | 16#3291 = 12945 | 16#2063/2E | 16#A1/01/92 = 161/01/146 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 1, value of parameter xx] (S115) | [Set 1] (PS1)
S201 | Parameter set 2 value 1 | 16#3297 = 12951 | 16#2063/34 | 16#A1/01/98 = 161/01/152 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S201) | [Set 2] (PS2)
S202 | Parameter set 2 value 2 | 16#3298 = 12952 | 16#2063/35 | 16#A1/01/99 = 161/01/153 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S202) | [Set 2] (PS2)
S203 | Parameter set 2 value 3 | 16#3299 = 12953 | 16#2063/36 | 16#A1/01/9A = 161/01/154 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S203) | [Set 2] (PS2)
S204 | Parameter set 2 value 4 | 16#329A = 12954 | 16#2063/37 | 16#A1/01/9B = 161/01/155 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S204) | [Set 2] (PS2)
S205 | Parameter set 2 value 5 | 16#329B = 12955 | 16#2063/38 | 16#A1/01/9C = 161/01/156 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S205) | [Set 2] (PS2)
S206 | Parameter set 2 value 6 | 16#329C = 12956 | 16#2063/39 | 16#A1/01/9D = 161/01/157 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S206) | [Set 2] (PS2)
S207 | Parameter set 2 value 7 | 16#329D = 12957 | 16#2063/3A | 16#A1/01/9E = 161/01/158 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S207) | [Set 2] (PS2)
S208 | Parameter set 2 value 8 | 16#329E = 12958 | 16#2063/3B | 16#A1/01/9F = 161/01/159 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S208) | [Set 2] (PS2)
S209 | Parameter set 2 value 9 | 16#329F = 12959 | 16#2063/3C | 16#A1/01/A0 = 161/01/160 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S209) | [Set 2] (PS2)
S210 | Parameter set 2 value 10 | 16#32A0 = 12960 | 16#2063/3D | 16#A1/01/A1 = 161/01/161 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S210) | [Set 2] (PS2)
S211 | Parameter set 2 value 11 | 16#32A1 = 12961 | 16#2063/3E | 16#A1/01/A2 = 161/01/162 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S211) | [Set 2] (PS2)
S212 | Parameter set 2 value 12 | 16#32A2 = 12962 | 16#2063/3F | 16#A1/01/A3 = 161/01/163 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S212) | [Set 2] (PS2)
S213 | Parameter set 2 value 13 | 16#32A3 = 12963 | 16#2063/40 | 16#A1/01/A4 = 161/01/164 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S213) | [Set 2] (PS2)
S214 | Parameter set 2 value 14 | 16#32A4 = 12964 | 16#2063/41 | 16#A1/01/A5 = 161/01/165 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S214) | [Set 2] (PS2)
S215 | Parameter set 2 value 15 | 16#32A5 = 12965 | 16#2063/42 | 16#A1/01/A6 = 161/01/166 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 2, value of parameter xx] (S215) | [Set 2] (PS2)
S301 | Parameter set 3 value 1 | 16#32AB = 12971 | 16#2063/48 | 16#A1/01/AC = 161/01/172 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S301) | [Set 3] (PS3)
S302 | Parameter set 3 value 2 | 16#32AC = 12972 | 16#2063/49 | 16#A1/01/AD = 161/01/173 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S302) | [Set 3] (PS3)
S303 | Parameter set 3 value 3 | 16#32AD = 12973 | 16#2063/4A | 16#A1/01/AE = 161/01/174 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S303) | [Set 3] (PS3)
S304 | Parameter set 3 value 4 | 16#32AE = 12974 | 16#2063/4B | 16#A1/01/AF = 161/01/175 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S304) | [Set 3] (PS3)
S305 | Parameter set 3 value 5 | 16#32AF = 12975 | 16#2063/4C | 16#A1/01/B0 = 161/01/176 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S305) | [Set 3] (PS3)
S306 | Parameter set 3 value 6 | 16#32B0 = 12976 | 16#2063/4D | 16#A1/01/B1 = 161/01/177 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S306) | [Set 3] (PS3)
S307 | Parameter set 3 value 7 | 16#32B1 = 12977 | 16#2063/4E | 16#A1/01/B2 = 161/01/178 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S307) | [Set 3] (PS3)
S308 | Parameter set 3 value 8 | 16#32B2 = 12978 | 16#2063/4F | 16#A1/01/B3 = 161/01/179 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S308) | [Set 3] (PS3)
S309 | Parameter set 3 value 9 | 16#32B3 = 12979 | 16#2063/50 | 16#A1/01/B4 = 161/01/180 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S309) | [Set 3] (PS3)
S310 | Parameter set 3 value 10 | 16#32B4 = 12980 | 16#2063/51 | 16#A1/01/B5 = 161/01/181 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S310) | [Set 3] (PS3)
S311 | Parameter set 3 value 11 | 16#32B5 = 12981 | 16#2063/52 | 16#A1/01/B6 = 161/01/182 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S311) | [Set 3] (PS3)
S312 | Parameter set 3 value 12 | 16#32B6 = 12982 | 16#2063/53 | 16#A1/01/B7 = 161/01/183 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S312) | [Set 3] (PS3)
S313 | Parameter set 3 value 13 | 16#32B7 = 12983 | 16#2063/54 | 16#A1/01/B8 = 161/01/184 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S313) | [Set 3] (PS3)
S314 | Parameter set 3 value 14 | 16#32B8 = 12984 | 16#2063/55 | 16#A1/01/B9 = 161/01/185 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S314) | [Set 3] (PS3)
S315 | Parameter set 3 value 15 | 16#32B9 = 12985 | 16#2063/56 | 16#A1/01/BA = 161/01/186 |  | Parameter set switching | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Parameter switching : Set 3, value of parameter xx] (S315) | [Set 3] (PS3)
LSP | Low Speed | 16#0C21 = 3105 | 16#2001/6 | 16#70/01/6A = 112/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Low Speed] (LSP) | [Simply start] (SIM) [Pump start stop] (PST) [Speed Limits] (SLM) [Settings] (SET)
HSP | High Speed | 16#0C20 = 3104 | 16#2001/5 | 16#70/01/69 = 112/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [High Speed] (HSP) | [Simply start] (SIM) [Pump start stop] (PST) [Speed Limits] (SLM) [Settings] (SET)
ITH | Motor Thermal Current | 16#2596 = 9622 | 16#2042/17 | 16#91/01/17 = 145/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Motor Th Current] (ITH) | [Simply start] (SIM) [Motor monitoring] (MOP) [Settings] (SET) [Motor thermal monit] (THT)
SPGU | Inertia factor | 16#259D = 9629 | 16#2042/1E | 16#91/01/1E = 145/01/30 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Inertia Factor] (SPGU) | [Motor control] (DRC) [Settings] (SET)
SPG | Speed proportional gain | 16#238F = 9103 | 16#203D/4 | 16#8E/01/68 = 142/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 40 % | 0 % ... 1000 % | [Speed prop. gain] (SPG) | [Spd Loop Optimization] (MCL) [Settings] (SET)
SIT | Speed time integral | 16#2390 = 9104 | 16#203D/5 | 16#8E/01/69 = 142/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 ms | Refer to programming manual | 1 ms ... 65535 ms | [Speed time integral] (SIT) | [Spd Loop Optimization] (MCL) [Settings] (SET)
SFC | K speed loop filter | 16#2391 = 9105 | 16#203D/6 | 16#8E/01/6A = 142/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 100 | [K speed loop filter] (SFC) | [Spd Loop Optimization] (MCL) [Settings] (SET)
JACO | Inertia Coefficient of the application | 16#2398 = 9112 | 16#203D/D | 16#8E/01/71 = 142/01/113 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | 1.00 | 0.10 ... 100.00 | [App. Inertia Coef.] (JACO) | [Spd Loop Optimization] (MCL)
SSL | Speed loop type | 16#2392 = 9106 | 16#203D/7 | 16#8E/01/6B = 142/01/107 | SSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Speed loop type] (SSL) | [Spd Loop Optimization] (MCL)
JEST | Estimated application inertia | 16#2393 = 9107 | 16#203D/8 | 16#8E/01/6C = 142/01/108 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Estim. app. inertia] (JEST) | [Spd Loop Optimization] (MCL)
JAPL | Application Inertia | 16#2394 = 9108 | 16#203D/9 | 16#8E/01/6D = 142/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Application Inertia] (JAPL) | [Spd Loop Optimization] (MCL)
JMUL | Inertia Multiplying Coefficient | 16#2395 = 9109 | 16#203D/A | 16#8E/01/6E = 142/01/110 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 g.m² |  | 0.0 g.m² ... 6553.5 g.m² | [Inertia Mult. Coef.] (JMUL) | [Spd Loop Optimization] (MCL)
FFP | Feed forward value | 16#2396 = 9110 | 16#203D/B | 16#8E/01/6F = 142/01/111 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 200 % | [Feed forward] (FFP) | [Spd Loop Optimization] (MCL)
FFV | Feed forward bandwidth | 16#2397 = 9111 | 16#203D/C | 16#8E/01/70 = 142/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 20 % ... 500 % | [FeedFwd Bandwidth] (FFV) | [Spd Loop Optimization] (MCL)
FFH | Filter time of the estimated speed | 16#239B = 9115 | 16#203D/10 | 16#8E/01/74 = 142/01/116 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | Refer to programming manual | 0.0 ms ... 100.0 ms | [Spd est. filter time] (FFH) | [Spd Loop Optimization] (MCL)
CRTF | Filter time of the current | 16#239C = 9116 | 16#203D/11 | 16#8E/01/75 = 142/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms | 0.0 ms | 0.0 ms ... 100.0 ms | [Current Filter Time] (CRTF) | [data] (MTD)
CTD | High current threshold | 16#2AF9 = 11001 | 16#2050/2 | 16#98/01/02 = 152/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [High Current Thd] (CTD) | [Threshold reached] (THRE) [Settings] (SET)
TTH | High torque threshold | 16#2B08 = 11016 | 16#2050/11 | 16#98/01/11 = 152/01/17 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 100 % | -300 % ... 300 % | [High torque thd.] (TTH) | [Threshold reached] (THRE) [Settings] (SET)
TTL | Low torque threshold | 16#2B07 = 11015 | 16#2050/10 | 16#98/01/10 = 152/01/16 |  | Configuration and settings | R/W | INT (Signed16) | 1 % | 50 % | -300 % ... 300 % | [Low torque thd.] (TTL) | [Threshold reached] (THRE) [Settings] (SET)
FTD | Motor frequency threshold | 16#2AFB = 11003 | 16#2050/4 | 16#98/01/04 = 152/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Motor Freq Thd] (FTD) | [Threshold reached] (THRE) [Settings] (SET)
F2D | Frequency threshold 2 | 16#2AFC = 11004 | 16#2050/5 | 16#98/01/05 = 152/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Freq. threshold 2] (F2D) | [Threshold reached] (THRE) [Settings] (SET)
JF2 | Skip frequency 2 | 16#2C26 = 11302 | 16#2053/3 | 16#99/01/67 = 153/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Skip Frequency 2] (JF2) | [Jump frequency] (JUF) [Jump frequency] (JUF) [Settings] (SET)
JPF | Skip frequency | 16#2C25 = 11301 | 16#2053/2 | 16#99/01/66 = 153/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Skip Frequency] (JPF) | [Jump frequency] (JUF) [Jump frequency] (JUF) [Settings] (SET)
JFH | Skip Freq. Hysteresis | 16#2C2F = 11311 | 16#2053/C | 16#99/01/70 = 153/01/112 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 0.1 Hz ... 10.0 Hz | [Skip Freq.Hysteresis] (JFH) | [Jump frequency] (JUF) [Jump frequency] (JUF) [Settings] (SET)
JF3 | 3rd Skip Frequency | 16#2C27 = 11303 | 16#2053/4 | 16#99/01/68 = 153/01/104 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [3rd Skip Frequency] (JF3) | [Jump frequency] (JUF) [Jump frequency] (JUF) [Settings] (SET)
BFR | Motor Standard | 16#0BC7 = 3015 | 16#2000/10 | 16#70/01/10 = 112/01/16 | BFR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Motor Standard] (BFR) | [Simply start] (SIM) [data] (MTD)
NPR | Nominal motor power | 16#258D = 9613 | 16#2042/E | 16#91/01/0E = 145/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nominal Motor Power] (NPR) | [Simply start] (SIM) [data] (MTD)
COS | Motor 1 Cosinus Phi | 16#2586 = 9606 | 16#2042/7 | 16#91/01/07 = 145/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 | Refer to programming manual | 0.50 ... 1.00 | [Motor 1 Cosinus Phi] (COS) | [Simply start] (SIM) [data] (MTD)
UNS | Nominal motor voltage | 16#2581 = 9601 | 16#2042/2 | 16#91/01/02 = 145/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 690 V | [Nom Motor Voltage] (UNS) | [Simply start] (SIM) [data] (MTD)
NCR | Nominal motor current | 16#2583 = 9603 | 16#2042/4 | 16#91/01/04 = 145/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Nom Motor Current] (NCR) | [Simply start] (SIM) [data] (MTD)
FRS | Nominal Motor Frequency | 16#2582 = 9602 | 16#2042/3 | 16#91/01/03 = 145/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 40.0 Hz ... 500.0 Hz | [Nominal Motor Freq] (FRS) | [Simply start] (SIM) [data] (MTD)
NSP | Nominal motor speed | 16#2584 = 9604 | 16#2042/5 | 16#91/01/05 = 145/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nominal Motor Speed] (NSP) | [Simply start] (SIM) [data] (MTD)
TFR | Max frequency | 16#0C1F = 3103 | 16#2001/4 | 16#70/01/68 = 112/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 500.0 Hz | [Max Frequency] (TFR) | [Simply start] (SIM)
TUN | Autotuning | 16#2588 = 9608 | 16#2042/9 | 16#91/01/09 = 145/01/09 | ACTION | Configuration and settings | R/W | WORD (Enumeration) | - | [No action] NO |  | [Autotuning] (TUN) | [Simply start] (SIM) [Motor tune] (MTU)
AUT | Automatic autotune | 16#258F = 9615 | 16#2042/10 | 16#91/01/10 = 145/01/16 | AUT | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Automatic autotune] (AUT) | [Motor tune] (MTU)
TUS | Autotuning status | 16#2589 = 9609 | 16#2042/A | 16#91/01/0A = 145/01/10 | ACT | Configuration and settings | R | WORD (Enumeration) | - | [Not done] TAB |  | [Autotuning Status] (TUS) | [Simply start] (SIM) [Motor tune] (MTU)
CTT | Motor control type | 16#2587 = 9607 | 16#2042/8 | 16#91/01/08 = 145/01/08 | CTT | Configuration and settings | R/WS | WORD (Enumeration) | - | [U/F VC Quadratic] UFQ |  | [Motor control type] (CTT) | [Motor parameters] (MPA)
U1 | Volt point 1 on 5pt V/F | 16#3073 = 12403 | 16#205E/4 | 16#9F/01/04 = 159/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U1] (U1) | [Motor control] (DRC)
F1 | Freq point 1on 5pt V/F | 16#3074 = 12404 | 16#205E/5 | 16#9F/01/05 = 159/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F1] (F1) | [Motor control] (DRC)
U2 | Volt point 2 on 5pt V/F | 16#3075 = 12405 | 16#205E/6 | 16#9F/01/06 = 159/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U2] (U2) | [Motor control] (DRC)
F2 | Freq point 2 on 5pt V/F | 16#3076 = 12406 | 16#205E/7 | 16#9F/01/07 = 159/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F2] (F2) | [Motor control] (DRC)
U3 | Volt point 3 on 5pt V/F | 16#3077 = 12407 | 16#205E/8 | 16#9F/01/08 = 159/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U3] (U3) | [Motor control] (DRC)
F3 | Freq point 3 on 5pt V/F | 16#3078 = 12408 | 16#205E/9 | 16#9F/01/09 = 159/01/09 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F3] (F3) | [Motor control] (DRC)
U4 | Volt point 4 on 5pt V/F | 16#3079 = 12409 | 16#205E/A | 16#9F/01/0A = 159/01/10 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U4] (U4) | [Motor control] (DRC)
F4 | Freq point 4 on 5pt V/F | 16#307A = 12410 | 16#205E/B | 16#9F/01/0B = 159/01/11 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F4] (F4) | [Motor control] (DRC)
U5 | Volt point 5 on 5pt V/F | 16#307B = 12411 | 16#205E/C | 16#9F/01/0C = 159/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | 0 V | 0 V ... 800 V | [U5] (U5) | [Motor control] (DRC)
F5 | Freq point 5 on 5pt V/F | 16#307C = 12412 | 16#205E/D | 16#9F/01/0D = 159/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [F5] (F5) | [Motor control] (DRC)
NCRS | Sync motor nominal current | 16#25C6 = 9670 | 16#2042/47 | 16#91/01/47 = 145/01/71 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Sync Nominal I ] (NCRS) | [data] (MTD)
NSPS | Nominal synchronous motor speed | 16#25C7 = 9671 | 16#2042/48 | 16#91/01/48 = 145/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 rpm | Refer to programming manual | 0 rpm ... 65535 rpm | [Nom SyncMotor Speed] (NSPS) | [data] (MTD)
PPNS | Pole pairs number (sync) | 16#25C8 = 9672 | 16#2042/49 | 16#91/01/49 = 145/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 50 | [Pole pairs] (PPNS) | [data] (MTD)
TQS | Nominal motor torque | 16#25D4 = 9684 | 16#2042/55 | 16#91/01/55 = 145/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 1 ... 65535 | [Nom Motor torque] (TQS) | [data] (MTD)
PHS | Sync. EMF constant | 16#25C9 = 9673 | 16#2042/4A | 16#91/01/4A = 145/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mV/rpm | 0.0 mV/rpm | 0.0 mV/rpm ... 6553.5 mV/rpm | [Syn. EMF constant] (PHS) | [data] (MTD)
LDS | Sync motor d inductance | 16#25CA = 9674 | 16#2042/4B | 16#91/01/4B = 145/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Autotune L d-axis] (LDS) | [data] (MTD)
LQS | Sync motor q inductance | 16#25CB = 9675 | 16#2042/4C | 16#91/01/4C = 145/01/76 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Autotune L q-axis] (LQS) | [data] (MTD)
RSAS | Calculated SyncMotor Stator R | 16#25D2 = 9682 | 16#2042/53 | 16#91/01/53 = 145/01/83 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [SyncMotor Stator R] (RSAS) | [data] (MTD)
UFR | IR compensation | 16#2597 = 9623 | 16#2042/18 | 16#91/01/18 = 145/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 200 % | [IR compensation] (UFR) | [Motor control] (DRC) [Settings] (SET)
SLP | Slip Compensation | 16#2599 = 9625 | 16#2042/1A | 16#91/01/1A = 145/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 300 % | [Slip compensation] (SLP) | [Motor control] (DRC) [Settings] (SET)
PPN | Number of pairs of poles calculated | 16#2592 = 9618 | 16#2042/13 | 16#91/01/13 = 145/01/19 |  | Configuration and settings | R | UINT (Unsigned16) | 1 | Refer to programming manual | 1 ... 100
FLG | Frequency loop gain | 16#2594 = 9620 | 16#2042/15 | 16#91/01/15 = 145/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [FreqLoopGain] (FLG) | [Spd Loop Optimization] (MCL)
STA | Frequency loop stability | 16#2595 = 9621 | 16#2042/16 | 16#91/01/16 = 145/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 20 % | 0 % ... 100 % | [FreqLoop Stab] (STA) | [Spd Loop Optimization] (MCL)
RSA | AsyncMotor Stator resistance | 16#25AA = 9642 | 16#2042/2B | 16#91/01/2B = 145/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [AsyncMotor R Stator] (RSA) | [data] (MTD)
IDA | Magnetizing Current | 16#25B4 = 9652 | 16#2042/35 | 16#91/01/35 = 145/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Magnetizing Current] (IDA) | [data] (MTD)
LFA | AsyncMotor Leakage inductance | 16#25BE = 9662 | 16#2042/3F | 16#91/01/3F = 145/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [AsyncMotor Lf Induct] (LFA) | [data] (MTD)
TRA | Rotor time constant | 16#25C3 = 9667 | 16#2042/44 | 16#91/01/44 = 145/01/68 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Rotor Time Const] (TRA) | [data] (MTD)
FRSS | Synchronous motor nominal freq | 16#25CF = 9679 | 16#2042/50 | 16#91/01/50 = 145/01/80 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10.0 Hz ... 500.0 Hz | [Sync Nominal Freq] (FRSS) | [data] (MTD)
SFR | Switching frequency | 16#0C1E = 3102 | 16#2001/3 | 16#70/01/67 = 112/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 kHz | Refer to programming manual | 1.0 kHz ... 16.0 kHz | [Switching frequency] (SFR) | [Switching frequency] (SWF) [Settings] (SET)
CLI | Current limitation | 16#23F1 = 9201 | 16#203E/2 | 16#8F/01/02 = 143/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Current Limitation] (CLI) | [Motor monitoring] (MOP) [Settings] (SET)
SFT | Switching frequency type | 16#0C1D = 3101 | 16#2001/2 | 16#70/01/66 = 112/01/102 | SFT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Switch.frequency type 1] HF1 |  | [Switch Freq Type] (SFT) | [Switching frequency] (SWF)
NRD | Motor Noise Reduction | 16#0C23 = 3107 | 16#2001/8 | 16#70/01/6C = 112/01/108 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Noise Reduction] (NRD) | [Switching frequency] (SWF)
BOA | Boost activation | 16#3656 = 13910 | 16#206D/B | 16#A6/01/6F = 166/01/111 | BOA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Boost activation] (BOA) | [Motor control] (DRC)
SVL | Motor surge limitation | 16#3139 = 12601 | 16#2060/2 | 16#A0/01/02 = 160/01/02 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Motor surge limit.] (SVL) | [Switching frequency] (SWF)
SOP | Attenuation time | 16#313A = 12602 | 16#2060/3 | 16#A0/01/03 = 160/01/03 | SOP | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Attenuation Time] (SOP) | [Motor monitoring] (MOP) [Switching frequency] (SWF)
FFM | Fan mode | 16#0C3A = 3130 | 16#2001/1F | 16#70/01/83 = 112/01/131 | FFM | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard] STD |  | [Fan mode] (FFM) | [Settings] (SET) [Fan management] (FAMA)
TCC | 2/3-wire control | 16#2B5D = 11101 | 16#2051/2 | 16#98/01/66 = 152/01/102 | TCC | Configuration and settings | R/WS | WORD (Enumeration) | - | [2-wire control] 2C |  | [2/3-Wire Control] (TCC) | [Simply start] (SIM) [Command and Reference] (CRP)
TCT | Type of 2-wire control | 16#2B5E = 11102 | 16#2051/3 | 16#98/01/67 = 152/01/103 | TCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Transition] TRN |  | [2-wire type] (TCT) | [Command and Reference] (CRP)
RRS | Reverse assignment | 16#2B61 = 11105 | 16#2051/6 | 16#98/01/6A = 152/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Reverse Assign] (RRS) | [Command and Reference] (CRP)
BSP | Reference frequency template selection | 16#0C22 = 3106 | 16#2001/7 | 16#70/01/6B = 112/01/107 | BSP | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard ref template] BSD |  | [Ref Freq template] (BSP) | [Pump start stop] (PST) [Speed Limits] (SLM) [Input/Output] (IO)
AI1T | Configuration of AI1 | 16#1132 = 4402 | 16#200E/3 | 16#77/01/03 = 119/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI1 Type] (AI1T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1 configuration] (AI1) [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
UIL1 | AI1 voltage scaling parameter of 0% | 16#113C = 4412 | 16#200E/D | 16#77/01/0D = 119/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI1 Min. Value] (UIL1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [AI1 configuration] (AI1) [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
UIH1 | AI1 voltage scaling parameter of 100% | 16#1146 = 4422 | 16#200E/17 | 16#77/01/17 = 119/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI1 Max Value] (UIH1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [AI1 configuration] (AI1) [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
AI1F | AI1 filter | 16#1164 = 4452 | 16#200E/35 | 16#77/01/35 = 119/01/53 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI1 filter] (AI1F) | [AI1] (AI1C) [AI1 configuration] (AI1)
AI1E | AI1 intermediate point X | 16#116E = 4462 | 16#200E/3F | 16#77/01/3F = 119/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point X] (AI1E) | [AI1 configuration] (AI1)
AI1S | AI1 intermediate point Y | 16#1178 = 4472 | 16#200E/49 | 16#77/01/49 = 119/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI1 Interm. point Y] (AI1S) | [AI1 configuration] (AI1)
AI2T | Configuration of AI2 | 16#1133 = 4403 | 16#200E/4 | 16#77/01/04 = 119/01/04 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Voltage] 10U |  | [AI2 Type] (AI2T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2 configuration] (AI2) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
UIL2 | AI2 voltage scaling parameter of 0% | 16#113D = 4413 | 16#200E/E | 16#77/01/0E = 119/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI2 Min. Value] (UIL2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [AI2 configuration] (AI2) [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
UIH2 | AI2 voltage scaling parameter of 100% | 16#1147 = 4423 | 16#200E/18 | 16#77/01/18 = 119/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI2 Max value] (UIH2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [AI2 configuration] (AI2) [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
AI2F | AI2 filter | 16#1165 = 4453 | 16#200E/36 | 16#77/01/36 = 119/01/54 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI2 filter] (AI2F) | [AI2] (AI2C) [AI2 configuration] (AI2)
AI2E | AI2 intermediate point X | 16#116F = 4463 | 16#200E/40 | 16#77/01/40 = 119/01/64 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point X] (AI2E) | [AI2 configuration] (AI2)
AI2S | AI2 intermediate point Y | 16#1179 = 4473 | 16#200E/4A | 16#77/01/4A = 119/01/74 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI2 Interm. point Y] (AI2S) | [AI2 configuration] (AI2)
AI3T | Configuration of AI3 | 16#1134 = 4404 | 16#200E/5 | 16#77/01/05 = 119/01/05 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI3 Type] (AI3T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3 configuration] (AI3) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
CRL3 | AI3 current scaling parameter of 0% | 16#1152 = 4434 | 16#200E/23 | 16#77/01/23 = 119/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI3 Min. Value] (CRL3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [AI3 configuration] (AI3) [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
CRH3 | AI3 current scaling parameter of 100% | 16#115C = 4444 | 16#200E/2D | 16#77/01/2D = 119/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI3 Max Value] (CRH3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [AI3 configuration] (AI3) [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
AI3F | AI3 filter | 16#1166 = 4454 | 16#200E/37 | 16#77/01/37 = 119/01/55 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI3 filter] (AI3F) | [AI3] (AI3C) [AI3 configuration] (AI3)
AI3E | AI3 intermediate point X | 16#1170 = 4464 | 16#200E/41 | 16#77/01/41 = 119/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 X Interm. point] (AI3E) | [AI3 configuration] (AI3)
AI3S | AI3 intermediate point Y | 16#117A = 4474 | 16#200E/4B | 16#77/01/4B = 119/01/75 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI3 Y Interm. point] (AI3S) | [AI3 configuration] (AI3)
AO1 | AQ1 assignment | 16#139D = 5021 | 16#2014/16 | 16#7A/01/16 = 122/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor frequency] OFR |  | [AQ1 assignment] (AO1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1T | AQ1 Type | 16#11F9 = 4601 | 16#2010/2 | 16#78/01/02 = 120/01/02 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AQ1 Type] (AO1T) | [AQ1 configuration] (AO1)
AOL1 | AQ1 min output value | 16#1221 = 4641 | 16#2010/2A | 16#78/01/2A = 120/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ1 min output] (AOL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AOH1 | AQ1 max output value | 16#122B = 4651 | 16#2010/34 | 16#78/01/34 = 120/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ1 max output] (AOH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
UOL1 | AQ1 minimum output | 16#120D = 4621 | 16#2010/16 | 16#78/01/16 = 120/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ1 min Output] (UOL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
UOH1 | AQ1 maximum output | 16#1217 = 4631 | 16#2010/20 | 16#78/01/20 = 120/01/32 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ1 max Output] (UOH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
ASL1 | Scaling AQ1 min | 16#1235 = 4661 | 16#2010/3E | 16#78/01/3E = 120/01/62 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 min] (ASL1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
ASH1 | Scaling AQ1 max | 16#123F = 4671 | 16#2010/48 | 16#78/01/48 = 120/01/72 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ1 max] (ASH1) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
AO1F | AQ1 filter | 16#1203 = 4611 | 16#2010/C | 16#78/01/0C = 120/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ1 Filter] (AO1F) | [AQ1] (AO1C) [AQ1 configuration] (AO1)
FR1 | Configuration reference frequency 1 | 16#20DD = 8413 | 16#2036/E | 16#8B/01/0E = 139/01/14 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 1 Config] (FR1) | [Command and Reference] (CRP) [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
RIN | Reverse direction disable | 16#0C24 = 3108 | 16#2001/9 | 16#70/01/6D = 112/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Reverse Disable] (RIN) | [Command and Reference] (CRP) [Reverse disable] (REIN)
PST | Stop key enable | 16#FA02 = 64002 |  |  | PST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Stop key priority] YES |  | [Stop Key Enable] (PST) | [Command and Reference] (CRP)
CHCF | Control mode configuration | 16#20D1 = 8401 | 16#2036/2 | 16#8B/01/02 = 139/01/02 | CHCF | Configuration and settings | R/WS | WORD (Enumeration) | - | [Combined channel mode] SIM |  | [Control Mode] (CHCF) | [Command and Reference] (CRP)
CCS | Command switching | 16#20E5 = 8421 | 16#2036/16 | 16#8B/01/16 = 139/01/22 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Command channel 1] CD1 |  | [Command Switching] (CCS) | [Command and Reference] (CRP)
CD1 | Command channel 1 assign | 16#20E7 = 8423 | 16#2036/18 | 16#8B/01/18 = 139/01/24 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Terminal block] TER |  | [Cmd channel 1] (CD1) | [Command and Reference] (CRP)
CD2 | Command channel 2 assign | 16#20E8 = 8424 | 16#2036/19 | 16#8B/01/19 = 139/01/25 | CDX | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus communication] MDB |  | [Cmd channel 2] (CD2) | [Command and Reference] (CRP)
RFC | Freq Switching Assignment | 16#20DB = 8411 | 16#2036/C | 16#8B/01/0C = 139/01/12 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Freq Switch Assign] (RFC) | [Command and Reference] (CRP)
FR2 | Configuration reference frequency 2 | 16#20DE = 8414 | 16#2036/F | 16#8B/01/0F = 139/01/15 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ref Freq 2 Config] (FR2) | [Command and Reference] (CRP)
COP | Copy Ch.1-Ch.2 | 16#20D2 = 8402 | 16#2036/3 | 16#8B/01/03 = 139/01/03 | COP | Configuration and settings | R/WS | WORD (Enumeration) | - | [No copy] NO |  | [Copy Ch1-Ch2] (COP) | [Command and Reference] (CRP)
FN1 | F1 key assignment | 16#34BD = 13501 | 16#2069/2 | 16#A4/01/66 = 164/01/102 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F1 key assignment] (FN1) | [Functions key mgnt] (FKG)
FN2 | F2 key assignment | 16#34BE = 13502 | 16#2069/3 | 16#A4/01/67 = 164/01/103 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F2 key assignment] (FN2) | [Functions key mgnt] (FKG)
FN3 | F3 key assignment | 16#34BF = 13503 | 16#2069/4 | 16#A4/01/68 = 164/01/104 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F3 key assignment] (FN3) | [Functions key mgnt] (FKG)
FN4 | F4 key assignment | 16#34C0 = 13504 | 16#2069/5 | 16#A4/01/69 = 164/01/105 | CSLFN | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [F4 key assignment] (FN4) | [Functions key mgnt] (FKG)
BMP | HMI command | 16#34D9 = 13529 | 16#2069/1E | 16#A4/01/82 = 164/01/130 | BMP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] DIS |  | [HMI cmd.] (BMP) | [Command and Reference] (CRP)
RCB | Select switching (1 to 1B) | 16#20DC = 8412 | 16#2036/D | 16#8B/01/0D = 139/01/13 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Reference frequency channel 1] FR1 |  | [Ref 1B switching] (RCB) | [Command and Reference] (CRP)
FR1B | Configuration ref. 1B | 16#20DF = 8415 | 16#2036/10 | 16#8B/01/10 = 139/01/16 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref.1B channel] (FR1B) | [Command and Reference] (CRP)
SA2 | Summing input 2 | 16#2E19 = 11801 | 16#2058/2 | 16#9C/01/02 = 156/01/02 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Summing Input 2] (SA2) | [Ref. operations] (OAI)
SA3 | Summing input 3 | 16#2E1A = 11802 | 16#2058/3 | 16#9C/01/03 = 156/01/03 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Summing Input 3] (SA3) | [Ref. operations] (OAI)
DA2 | Subtract reference frequency 2 | 16#2E23 = 11811 | 16#2058/C | 16#9C/01/0C = 156/01/12 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 2] (DA2) | [Ref. operations] (OAI)
DA3 | Subtract reference frequency 3 | 16#2E24 = 11812 | 16#2058/D | 16#9C/01/0D = 156/01/13 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Subtract Ref Freq 3] (DA3) | [Ref. operations] (OAI)
MA2 | Reference frequency 2 multiply | 16#2E2D = 11821 | 16#2058/16 | 16#9C/01/16 = 156/01/22 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 2 Multiply] (MA2) | [Ref. operations] (OAI)
MA3 | Reference frequency 3 multiply | 16#2E2E = 11822 | 16#2058/17 | 16#9C/01/17 = 156/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Ref Freq 3 Multiply] (MA3) | [Ref. operations] (OAI)
RPT | Type of Ramp | 16#232C = 9004 | 16#203C/5 | 16#8E/01/05 = 142/01/05 | RPT | Configuration and settings | R/W | WORD (Enumeration) | - | [Linear ramp] LIN |  | [Ramp Type] (RPT) | [Ramp] (RAMP)
INR | Ramp increment | 16#233C = 9020 | 16#203C/15 | 16#8E/01/15 = 142/01/21 | INR | Configuration and settings | R/W | WORD (Enumeration) | - | [Tenths of seconds] 01 |  | [Ramp increment] (INR) | [Ramp] (RAMP) [Settings] (SET)
ACC | Acceleration ramp time | 16#2329 = 9001 | 16#203C/2 | 16#8E/01/02 = 142/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 9999 | [Acceleration] (ACC) | [Simply start] (SIM) [Pump start stop] (PST) [Ramp] (RAMP) [Settings] (SET)
DEC | Deceleration ramp time | 16#232A = 9002 | 16#203C/3 | 16#8E/01/03 = 142/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 9999 | [Deceleration] (DEC) | [Simply start] (SIM) [Pump start stop] (PST) [Ramp] (RAMP) [Settings] (SET)
TA1 | Start ACC ramp rounding | 16#232D = 9005 | 16#203C/6 | 16#8E/01/06 = 142/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Acc round] (TA1) | [Ramp] (RAMP) [Settings] (SET)
TA2 | End ACC ramp rounding | 16#232E = 9006 | 16#203C/7 | 16#8E/01/07 = 142/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Acc round] (TA2) | [Ramp] (RAMP) [Settings] (SET)
TA3 | Start DEC ramp rounding | 16#232F = 9007 | 16#203C/8 | 16#8E/01/08 = 142/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [Begin Dec round] (TA3) | [Ramp] (RAMP) [Settings] (SET)
TA4 | End DEC ramp rounding | 16#2330 = 9008 | 16#203C/9 | 16#8E/01/09 = 142/01/09 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 10 % | 0 % ... 100 % | [End Dec round] (TA4) | [Ramp] (RAMP) [Settings] (SET)
FRT | Ramp 2 frequency threshold | 16#2333 = 9011 | 16#203C/C | 16#8E/01/0C = 142/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Ramp 2 Thd] (FRT) | [Ramp switching] (RPT)
RPS | Ramp switching Assignment | 16#2332 = 9010 | 16#203C/B | 16#8E/01/0B = 142/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Ramp Switch Assign] (RPS) | [Ramp switching] (RPT)
AC2 | Acceleration 2 ramp time | 16#2334 = 9012 | 16#203C/D | 16#8E/01/0D = 142/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Acceleration 2] (AC2) | [Ramp switching] (RPT) [Settings] (SET)
DE2 | Deceleration 2 | 16#2335 = 9013 | 16#203C/E | 16#8E/01/0E = 142/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Deceleration 2] (DE2) | [Ramp switching] (RPT) [Settings] (SET)
BRA | Decel ramp adaptation | 16#232B = 9003 | 16#203C/4 | 16#8E/01/04 = 142/01/04 | BRA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Dec.Ramp Adapt] (BRA) | [Ramp] (RAMP)
STT | Type of stop | 16#2BC1 = 11201 | 16#2052/2 | 16#99/01/02 = 153/01/02 | STT | Configuration and settings | R/WS | WORD (Enumeration) | - | [On ramp] RMP |  | [Type of stop] (STT) | [Stop configuration] (STT)
FFT | Freewheel stop threshold | 16#2BD4 = 11220 | 16#2052/15 | 16#99/01/15 = 153/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.2 Hz ... 500.0 Hz | [Freewheel stop Thd] (FFT) | [Stop configuration] (STT) [Settings] (SET)
NST | Freewheel stop | 16#2BC2 = 11202 | 16#2052/3 | 16#99/01/03 = 153/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Freewheel Stop] (NST) | [Stop configuration] (STT)
FST | Fast stop assignment | 16#2BC4 = 11204 | 16#2052/5 | 16#99/01/05 = 153/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Fast Stop Assign] (FST) | [Stop configuration] (STT)
DCF | Fast Stop Ramp Divider | 16#2BDE = 11230 | 16#2052/1F | 16#99/01/1F = 153/01/31 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 4 | 0 ... 10 | [Ramp Divider] (DCF) | [Stop configuration] (STT) [Settings] (SET)
DCI | DC Injection Assignment | 16#2BC3 = 11203 | 16#2052/4 | 16#99/01/04 = 153/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DC Injection Assign] (DCI) | [Stop configuration] (STT)
IDC | DC injection level 1 | 16#2BCA = 11210 | 16#2052/B | 16#99/01/0B = 153/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [DC Inj Level 1] (IDC) | [Stop configuration] (STT) [Settings] (SET)
TDI | DC injection time 1 | 16#2BCD = 11213 | 16#2052/E | 16#99/01/0E = 153/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 1] (TDI) | [Stop configuration] (STT) [Settings] (SET)
IDC2 | DC injection level 2 | 16#2BCC = 11212 | 16#2052/D | 16#99/01/0D = 153/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [DC Inj Level 2] (IDC2) | [Stop configuration] (STT) [Settings] (SET)
TDC | DC injection time 2 | 16#2BCB = 11211 | 16#2052/C | 16#99/01/0C = 153/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [DC Inj Time 2] (TDC) | [Stop configuration] (STT) [Settings] (SET)
ADC | Automatic DC Injection | 16#28A1 = 10401 | 16#204A/2 | 16#95/01/02 = 149/01/02 | ADC | Configuration and settings | R/W | WORD (Enumeration) | - | [No DC injection] NO |  | [Auto DC Injection] (ADC) | [Auto DC injection] (ADC)
SDC1 | Auto DC injection level 1 | 16#28A3 = 10403 | 16#204A/4 | 16#95/01/04 = 149/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Auto DC inj Level 1] (SDC1) | [Auto DC injection] (ADC) [Settings] (SET)
TDC1 | Auto DC injection time 1 | 16#28A2 = 10402 | 16#204A/3 | 16#95/01/03 = 149/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 30.0 s | [Auto DC Inj Time 1] (TDC1) | [Auto DC injection] (ADC) [Settings] (SET)
SDC2 | Auto DC injection level 2 | 16#28A5 = 10405 | 16#204A/6 | 16#95/01/06 = 149/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | Refer to programming manual | 0 ... 65535 | [Auto DC inj Level 2] (SDC2) | [Auto DC injection] (ADC) [Settings] (SET)
TDC2 | Auto DC injection time 2 | 16#28A4 = 10404 | 16#204A/5 | 16#95/01/05 = 149/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 30.0 s | [Auto DC Inj Time 2] (TDC2) | [Auto DC injection] (ADC) [Settings] (SET)
PS2 | 2 Preset Freq assignment | 16#2C89 = 11401 | 16#2054/2 | 16#9A/01/02 = 154/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 Preset Freq] (PS2) | [Preset speeds] (PSS)
PS4 | 4 Preset Freq assignment | 16#2C8A = 11402 | 16#2054/3 | 16#9A/01/03 = 154/01/03 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 Preset Freq] (PS4) | [Preset speeds] (PSS)
PS8 | 8 Preset Freq assignment | 16#2C8B = 11403 | 16#2054/4 | 16#9A/01/04 = 154/01/04 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [8 Preset Freq] (PS8) | [Preset speeds] (PSS)
PS16 | 16 Preset Freq assignment | 16#2C8C = 11404 | 16#2054/5 | 16#9A/01/05 = 154/01/05 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [16 Preset Freq] (PS16) | [Preset speeds] (PSS)
SP2 | Preset speed 2 | 16#2C92 = 11410 | 16#2054/B | 16#9A/01/0B = 154/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 10.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 2] (SP2) | [Preset speeds] (PSS) [Settings] (SET)
SP3 | Preset speed 3 | 16#2C93 = 11411 | 16#2054/C | 16#9A/01/0C = 154/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 15.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 3] (SP3) | [Preset speeds] (PSS) [Settings] (SET)
SP4 | Preset speed 4 | 16#2C94 = 11412 | 16#2054/D | 16#9A/01/0D = 154/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 20.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 4] (SP4) | [Preset speeds] (PSS) [Settings] (SET)
SP5 | Preset speed 5 | 16#2C95 = 11413 | 16#2054/E | 16#9A/01/0E = 154/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 5] (SP5) | [Preset speeds] (PSS) [Settings] (SET)
SP6 | Preset speed 6 | 16#2C96 = 11414 | 16#2054/F | 16#9A/01/0F = 154/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 30.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 6] (SP6) | [Preset speeds] (PSS) [Settings] (SET)
SP7 | Preset speed 7 | 16#2C97 = 11415 | 16#2054/10 | 16#9A/01/10 = 154/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 7] (SP7) | [Preset speeds] (PSS) [Settings] (SET)
SP8 | Preset speed 8 | 16#2C98 = 11416 | 16#2054/11 | 16#9A/01/11 = 154/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 40.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 8] (SP8) | [Preset speeds] (PSS) [Settings] (SET)
SP9 | Preset speed 9 | 16#2C99 = 11417 | 16#2054/12 | 16#9A/01/12 = 154/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 45.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 9] (SP9) | [Preset speeds] (PSS) [Settings] (SET)
SP10 | Preset speed 10 | 16#2C9A = 11418 | 16#2054/13 | 16#9A/01/13 = 154/01/19 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 50.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 10] (SP10) | [Preset speeds] (PSS) [Settings] (SET)
SP11 | Preset speed 11 | 16#2C9B = 11419 | 16#2054/14 | 16#9A/01/14 = 154/01/20 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 55.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 11] (SP11) | [Preset speeds] (PSS) [Settings] (SET)
SP12 | Preset speed 12 | 16#2C9C = 11420 | 16#2054/15 | 16#9A/01/15 = 154/01/21 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 12] (SP12) | [Preset speeds] (PSS) [Settings] (SET)
SP13 | Preset speed 13 | 16#2C9D = 11421 | 16#2054/16 | 16#9A/01/16 = 154/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 70.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 13] (SP13) | [Preset speeds] (PSS) [Settings] (SET)
SP14 | Preset speed 14 | 16#2C9E = 11422 | 16#2054/17 | 16#9A/01/17 = 154/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 80.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 14] (SP14) | [Preset speeds] (PSS) [Settings] (SET)
SP15 | Preset speed 15 | 16#2C9F = 11423 | 16#2054/18 | 16#9A/01/18 = 154/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 90.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 15] (SP15) | [Preset speeds] (PSS) [Settings] (SET)
SP16 | Preset speed 16 | 16#2CA0 = 11424 | 16#2054/19 | 16#9A/01/19 = 154/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 100.0 Hz | 0.0 Hz ... 500.0 Hz | [Preset speed 16] (SP16) | [Preset speeds] (PSS) [Settings] (SET)
USP | + speed assignment | 16#2CED = 11501 | 16#2055/2 | 16#9A/01/66 = 154/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [+ Speed Assign] (USP) | [+/- speed] (UPD)
DSP | - speed assignment | 16#2CEE = 11502 | 16#2055/3 | 16#9A/01/67 = 154/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [- Speed Assign] (DSP) | [+/- speed] (UPD)
STR | Reference frequency save | 16#2CEF = 11503 | 16#2055/4 | 16#9A/01/68 = 154/01/104 | STR | Configuration and settings | R/WS | WORD (Enumeration) | - | [No save] NO |  | [Ref Frequency Save] (STR) | [+/- speed] (UPD)
AST | Auto angle setting type | 16#3665 = 13925 | 16#206D/1A | 16#A6/01/7E = 166/01/126 | AST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pulse Signal Injection - Optimized] PSIO |  | [Angle setting type] (AST) | [data] (MTD) [Motor tune] (MTU)
MCR | Maximum current of PSI alignment | 16#3CF7 = 15607 | 16#207E/8 | 16#AF/01/08 = 175/01/08 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [PSI Align Curr Max] (MCR) | [data] (MTD) [Motor tune] (MTU)
PIF | PID controller feedback | 16#2E7D = 11901 | 16#2059/2 | 16#9C/01/66 = 156/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID feedback Assign] (PIF) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB)
PIF1 | Minimum PID feedback | 16#2E80 = 11904 | 16#2059/5 | 16#9C/01/69 = 156/01/105 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 32767 | [Min PID feedback] (PIF1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB)
PIF2 | Maximum PID feedback | 16#2E81 = 11905 | 16#2059/6 | 16#9C/01/6A = 156/01/106 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 1000 | 0 ... 32767 | [Max PID feedback] (PIF2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB)
PIP1 | Minimum PID process | 16#2E82 = 11906 | 16#2059/7 | 16#9C/01/6B = 156/01/107 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 150 | 0 ... 32767 | [Min PID Process] (PIP1) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
PIP2 | Maximum PID process | 16#2E83 = 11907 | 16#2059/8 | 16#9C/01/6C = 156/01/108 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 900 | 0 ... 32767 | [Max PID Process] (PIP2) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
PII | Internal PID reference | 16#2E84 = 11908 | 16#2059/9 | 16#9C/01/6D = 156/01/109 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Intern PID Ref] (PII) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
RPI | Internal PID reference | 16#2E90 = 11920 | 16#2059/15 | 16#9C/01/79 = 156/01/121 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 150 | 0 ... 32767 | [Internal PID ref] (RPI) | [PID display] (PIC) [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
RPG | PID Proportional gain | 16#2EA5 = 11941 | 16#2059/2A | 16#9C/01/8E = 156/01/142 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Prop.Gain] (RPG) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
RIG | PID controller integral gain | 16#2EA6 = 11942 | 16#2059/2B | 16#9C/01/8F = 156/01/143 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 1.00 | 0.01 ... 100.00 | [PID Intgl.Gain] (RIG) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
RDG | PID derivative gain | 16#2EA7 = 11943 | 16#2059/2C | 16#9C/01/90 = 156/01/144 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 | 0.00 | 0.00 ... 100.00 | [PID derivative gain] (RDG) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
PRP | PID ramp | 16#2ED0 = 11984 | 16#2059/55 | 16#9C/01/B9 = 156/01/185 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [PID ramp] (PRP) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
PIC | PID inversion | 16#2EA4 = 11940 | 16#2059/29 | 16#9C/01/8D = 156/01/141 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Inversion] (PIC) | [Settings] (ST) [Settings] (ST) [Settings] (ST)
POL | PID controller min. output | 16#2EB0 = 11952 | 16#2059/35 | 16#9C/01/99 = 156/01/153 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | -500.0 Hz ... 500.0 Hz | [PID Min Output] (POL) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
POH | PID controller max. output | 16#2EB1 = 11953 | 16#2059/36 | 16#9C/01/9A = 156/01/154 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 60.0 Hz | 0.0 Hz ... 500.0 Hz | [PID Max Output] (POH) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
PAL | Minimum feedback level Warning | 16#2EB9 = 11961 | 16#2059/3E | 16#9C/01/A2 = 156/01/162 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 65535 | [Min fbk Warning] (PAL) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [Settings] (SET)
PAH | Maximum feedback level Warning | 16#2EBA = 11962 | 16#2059/3F | 16#9C/01/A3 = 156/01/163 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 1000 | 0 ... 65535 | [Max fbk Warning] (PAH) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [Settings] (SET)
PER | PID error Warning | 16#2EBB = 11963 | 16#2059/40 | 16#9C/01/A4 = 156/01/164 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 100 | 0 ... 65535 | [PID error Warning] (PER) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
PIS | PID integral disabled | 16#2EA8 = 11944 | 16#2059/2D | 16#9C/01/91 = 156/01/145 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [PID Integral OFF] (PIS) | [Settings] (ST) [Settings] (ST) [Settings] (ST)
FPI | Predictive speed reference | 16#2EAE = 11950 | 16#2059/33 | 16#9C/01/97 = 156/01/151 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Predictive Speed Ref] (FPI) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
PSR | PID speed input % ref | 16#2EAF = 11951 | 16#2059/34 | 16#9C/01/98 = 156/01/152 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 1 % ... 100 % | [Speed input %] (PSR) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF) [Settings] (SET)
PAU | Auto/Manual select input | 16#2EC2 = 11970 | 16#2059/47 | 16#9C/01/AB = 156/01/171 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Auto/Manual assign.] (PAU) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
PIM | Manual PID reference | 16#2EB2 = 11954 | 16#2059/37 | 16#9C/01/9B = 156/01/155 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Manual PID reference] (PIM) | [PID Reference] (RF) [PID Reference] (RF) [PID Reference] (RF)
TLS | Low speed timeout | 16#2DB5 = 11701 | 16#2057/2 | 16#9B/01/66 = 155/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Low Speed Timeout] (TLS) | [Settings] (SET) [Stop after speed timeout] (PRSP)
PR2 | 2 PID Preset assignment | 16#2E85 = 11909 | 16#2059/A | 16#9C/01/6E = 156/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [2 PID Preset Assign] (PR2) | [PID preset references] (PRI) [PID preset references] (PRI) [PID preset references] (PRI)
PR4 | 4 PID Preset assignment | 16#2E86 = 11910 | 16#2059/B | 16#9C/01/6F = 156/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [4 PID Preset Assign] (PR4) | [PID preset references] (PRI) [PID preset references] (PRI) [PID preset references] (PRI)
RP2 | 2nd PID preset reference | 16#2E91 = 11921 | 16#2059/16 | 16#9C/01/7A = 156/01/122 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 300 | 0 ... 32767 | [Ref PID Preset 2] (RP2) | [Settings] (SET) [PID preset references] (PRI) [PID preset references] (PRI) [PID preset references] (PRI)
RP3 | 3rd PID preset reference | 16#2E92 = 11922 | 16#2059/17 | 16#9C/01/7B = 156/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 600 | 0 ... 32767 | [Ref PID Preset 3] (RP3) | [Settings] (SET) [PID preset references] (PRI) [PID preset references] (PRI) [PID preset references] (PRI)
RP4 | 4th PID preset reference | 16#2E93 = 11923 | 16#2059/18 | 16#9C/01/7C = 156/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 900 | 0 ... 32767 | [Ref PID Preset 4] (RP4) | [PID preset references] (PRI) [PID preset references] (PRI) [PID preset references] (PRI) [Settings] (SET)
TLA | Torque limit. activation | 16#23FA = 9210 | 16#203E/B | 16#8F/01/0B = 143/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque limit activ.] (TLA) | [Torque limitation] (TOL)
LLC | Mains contactor control | 16#3522 = 13602 | 16#206A/3 | 16#A5/01/03 = 165/01/03 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Mains Contactor] (LLC) | [Mains contactor command] (LLC)
LES | Drive lock assignment | 16#3521 = 13601 | 16#206A/2 | 16#A5/01/02 = 165/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Drive Lock ] (LES) | [Mains contactor command] (LLC) [Circuit breaker] (CCBK)
LCT | Time-out after cont. activ. | 16#3523 = 13603 | 16#206A/4 | 16#A5/01/04 = 165/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 5 s | 1 s ... 999 s | [Mains V. time out ] (LCT) | [Mains contactor command] (LLC) [Circuit breaker] (CCBK)
TUL | Autotuning input assignment | 16#258A = 9610 | 16#2042/B | 16#91/01/0B = 145/01/11 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Autotuning Assign] (TUL) | [Motor tune] (MTU)
RSF | Fault reset input assignment | 16#1BD4 = 7124 | 16#2029/19 | 16#84/01/7D = 132/01/125 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Fault Reset Assign] (RSF) | [Fault reset] (RST)
RP | Product restart | 16#1BD8 = 7128 | 16#2029/1D | 16#84/01/81 = 132/01/129 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Product restart] (RP) | [Fault reset] (RST)
RPA | Product restart assignment | 16#1BD9 = 7129 | 16#2029/1E | 16#84/01/82 = 132/01/130 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Prod Restart Assign] (RPA) | [Fault reset] (RST)
ATR | Automatic Fault reset | 16#1BD2 = 7122 | 16#2029/17 | 16#84/01/7B = 132/01/123 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Auto Fault Reset] (ATR) | [Fan] (CSFA) [Auto Fault Reset] (ATR)
TAR | Fault Reset Time | 16#1BD3 = 7123 | 16#2029/18 | 16#84/01/7C = 132/01/124 | DUR | Configuration and settings | R/WS | WORD (Enumeration) | - | [5 minutes] 5 |  | [Fault Reset Time] (TAR) | [Auto Fault Reset] (ATR)
FLR | Catch on fly | 16#0C26 = 3110 | 16#2001/B | 16#70/01/6F = 112/01/111 | FLR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Catch On Fly] (FLR) | [Fan] (CSFA) [Catch on the fly] (FLR)
THT | Motor thermal monitoring mode | 16#258C = 9612 | 16#2042/D | 16#91/01/0D = 145/01/13 | THT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Self cooled motor] ACL |  | [Motor Thermal Mode] (THT) | [Motor monitoring] (MOP) [Motor thermal monit] (THT)
TTD | Motor thermal threshold | 16#2AFA = 11002 | 16#2050/3 | 16#98/01/03 = 152/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Motor Therm Thd] (TTD) | [Motor monitoring] (MOP) [Threshold reached] (THRE) [Settings] (SET)
OLL | Motor overtemp error response | 16#1B61 = 7009 | 16#2028/A | 16#84/01/0A = 132/01/10 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorTemp ErrorResp] (OLL) | [Motor monitoring] (MOP)
OPL | Output Phase Loss assignment | 16#258B = 9611 | 16#2042/C | 16#91/01/0C = 145/01/12 | OPL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [OutPhaseLoss Assign] (OPL) | [Output phase loss] (OPL)
ODT | Output Phase Loss delay | 16#1BA9 = 7081 | 16#2028/52 | 16#84/01/52 = 132/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.5 s ... 10.0 s | [OutPhaseLoss Delay] (ODT) | [Output phase loss] (OPL)
IPL | Input Phase Loss assignment | 16#1B5A = 7002 | 16#2028/3 | 16#84/01/03 = 132/01/03 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [InPhaseLoss Assign] (IPL) | [Input phase loss] (IPL)
OHL | Drive overtemp error response | 16#1B60 = 7008 | 16#2028/9 | 16#84/01/09 = 132/01/09 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [DriveTemp ErrorResp] (OHL) | [Drive overload monit] (OBR)
THA | Drive thermal state Warning | 16#2B01 = 11009 | 16#2050/A | 16#98/01/0A = 152/01/10 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 100 % | 0 % ... 118 % | [Drv Thermal Warning] (THA) | [Drive overload monit] (OBR)
ETF | External error assignment | 16#1BDB = 7131 | 16#2029/20 | 16#84/01/84 = 132/01/132 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Ext Error assign] (ETF) | [External error] (ETF)
EPL | Drive response to external error | 16#1B5E = 7006 | 16#2028/7 | 16#84/01/07 = 132/01/07 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Ext Error Resp] (EPL) | [External error] (ETF)
USB | Response to undervoltage | 16#35EB = 13803 | 16#206C/4 | 16#A6/01/04 = 166/01/04 | USB | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error triggered] 0 |  | [Undervoltage Resp] (USB) | [Undervoltage handling] (USB)
URES | Evacuation mains voltage | 16#35E9 = 13801 | 16#206C/2 | 16#A6/01/02 = 166/01/02 | URES | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Mains voltage] (URES) | [Undervoltage handling] (USB)
USL | Undervoltage level | 16#35EA = 13802 | 16#206C/3 | 16#A6/01/03 = 166/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 100 V ... 435 V | [Undervoltage level] (USL) | [Undervoltage handling] (USB)
UST | Undervoltage timeout | 16#35EC = 13804 | 16#206C/5 | 16#A6/01/05 = 166/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.2 s | 0.2 s ... 999.9 s | [UnderVolt timeout] (UST) | [Undervoltage handling] (USB)
STP | Stop type on power loss | 16#1B5C = 7004 | 16#2028/5 | 16#84/01/05 = 132/01/05 | STP | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [Stop Type PLoss] (STP) | [Undervoltage handling] (USB)
TSM | Undervolt. restart time | 16#35F5 = 13813 | 16#206C/E | 16#A6/01/0E = 166/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 999.9 s | [UnderV. restart tm] (TSM) | [Undervoltage handling] (USB)
UPL | Under V prevention level | 16#35F3 = 13811 | 16#206C/C | 16#A6/01/0C = 166/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | Refer to programming manual | 141 V ... 495 V | [Prevention level] (UPL) | [Undervoltage handling] (USB)
STM | Maximum stop time | 16#35F6 = 13814 | 16#206C/F | 16#A6/01/0F = 166/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.01 s ... 60.00 s | [Max stop time] (STM) | [Undervoltage handling] (USB)
TBS | DC bus maintain time | 16#35F4 = 13812 | 16#206C/D | 16#A6/01/0D = 166/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 9999 s | 1 s ... 9999 s | [DC bus maintain time] (TBS) | [Undervoltage handling] (USB)
STRT | Output short circuit test | 16#0C28 = 3112 | 16#2001/D | 16#70/01/71 = 112/01/113 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Output Short Circuit Test] (STRT) | [Motor monitoring] (MOP)
COFM | Catch on fly mode | 16#0C29 = 3113 | 16#2001/E | 16#70/01/72 = 112/01/114 | COFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Measured] HWCOF |  | [Catch On Fly Mode] (COFM) | [Catch on the fly] (FLR)
LFL3 | Response to 4-20mA loss on AI3 | 16#1B65 = 7013 | 16#2028/E | 16#84/01/0E = 132/01/14 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI3 4-20mA loss] (LFL3) | [4-20 mA loss] (LFL)
INH | Disable Error Detection | 16#1BD5 = 7125 | 16#2029/1A | 16#84/01/7E = 132/01/126 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [ErrorDetect Disable] (INH) | [Fan] (CSFA) [Error detection disable] (INH)
INHS | Forced Run | 16#1BD6 = 7126 | 16#2029/1B | 16#84/01/7F = 132/01/127 | INHS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disabled] NO |  | [Forced Run] (INHS) | [Error detection disable] (INH)
INHR | Forced Run Reference Frequency | 16#1BD7 = 7127 | 16#2029/1C | 16#84/01/80 = 132/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 6553.5 Hz | [Forced Run Ref] (INHR) | [Error detection disable] (INH)
CLL | Response to Fieldbus module communication interruption | 16#1B67 = 7015 | 16#2028/10 | 16#84/01/10 = 132/01/16 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Fieldbus Interrupt Resp] (CLL) | [Communication Module] (COMO)
COL | Response to CANopen error | 16#1B63 = 7011 | 16#2028/C | 16#84/01/0C = 132/01/12 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CANopen Error Resp] (COL) | [Communication Module] (COMO)
SLL | Response to Modbus interruption | 16#1B62 = 7010 | 16#2028/B | 16#84/01/0B = 132/01/11 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Modbus Error Resp] (SLL) | [Fieldbus monitoring] (CLL)
TNL | Response to Autotuning error | 16#1B64 = 7012 | 16#2028/D | 16#84/01/0D = 132/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Tuning Error Resp] (TNL) | [Motor tune] (MTU)
PPI | Pairing password | 16#36B1 = 14001 | 16#206E/2 | 16#A7/01/02 = 167/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 9999 | [Pairing password] (PPI) | [My preferences] (MYP)
LFF | Fall back speed | 16#1BA8 = 7080 | 16#2028/51 | 16#84/01/51 = 132/01/81 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [FallbackSpeed] (LFF) | [4-20 mA loss] (LFL) [External error] (ETF) [Communication Module] (COMO) [Fieldbus monitoring] (CLL) [Fallback speed] (LFF) [Embedded modbus TCP] (EMTC) [High flow monitoring] (HFP) [Inlet pressure monitoring] (IPP) [Outlet pressure monitoring] (OPP) [Pumpcycle monitoring] (CSP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Pump low flow Monit] (PLF)
NCA1 | Scan output 1 address | 16#31B1 = 12721 | 16#2061/16 | 16#A0/01/7A = 160/01/122 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535
NCA2 | Scan output 2 address | 16#31B2 = 12722 | 16#2061/17 | 16#A0/01/7B = 160/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535
NCA3 | Scan output 3 address | 16#31B3 = 12723 | 16#2061/18 | 16#A0/01/7C = 160/01/124 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA4 | Scan output 4 address | 16#31B4 = 12724 | 16#2061/19 | 16#A0/01/7D = 160/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA5 | Scan output 5 address | 16#31B5 = 12725 | 16#2061/1A | 16#A0/01/7E = 160/01/126 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA6 | Scan output 6 address | 16#31B6 = 12726 | 16#2061/1B | 16#A0/01/7F = 160/01/127 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA7 | Scan output 7 address | 16#31B7 = 12727 | 16#2061/1C | 16#A0/01/80 = 160/01/128 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NCA8 | Scan output 8 address | 16#31B8 = 12728 | 16#2061/1D | 16#A0/01/81 = 160/01/129 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA1 | Scan input 1 address | 16#319D = 12701 | 16#2061/2 | 16#A0/01/66 = 160/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535
NMA2 | Scan input 2 address | 16#319E = 12702 | 16#2061/3 | 16#A0/01/67 = 160/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535
NMA3 | Scan input 3 address | 16#319F = 12703 | 16#2061/4 | 16#A0/01/68 = 160/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA4 | Scan input 4 address | 16#31A0 = 12704 | 16#2061/5 | 16#A0/01/69 = 160/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA5 | Scan input 5 address | 16#31A1 = 12705 | 16#2061/6 | 16#A0/01/6A = 160/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA6 | Scan input 6 address | 16#31A2 = 12706 | 16#2061/7 | 16#A0/01/6B = 160/01/107 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA7 | Scan input 7 address | 16#31A3 = 12707 | 16#2061/8 | 16#A0/01/6C = 160/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
NMA8 | Scan input 8 address | 16#31A4 = 12708 | 16#2061/9 | 16#A0/01/6D = 160/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA1 | Scan input 1 address | 16#3C29 = 15401 | 16#207C/2 | 16#AE/01/02 = 174/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 | [Scan. IN1 address] (OMA1) | [DeviceNet] (DNC)
OMA2 | Scan input 2 address | 16#3C2A = 15402 | 16#207C/3 | 16#AE/01/03 = 174/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 | [Scan. IN2 address] (OMA2) | [DeviceNet] (DNC)
OMA3 | Scan input 3 address | 16#3C2B = 15403 | 16#207C/4 | 16#AE/01/04 = 174/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan. IN3 address] (OMA3) | [DeviceNet] (DNC)
OMA4 | Scan input 4 address | 16#3C2C = 15404 | 16#207C/5 | 16#AE/01/05 = 174/01/05 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan. IN4 address] (OMA4) | [DeviceNet] (DNC)
OMA5 | Scan input 5 address | 16#3C2D = 15405 | 16#207C/6 | 16#AE/01/06 = 174/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA6 | Scan input 6 address | 16#3C2E = 15406 | 16#207C/7 | 16#AE/01/07 = 174/01/07 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA1 | Scan output 1 address | 16#3C3D = 15421 | 16#207C/16 | 16#AE/01/16 = 174/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 | [Scan.Out1 address] (OCA1) | [DeviceNet] (DNC)
OCA2 | Scan output 2 address | 16#3C3E = 15422 | 16#207C/17 | 16#AE/01/17 = 174/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 | [Scan.Out2 address] (OCA2) | [DeviceNet] (DNC)
OCA3 | Scan output 3 address | 16#3C3F = 15423 | 16#207C/18 | 16#AE/01/18 = 174/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan.Out3 address] (OCA3) | [DeviceNet] (DNC)
OCA4 | Scan output 4 address | 16#3C40 = 15424 | 16#207C/19 | 16#AE/01/19 = 174/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Scan.Out4 address] (OCA4) | [DeviceNet] (DNC)
OCA5 | Scan output 5 address | 16#3C41 = 15425 | 16#207C/1A | 16#AE/01/1A = 174/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA6 | Scan output 6 address | 16#3C42 = 15426 | 16#207C/1B | 16#AE/01/1B = 174/01/27 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
ADD | Drive Modbus Address | 16#1771 = 6001 | 16#201E/2 | 16#7F/01/02 = 127/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus Address] (ADD) | [Modbus Fieldbus] (MD1)
AMOC | Mdb add comm. Module | 16#19FB = 6651 | 16#2024/34 | 16#82/01/34 = 130/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 247 | [Modbus add Com.C.] (AMOC) | [Modbus Fieldbus] (MD1)
TBR | Modbus baud rate | 16#1773 = 6003 | 16#201E/4 | 16#7F/01/04 = 127/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [Modbus baud rate] (TBR) | [Modbus Fieldbus] (MD1)
TFO | Modbus format | 16#1774 = 6004 | 16#201E/5 | 16#7F/01/05 = 127/01/05 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [Modbus Format] (TFO) | [Modbus Fieldbus] (MD1)
TTO | Modbus timeout | 16#1775 = 6005 | 16#201E/6 | 16#7F/01/06 = 127/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [ModbusTimeout] (TTO) | [Modbus Fieldbus] (MD1)
ADCO | Drive CANopen address | 16#17A3 = 6051 | 16#201E/34 | 16#7F/01/34 = 127/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 127 | [CANopen Address ] (ADCO) | [CANopen ] (CNO)
BDCO | CANopen baudrate | 16#17A5 = 6053 | 16#201E/36 | 16#7F/01/36 = 127/01/54 | BDCO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Baud rate 250kbps] 250K |  | [CANopen Baudrate] (BDCO) | [CANopen ] (CNO)
ERCO | CANopen error | 16#17A8 = 6056 | 16#201E/39 | 16#7F/01/39 = 127/01/57 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [CANopen Error] (ERCO) | [CANopen map] (CNM) [CANopen ] (CNO)
FLO | Forced local assignment | 16#20EF = 8431 | 16#2036/20 | 16#8B/01/20 = 139/01/32 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Forced Local Assign] (FLO) | [Command and Reference] (CRP)
FLOC | Forced Local frequency assignment | 16#20F0 = 8432 | 16#2036/21 | 16#8B/01/21 = 139/01/33 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Forced Local Freq] (FLOC) | [Command and Reference] (CRP)
FLOT | Time-out forc. local | 16#20F1 = 8433 | 16#2036/22 | 16#8B/01/22 = 139/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s | [Time-out forc. local] (FLOT) | [Command and Reference] (CRP)
ADRC | Drive address | 16#19C9 = 6601 | 16#2024/2 | 16#82/01/02 = 130/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 65535 | [Address] (ADRC) | [DeviceNet] (DNC) [BACnet MS/TP] (BACM) [Profibus] (PBC) [Powerlink] (EPL)
PRFL | PPO profile used | 16#1A09 = 6665 | 16#2024/42 | 16#82/01/42 = 130/01/66 | PRFL | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [PPO profile used] (PRFL) | [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN)
DPMA | DP Master Active | 16#1A0A = 6666 | 16#2024/43 | 16#82/01/43 = 130/01/67 | DPMA | Communication parameters | R/W | WORD (Enumeration) | - | [Master 1] 1 |  | [DP Master Active] (DPMA) | [PROFIBUS DIAG] (PRB) [PROFINET DIAG] (PRN)
CIOA | Configured Assembly | 16#1A0B = 6667 | 16#2024/44 | 16#82/01/44 = 130/01/68 | CIOA | Configuration and settings | R/W | WORD (Enumeration) | - | [21/71] 21 |  | [Conf. Assembly] (CIOA) | [DeviceNet] (DNC)
BDR | Comm. option baud rate | 16#19CB = 6603 | 16#2024/4 | 16#82/01/04 = 130/01/04 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [Automatic] AUTO |  | [Bit rate] (BDR) | [DeviceNet] (DNC) [BACnet MS/TP] (BACM)
BDRU | Data rate used | 16#1A04 = 6660 | 16#2024/3D | 16#82/01/3D = 130/01/61 | TBR | Configuration and settings | R/W | WORD (Enumeration) | - | [Automatic] AUTO |  | [Data rate used] (BDRU) | [DEVICENET DIAG] (DVN) [PROFIBUS DIAG] (PRB) [BACnet MS/TP] (BACM)
RDS | Rate and duplex setting | 16#FAFB = 64251 |  |  | RDS | Configuration and settings | R/W | WORD (Enumeration) | - | [Auto detected] AUTO
EWE | Enable web and/or email | 16#FB08 = 64264 |  |  |  | Configuration and settings | R/W | WORD (BitString16) | - | 1
ARD | Actual rate and duplex | 16#FB0A = 64266 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Actual rate] (ARD) | [Ethernet Module Diag] (MTE)
L1D | DI1 Delay | 16#0FA1 = 4001 | 16#200A/2 | 16#75/01/02 = 117/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI1 Delay] (L1D) | [DI1 Configuration] (DI1)
R1 | R1 Assignment | 16#1389 = 5001 | 16#2014/2 | 16#7A/01/02 = 122/01/02 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in operating state "Fault"] FLT |  | [R1 Assignment] (R1) | [R1 configuration] (R1)
R2 | R2 Assignment | 16#138A = 5002 | 16#2014/3 | 16#7A/01/03 = 122/01/03 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [R2 Assignment] (R2) | [R2 configuration] (R2)
L2D | DI2 Delay | 16#0FA2 = 4002 | 16#200A/3 | 16#75/01/03 = 117/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI2 Delay] (L2D) | [DI2 Configuration] (DI2)
R1D | R1 Delay time | 16#1091 = 4241 | 16#200C/2A | 16#76/01/2A = 118/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R1 Delay time] (R1D) | [R1 configuration] (R1)
R2D | R2 Delay time | 16#1092 = 4242 | 16#200C/2B | 16#76/01/2B = 118/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R2 Delay time] (R2D) | [R2 configuration] (R2)
L3D | DI3 Delay | 16#0FA3 = 4003 | 16#200A/4 | 16#75/01/04 = 117/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI3 Delay] (L3D) | [DI3 Configuration] (DI3)
R1S | R1 Active level | 16#1069 = 4201 | 16#200C/2 | 16#76/01/02 = 118/01/02 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R1 Active at] (R1S) | [R1 configuration] (R1)
R2S | R2 Active level | 16#106A = 4202 | 16#200C/3 | 16#76/01/03 = 118/01/03 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R2 Active at] (R2S) | [R2 configuration] (R2)
L4D | DI4 Delay | 16#0FA4 = 4004 | 16#200A/5 | 16#75/01/05 = 117/01/05 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI4 Delay] (L4D) | [DI4 Configuration] (DI4)
R1H | R1 Holding time | 16#107D = 4221 | 16#200C/16 | 16#76/01/16 = 118/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R1 Holding time] (R1H) | [R1 configuration] (R1)
R2H | R2 Holding time | 16#107E = 4222 | 16#200C/17 | 16#76/01/17 = 118/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R2 Holding time] (R2H) | [R2 configuration] (R2)
L5D | DI5 Delay | 16#0FA5 = 4005 | 16#200A/6 | 16#75/01/06 = 117/01/06 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI5 Delay] (L5D) | [DI5 Configuration] (DI5)
L6D | DI6 Delay | 16#0FA6 = 4006 | 16#200A/7 | 16#75/01/07 = 117/01/07 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI6 Delay] (L6D) | [DI6 Configuration] (DI6)
FRHT | FRH high resolution | 16#0C96 = 3222 | 16#2002/17 | 16#71/01/17 = 113/01/23 |  | Configuration and settings | R | INT (Signed16) | 1 |  | -32767 ... 32767
SLCR | LCR without filter | 16#0C98 = 3224 | 16#2002/19 | 16#71/01/19 = 113/01/25 |  | Configuration and settings | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535
SRFR | RFR without filter | 16#0C99 = 3225 | 16#2002/1A | 16#71/01/1A = 113/01/26 |  | Configuration and settings | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz
SOTR | OTR without filter | 16#0C9A = 3226 | 16#2002/1B | 16#71/01/1B = 113/01/27 |  | Configuration and settings | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 %
SULN | ULN without filter | 16#0C9D = 3229 | 16#2002/1E | 16#71/01/1E = 113/01/30 |  | Configuration and settings | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V
SOPR | OPR without filter | 16#0CDA = 3290 | 16#2002/5B | 16#71/01/5B = 113/01/91 |  | Configuration and settings | R | INT (Signed16) | 1 % |  | -32767 % ... 32767 %
SAI1 | AI1 physical value without filter | 16#14AB = 5291 | 16#2016/5C | 16#7B/01/5C = 123/01/92 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI2 | AI2 physical value without filter | 16#14AC = 5292 | 16#2016/5D | 16#7B/01/5D = 123/01/93 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI3 | AI3 physical value without filter | 16#14AD = 5293 | 16#2016/5E | 16#7B/01/5E = 123/01/94 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO1 | AO1 physical value without filter | 16#14AF = 5295 | 16#2016/60 | 16#7B/01/60 = 123/01/96 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
ULT | Underld T. Delay Detect. | 16#384B = 14411 | 16#2072/C | 16#A9/01/0C = 169/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Unld T. Del. Detect] (ULT) | [Process underload] (ULD)
SRB | Hysteresis Frequency | 16#3841 = 14401 | 16#2072/2 | 16#A9/01/02 = 169/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.3 Hz | 0.3 Hz ... 500.0 Hz | [Hysteresis Freq] (SRB) | [Settings] (SET) [Process underload] (ULD) [Process overload] (OLD)
UDL | Underload Management | 16#384C = 14412 | 16#2072/D | 16#A9/01/0D = 169/01/13 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Underload Mangmt.] (UDL) | [Process underload] (ULD)
RMUD | Unld. Freq.Thr. Detection | 16#384E = 14414 | 16#2072/F | 16#A9/01/0F = 169/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Unld. FreqThr. Det.] (RMUD) | [Settings] (SET) [Process underload] (ULD)
LUL | Unld.Thr. at O speed | 16#384F = 14415 | 16#2072/10 | 16#A9/01/10 = 169/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [Unld.Thr.0.Speed] (LUL) | [Settings] (SET) [Process underload] (ULD)
LUN | Unld.Thr. at Nom. speed | 16#3850 = 14416 | 16#2072/11 | 16#A9/01/11 = 169/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 60 % | 20 % ... 100 % | [Unld.Thr.Nom.Speed] (LUN) | [Settings] (SET) [Process underload] (ULD)
TOL | Overload Time Detect. | 16#3855 = 14421 | 16#2072/16 | 16#A9/01/16 = 169/01/22 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 100 s | [Ovld Time Detect.] (TOL) | [Process overload] (OLD)
ODL | Ovld.Proces Management | 16#3856 = 14422 | 16#2072/17 | 16#A9/01/17 = 169/01/23 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Ovld.Proces.Mngmt] (ODL) | [Process overload] (OLD)
STOS | Safe Torque Off function Status | 16#3BDA = 15322 | 16#207B/17 | 16#AD/01/7B = 173/01/123 | STOS | Safety function | R | WORD (Enumeration) | -
ACCP | PID acceleration time | 16#2ED1 = 11985 | 16#2059/56 | 16#9C/01/BA = 156/01/186 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [PID acceleration time] (ACCP) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET) [Booster Control] (BSC)
ACCS | Acceleration on Start | 16#2350 = 9040 | 16#203C/29 | 16#8E/01/29 = 142/01/41 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 9999 | [Start Accel Ramp] (ACCS) | [Pump start stop] (PST) [Settings] (SET)
AI1I | AI1 input physical image (MAX = 8192) | 16#1466 = 5222 | 16#2016/17 | 16#7B/01/17 = 123/01/23 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI1J | AI1 Lowest Process | 16#1196 = 4502 | 16#200F/3 | 16#77/01/67 = 119/01/103 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI1 Lowest Process] (AI1J) | [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
AI1K | AI1 Highest Process | 16#11A0 = 4512 | 16#200F/D | 16#77/01/71 = 119/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI1 Highest Process] (AI1K) | [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
AI2I | AI2 input physical image (MAX = 8192) | 16#1467 = 5223 | 16#2016/18 | 16#7B/01/18 = 123/01/24 |  | Measurement parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI2J | AI2 Lowest Process | 16#1197 = 4503 | 16#200F/4 | 16#77/01/68 = 119/01/104 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI2 Lowest Process] (AI2J) | [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
AI2K | AI2 Highest Process | 16#11A1 = 4513 | 16#200F/E | 16#77/01/72 = 119/01/114 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI2 Highest Process] (AI2K) | [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
AI3I | AI3 input physical image (MAX = 8192) | 16#1468 = 5224 | 16#2016/19 | 16#7B/01/19 = 123/01/25 |  | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AI3J | AI3 Lowest Process | 16#1198 = 4504 | 16#200F/5 | 16#77/01/69 = 119/01/105 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI3 Lowest Process] (AI3J) | [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
AI3K | AI3 Highest Process | 16#11A2 = 4514 | 16#200F/F | 16#77/01/73 = 119/01/115 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI3 Highest Process] (AI3K) | [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
AI4C | Physical value AI4 | 16#147D = 5245 | 16#2016/2E | 16#7B/01/2E = 123/01/46 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI4E | AI4 intermediate point X | 16#1171 = 4465 | 16#200E/42 | 16#77/01/42 = 119/01/66 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 X Interm. point] (AI4E) | [AI4 configuration] (AI4)
AI4F | AI4 filter | 16#1167 = 4455 | 16#200E/38 | 16#77/01/38 = 119/01/56 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI4 filter] (AI4F) | [AI4] (AI4C) [AI4 configuration] (AI4)
AI4I | AI4 input physical image (MAX = 8192) | 16#1469 = 5225 | 16#2016/1A | 16#7B/01/1A = 123/01/26 |  | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AI4J | AI4 Lowest Process | 16#1199 = 4505 | 16#200F/6 | 16#77/01/6A = 119/01/106 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI4 Lowest Process] (AI4J) | [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
AI4K | AI4 Highest Process | 16#11A3 = 4515 | 16#200F/10 | 16#77/01/74 = 119/01/116 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI4 Highest Process] (AI4K) | [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
AI4R | AI4 real application image (MAX = 8192) | 16#1473 = 5235 | 16#2016/24 | 16#7B/01/24 = 123/01/36 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI4S | AI4 intermediate point Y | 16#117B = 4475 | 16#200E/4C | 16#77/01/4C = 119/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI4 Y Interm.point] (AI4S) | [AI4 configuration] (AI4)
AI4T | Configuration of AI4 | 16#1135 = 4405 | 16#200E/6 | 16#77/01/06 = 119/01/06 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI4 Type] (AI4T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4 configuration] (AI4) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
AI5C | AI5 customer image (1mV, 0.001mA) | 16#147E = 5246 | 16#2016/2F | 16#7B/01/2F = 123/01/47 |  | I/O parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AI5E | AI5 delinearization input level | 16#1172 = 4466 | 16#200E/43 | 16#77/01/43 = 119/01/67 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 X Interm. point] (AI5E) | [AI5 configuration] (AI5)
AI5F | AI5 cutoff time of the low-filter | 16#1168 = 4456 | 16#200E/39 | 16#77/01/39 = 119/01/57 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AI5 filter] (AI5F) | [AI5] (AI5C) [AI5 configuration] (AI5)
AI5I | AI5 input physical image (MAX = 8192) | 16#146A = 5226 | 16#2016/1B | 16#7B/01/1B = 123/01/27 |  | Measurement parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AI5J | AI5 Lowest Process | 16#119A = 4506 | 16#200F/7 | 16#77/01/6B = 119/01/107 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI5 Lowest Process] (AI5J) | [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
AI5K | AI5 Highest Process | 16#11A4 = 4516 | 16#200F/11 | 16#77/01/75 = 119/01/117 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AI5 Highest Process] (AI5K) | [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
AI5R | AI5 real application image (MAX = 8192) | 16#1474 = 5236 | 16#2016/25 | 16#7B/01/25 = 123/01/37 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AI5S | AI5 delinearization output level | 16#117C = 4476 | 16#200E/4D | 16#77/01/4D = 119/01/77 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 100 % | [AI5 Y Interm.point] (AI5S) | [AI5 configuration] (AI5)
AI5T | AI5 type | 16#1136 = 4406 | 16#200E/7 | 16#77/01/07 = 119/01/07 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AI5 Type] (AI5T) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5 configuration] (AI5) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
AIC1 | Channel assignment for virtual Analog Input AIV1 | 16#14A2 = 5282 | 16#2016/53 | 16#7B/01/53 = 123/01/83 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AIV1 Channel Assign] (AIC1) | [Virtual AI1] (AV1) [AIV1 Sensor Config.] (ICV1) [AIV1 Sensor Config.] (OCV1) [AIV1 Sensor Config.] (IFV1) [AIV1 Configuration] (PFV1) [AIV1 Sensor Config.] (LSV1) [AIV1 Sensor Config.] (BIV1) [AIV1 Configuration] (LCV1) [AIV1 Configuration] (LIV1) [AIV1 Sensor Config.] (SIV1) [AIV1 Sensor Config.] (SOV1) [AIV1 Sensor Config.] (WOV1) [AIV1 Sensor Config.] (PF1V) [AIV1 Sensor Config.] (FIV1) [AIV1 Configuration] (PPV1) [AIV1 Sensor Config. ] (LFV1) [AIV1 Sensor Config.] (NPV1) [AIV1 Sensor Config.] (IPV1) [AIV1 Sensor Config.] (OOV1) [AIV1 Sensor Config.] (HIV1)
AO1I | AO1 output physical image (MAX = 8192) | 16#1483 = 5251 | 16#2016/34 | 16#7B/01/34 = 123/01/52 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO2 | AQ2 assignment | 16#139E = 5022 | 16#2014/17 | 16#7A/01/17 = 122/01/23 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Motor current] OCR |  | [AQ2 assignment] (AO2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AO2C | AQ2 physical value | 16#1498 = 5272 | 16#2016/49 | 16#7B/01/49 = 123/01/73 |  | I/O parameters | R/W | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
AO2F | AQ2 filter | 16#1204 = 4612 | 16#2010/D | 16#78/01/0D = 120/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.00 s | 0.00 s ... 10.00 s | [AQ2 Filter] (AO2F) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AO2I | AO2 output physical image (MAX = 8192) | 16#1484 = 5252 | 16#2016/35 | 16#7B/01/35 = 123/01/53 |  | I/O parameters | R | INT (Signed16) | 1 |  | -32767 ... 32767
AO2R | AO2 real application image (MAX = 8192) | 16#148E = 5262 | 16#2016/3F | 16#7B/01/3F = 123/01/63 |  | I/O parameters | R/W | INT (Signed16) | 1 |  | -32767 ... 32767
AO2T | Configuration of AQ2 | 16#11FA = 4602 | 16#2010/3 | 16#78/01/03 = 120/01/03 | AIOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Current] 0A |  | [AQ2 Type] (AO2T) | [AQ2 configuration] (AO2)
AOH2 | AQ2 max output value | 16#122C = 4652 | 16#2010/35 | 16#78/01/35 = 120/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AQ2 max output] (AOH2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
AOL2 | AQ2 min output value | 16#1222 = 4642 | 16#2010/2B | 16#78/01/2B = 120/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AQ2 min output] (AOL2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
APPS | Application state | 16#3E6C = 15980 | 16#2081/51 | 16#B0/01/B5 = 176/01/181 | APPS | Status parameters | R | WORD (Enumeration) | - |  |  | [Application state] (APPS) | [Control] (CTR) [Application Parameters] (APR)
ASH2 | Scaling AQ2 max | 16#1240 = 4672 | 16#2010/49 | 16#78/01/49 = 120/01/73 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 max] (ASH2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
ASL2 | Scaling AQ2 min | 16#1236 = 4662 | 16#2010/3F | 16#78/01/3F = 120/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Scaling AQ2 min] (ASL2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
ASLC | Advanced Sleep Check Speed Condition | 16#2E05 = 11781 | 16#2057/52 | 16#9B/01/B6 = 155/01/182 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Condition] (ASLC) | [Advanced sleep check] (ADS) [Settings] (SET)
ASLD | Advanced Sleep Check Delay | 16#2E06 = 11782 | 16#2057/53 | 16#9B/01/B7 = 155/01/183 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 20 s | 0 s ... 9999 s | [Sleep Check Delay] (ASLD) | [Advanced sleep check] (ADS) [Settings] (SET)
ASLM | Advanced Sleep Mode | 16#2E04 = 11780 | 16#2057/51 | 16#9B/01/B5 = 155/01/181 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sleep Mode] (ASLM) | [Advanced sleep check] (ADS)
ASLR | Advanced Sleep Check Reference Speed | 16#2E07 = 11783 | 16#2057/54 | 16#9B/01/B8 = 155/01/184 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Sleep Ref spd] (ASLR) | [Advanced sleep check] (ADS) [Settings] (SET)
CAR | Customer Warning clearing | 16#3F98 = 16280 | 16#2084/51 | 16#B2/01/51 = 178/01/81 | CAR | Configuration and settings | R/W | WORD (Enumeration) | - | [No Warning clearing] NO |  | [Warning Clearing] (CAR) | [Customer events] (CUEV)
CASH | Money saved | 16#2A36 = 10806 | 16#204E/7 | 16#97/01/07 = 151/01/07 |  | Actual values parameters | R | UINT (Unsigned32) | Refer to programming manual |  | 0 ... 4294967295 | [Money Saved] (CASH) | [Energy Saving] (ESA)
CC1 | Time Counter 1 | 16#3F84 = 16260 | 16#2084/3D | 16#B2/01/3D = 178/01/61 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 1] (CC1) | [Customer event 1] (CE1)
CC2 | Time Counter 2 | 16#3F86 = 16262 | 16#2084/3F | 16#B2/01/3F = 178/01/63 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 2] (CC2) | [Customer event 2] (CE2)
CC3 | Time Counter 3 | 16#3F88 = 16264 | 16#2084/41 | 16#B2/01/41 = 178/01/65 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 3] (CC3) | [Customer event 3] (CE3)
CC4 | Time Counter 4 | 16#3F8A = 16266 | 16#2084/43 | 16#B2/01/43 = 178/01/67 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 4] (CC4) | [Customer event 4] (CE4)
CC5 | Time Counter 5 | 16#3F8C = 16268 | 16#2084/45 | 16#B2/01/45 = 178/01/69 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Time counter 5] (CC5) | [Customer event 5] (CE5)
CCA1 | Configuration of customer Warning 1 | 16#3F48 = 16200 | 16#2084/1 | 16#B2/01/01 = 178/01/01 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 1] (CCA1) | [Customer event 1] (CE1)
CCA2 | Configuration of customer Warning 2 | 16#3F49 = 16201 | 16#2084/2 | 16#B2/01/02 = 178/01/02 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 2] (CCA2) | [Customer event 2] (CE2)
CCA3 | Configuration of customer Warning 3 | 16#3F4A = 16202 | 16#2084/3 | 16#B2/01/03 = 178/01/03 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 3] (CCA3) | [Customer event 3] (CE3)
CCA4 | Configuration of customer Warning 4 | 16#3F4B = 16203 | 16#2084/4 | 16#B2/01/04 = 178/01/04 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 4] (CCA4) | [Customer event 4] (CE4)
CCA5 | Configuration of customer Warning 5 | 16#3F4C = 16204 | 16#2084/5 | 16#B2/01/05 = 178/01/05 | CCA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not Configured] NO |  | [Config Warning 5] (CCA5) | [Customer event 5] (CE5)
CCL1 | Configuration Counter Limit 1 | 16#3F70 = 16240 | 16#2084/29 | 16#B2/01/29 = 178/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 1] (CCL1) | [Customer event 1] (CE1)
CCL2 | Configuration Counter Limit 2 | 16#3F72 = 16242 | 16#2084/2B | 16#B2/01/2B = 178/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 2] (CCL2) | [Customer event 2] (CE2)
CCL3 | Configuration Counter Limit 3 | 16#3F74 = 16244 | 16#2084/2D | 16#B2/01/2D = 178/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 3] (CCL3) | [Customer event 3] (CE3)
CCL4 | Configuration Counter Limit 4 | 16#3F76 = 16246 | 16#2084/2F | 16#B2/01/2F = 178/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 4] (CCL4) | [Customer event 4] (CE4)
CCL5 | Configuration Counter Limit 5 | 16#3F78 = 16248 | 16#2084/31 | 16#B2/01/31 = 178/01/49 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s | 0 s | 0 s ... 4294967295 s | [Counter limit 5] (CCL5) | [Customer event 5] (CE5)
CCS1 | Configuration Counter Source 1 | 16#3F52 = 16210 | 16#2084/B | 16#B2/01/0B = 178/01/11 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 1] (CCS1) | [Customer event 1] (CE1)
CCS2 | Configuration Counter Source 2 | 16#3F53 = 16211 | 16#2084/C | 16#B2/01/0C = 178/01/12 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 2] (CCS2) | [Customer event 2] (CE2)
CCS3 | Configuration Counter Source 3 | 16#3F54 = 16212 | 16#2084/D | 16#B2/01/0D = 178/01/13 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 3] (CCS3) | [Customer event 3] (CE3)
CCS4 | Configuration Counter Source 4 | 16#3F55 = 16213 | 16#2084/E | 16#B2/01/0E = 178/01/14 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 4] (CCS4) | [Customer event 4] (CE4)
CCS5 | Configuration Counter Source 5 | 16#3F56 = 16214 | 16#2084/F | 16#B2/01/0F = 178/01/15 | CCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [Drive in Running State] 2 |  | [Counter Source 5] (CCS5) | [Customer event 5] (CE5)
CDT1 | Date Time Warning 1 | 16#3F5C = 16220 | 16#2084/15 | 16#B2/01/15 = 178/01/21 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT2 | Date Time Warning 2 | 16#3F5E = 16222 | 16#2084/17 | 16#B2/01/17 = 178/01/23 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT3 | Date Time Warning 3 | 16#3F60 = 16224 | 16#2084/19 | 16#B2/01/19 = 178/01/25 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT4 | Date Time Warning 4 | 16#3F62 = 16226 | 16#2084/1B | 16#B2/01/1B = 178/01/27 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CDT5 | Date Time Warning 5 | 16#3F64 = 16228 | 16#2084/1D | 16#B2/01/1D = 178/01/29 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 2162688 | 2162688 ... 4288616251
CHT | Flow Limit Threshold active | 16#38B0 = 14512 | 16#2073/D | 16#A9/01/71 = 169/01/113 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow Lim Thd Active] (CHT) | [Settings] (SET) [Flow limitation] (FLM)
CMP9 | Cmd word | 16#1C47 = 7239 | 16#202A/28 | 16#85/01/28 = 133/01/40 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMP9) | [None] (DP9)
CMPA | Cmd word | 16#1DCE = 7630 | 16#202E/1F | 16#87/01/1F = 135/01/31 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPA) | [None] (DPA)
CMPB | Cmd word | 16#1DCF = 7631 | 16#202E/20 | 16#87/01/20 = 135/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [Cmd word] (CMPB) | [None] (DPB)
CMPC | CMD command word | 16#1DD0 = 7632 | 16#202E/21 | 16#87/01/21 = 135/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPC) | [None] (DPC)
CMPD | CMD command word | 16#1DD1 = 7633 | 16#202E/22 | 16#87/01/22 = 135/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPD) | [None] (DPD)
CMPE | CMD command word | 16#1DD2 = 7634 | 16#202E/23 | 16#87/01/23 = 135/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPE) | [None] (DPE)
CMPF | CMD command word | 16#1DD3 = 7635 | 16#202E/24 | 16#87/01/24 = 135/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [CMD word] (CMPF) | [None] (DPF)
CO2S | Co2 Saved | 16#2A38 = 10808 | 16#204E/9 | 16#97/01/09 = 151/01/09 |  | Actual values parameters | R | UINT (Unsigned32) | 0.1 t |  | 0.0 t ... 429496729.5 t | [Co2 Saved] (CO2S) | [Energy Saving] (ESA)
CRH1 | AI1 current scaling parameter of 100% | 16#115A = 4442 | 16#200E/2B | 16#77/01/2B = 119/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI1 Max Value] (CRH1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [AI1 configuration] (AI1) [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
CRH2 | AI2 current scaling parameter of 100% | 16#115B = 4443 | 16#200E/2C | 16#77/01/2C = 119/01/44 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI2 Max Value] (CRH2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [AI2 configuration] (AI2) [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
CRH4 | AI4 current scaling parameter of 100% | 16#115D = 4445 | 16#200E/2E | 16#77/01/2E = 119/01/46 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI4 Max Value] (CRH4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [AI4 configuration] (AI4) [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
CRH5 | AI5 current scaling parameter of 100% | 16#115E = 4446 | 16#200E/2F | 16#77/01/2F = 119/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 20.0 mA | 0.0 mA ... 20.0 mA | [AI5 Max Value] (CRH5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [AI5 configuration] (AI5) [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
CRL1 | AI1 current scaling parameter of 0% | 16#1150 = 4432 | 16#200E/21 | 16#77/01/21 = 119/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI1 Min. Value] (CRL1) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1] (AI1C) [AI1 configuration] (AI1) [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
CRL2 | AI2 current scaling parameter of 0% | 16#1151 = 4433 | 16#200E/22 | 16#77/01/22 = 119/01/34 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI2 Min. Value] (CRL2) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2] (AI2C) [AI2 configuration] (AI2) [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
CRL4 | AI4 current scaling parameter of 0% | 16#1153 = 4435 | 16#200E/24 | 16#77/01/24 = 119/01/36 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI4 Min. Value] (CRL4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [AI4 configuration] (AI4) [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
CRL5 | AI5 current scaling parameter of 0% | 16#1154 = 4436 | 16#200E/25 | 16#77/01/25 = 119/01/37 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 mA | 0.0 mA | 0.0 mA ... 20.0 mA | [AI5 Min. Value] (CRL5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [AI5 configuration] (AI5) [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
CRP9 | Cmd & ref channel | 16#1C83 = 7299 | 16#202A/64 | 16#85/01/64 = 133/01/100 |  | History parameters | R | WORD (BitString16) | -
CRPA | Cmd & ref channel | 16#1E0A = 7690 | 16#202E/5B | 16#87/01/5B = 135/01/91 |  | History parameters | R | WORD (BitString16) | -
CRPB | Cmd & ref channel | 16#1E0B = 7691 | 16#202E/5C | 16#87/01/5C = 135/01/92 |  | History parameters | R | WORD (BitString16) | -
CRPC | Cmd & ref channel | 16#1E0C = 7692 | 16#202E/5D | 16#87/01/5D = 135/01/93 |  | History parameters | R | WORD (BitString16) | -
CRPD | Cmd & ref channel | 16#1E0D = 7693 | 16#202E/5E | 16#87/01/5E = 135/01/94 |  | History parameters | R | WORD (BitString16) | -
CRPE | Cmd & ref channel | 16#1E0E = 7694 | 16#202E/5F | 16#87/01/5F = 135/01/95 |  | History parameters | R | WORD (BitString16) | -
CRPF | Cmd & ref channel | 16#1E0F = 7695 | 16#202E/60 | 16#87/01/60 = 135/01/96 |  | History parameters | R | WORD (BitString16) | -
CTDL | Low Current Threshold | 16#2B02 = 11010 | 16#2050/B | 16#98/01/0B = 152/01/11 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Low I Threshold] (CTDL) | [Threshold reached] (THRE) [Settings] (SET)
CVHS | Speed level from which check-valve ramp is used | 16#2352 = 9042 | 16#203C/2B | 16#8E/01/2B = 142/01/43 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Valve Spd 2] (CVHS) | [Pump start stop] (PST) [Settings] (SET)
CVLS | Speed Level up to which check-valve ramp is used | 16#2353 = 9043 | 16#203C/2C | 16#8E/01/2C = 142/01/44 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Check Valve Spd 1] (CVLS) | [Pump start stop] (PST) [Settings] (SET)
D11D | DQ11 activation delay | 16#10BB = 4283 | 16#200C/54 | 16#76/01/54 = 118/01/84 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ11 actv delay] (D11D) | [DQ11 Configuration] (DO11)
D11H | DQ11 holding delay | 16#10B1 = 4273 | 16#200C/4A | 16#76/01/4A = 118/01/74 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ11 hold delay] (D11H) | [DQ11 Configuration] (DO11)
D11S | DQ11 status (output active level) | 16#10A7 = 4263 | 16#200C/40 | 16#76/01/40 = 118/01/64 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [DQ11 status] (D11S) | [DQ11 Configuration] (DO11)
D12D | DQ12 activation delay | 16#10BC = 4284 | 16#200C/55 | 16#76/01/55 = 118/01/85 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [DQ12 actv delay] (D12D) | [DQ12 Configuration] (DO12)
D12H | DQ12 holding delay | 16#10B2 = 4274 | 16#200C/4B | 16#76/01/4B = 118/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [DQ12 hold delay] (D12H) | [DQ12 Configuration] (DO12)
D12S | DQ12 status (output active level) | 16#10A8 = 4264 | 16#200C/41 | 16#76/01/41 = 118/01/65 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [DQ12 status] (D12S) | [DQ12 Configuration] (DO12)
DECS | Deceleration on Stop | 16#2354 = 9044 | 16#203C/2D | 16#8E/01/2D = 142/01/45 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 9999 | [Final Dec. Ramp] (DECS) | [Pump start stop] (PST) [Settings] (SET)
DECV | Deceleration while check valve is closing (Smooth) | 16#2351 = 9041 | 16#203C/2A | 16#8E/01/2A = 142/01/42 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 9999 | [Dec. Check Valve] (DECV) | [Pump start stop] (PST) [Settings] (SET)
DFL | Flow limit Deceleration | 16#38B2 = 14514 | 16#2073/F | 16#A9/01/73 = 169/01/115 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 50 | 1 ... 9999 | [Flow. Limit Dec.] (DFL) | [Settings] (SET) [Flow limitation] (FLM)
DM0 | Hour and minute of actual fault | 16#1C8E = 7310 | 16#202B/B | 16#85/01/6F = 133/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM1 | Hour and minute of fault record x (1 is last) | 16#1C8F = 7311 | 16#202B/C | 16#85/01/70 = 133/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM2 | Hour and minute of fault record x (1 is last) | 16#1C90 = 7312 | 16#202B/D | 16#85/01/71 = 133/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM3 | Hour and minute of fault record x (1 is last) | 16#1C91 = 7313 | 16#202B/E | 16#85/01/72 = 133/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM4 | Hour and minute of fault record x (1 is last) | 16#1C92 = 7314 | 16#202B/F | 16#85/01/73 = 133/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM5 | Hour and minute of fault record x (1 is last) | 16#1C93 = 7315 | 16#202B/10 | 16#85/01/74 = 133/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM6 | Hour and minute of fault record x (1 is last) | 16#1C94 = 7316 | 16#202B/11 | 16#85/01/75 = 133/01/117 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM7 | Hour and minute of fault record x (1 is last) | 16#1C95 = 7317 | 16#202B/12 | 16#85/01/76 = 133/01/118 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM8 | Hour and minute of fault record x (1 is last) | 16#1C96 = 7318 | 16#202B/13 | 16#85/01/77 = 133/01/119 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DM9 | Hour and minute of fault record x (1 is last) | 16#1C97 = 7319 | 16#202B/14 | 16#85/01/78 = 133/01/120 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMA | Hour and minute of fault record x (1 is last) | 16#1E1E = 7710 | 16#202F/B | 16#87/01/6F = 135/01/111 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMB | Hour and minute of fault record x (1 is last) | 16#1E1F = 7711 | 16#202F/C | 16#87/01/70 = 135/01/112 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMC | Hour and minute of fault record x (1 is last) | 16#1E20 = 7712 | 16#202F/D | 16#87/01/71 = 135/01/113 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMD | Hour and minute of fault record x (1 is last) | 16#1E21 = 7713 | 16#202F/E | 16#87/01/72 = 135/01/114 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DME | Hour and minute of fault record x (1 is last) | 16#1E22 = 7714 | 16#202F/F | 16#87/01/73 = 135/01/115 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DMF | Hour and minute of fault record x (1 is last) | 16#1E23 = 7715 | 16#202F/10 | 16#87/01/74 = 135/01/116 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
DO11 | DO11 assignment | 16#13A9 = 5033 | 16#2014/22 | 16#7A/01/22 = 122/01/34 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ11 assignment] (DO11) | [DQ11 Configuration] (DO11)
DO12 | DO12 assignment | 16#13AA = 5034 | 16#2014/23 | 16#7A/01/23 = 122/01/35 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [DQ12 assignment] (DO12) | [DQ12 Configuration] (DO12)
DP9 | Fault record 9 (1 is last) | 16#1C29 = 7209 | 16#202A/A | 16#85/01/0A = 133/01/10 | LFT | History parameters | R | WORD (Enumeration) | -
DPA | Fault record 10 (1 is last) | 16#1DB0 = 7600 | 16#202E/1 | 16#87/01/01 = 135/01/01 | LFT | History parameters | R | WORD (Enumeration) | -
DPB | Fault record 11 (1 is last) | 16#1DB1 = 7601 | 16#202E/2 | 16#87/01/02 = 135/01/02 | LFT | History parameters | R | WORD (Enumeration) | -
DPC | Fault record 12 (1 is last) | 16#1DB2 = 7602 | 16#202E/3 | 16#87/01/03 = 135/01/03 | LFT | History parameters | R | WORD (Enumeration) | -
DPD | Fault record 13 (1 is last) | 16#1DB3 = 7603 | 16#202E/4 | 16#87/01/04 = 135/01/04 | LFT | History parameters | R | WORD (Enumeration) | -
DPE | Fault record 14 (1 is last) | 16#1DB4 = 7604 | 16#202E/5 | 16#87/01/05 = 135/01/05 | LFT | History parameters | R | WORD (Enumeration) | -
DPF | Fault record 15 (1 is last) | 16#1DB5 = 7605 | 16#202E/6 | 16#87/01/06 = 135/01/06 | LFT | History parameters | R | WORD (Enumeration) | -
DRT | Dual rating state | 16#0BC2 = 3010 | 16#2000/B | 16#70/01/0B = 112/01/11 | DRT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Normal duty] NORMAL |  | [Dual rating] (DRT) | [Motor parameters] (MPA)
DRYD | Dry Run error time delay | 16#3E50 = 15952 | 16#2081/35 | 16#B0/01/99 = 176/01/153 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 5 s | 0 s ... 3600 s | [DryRun Error Delay] (DRYD) | [Dry run Monit] (DYR) [Settings] (SET)
DRYM | Dry Run Mode | 16#3E4E = 15950 | 16#2081/33 | 16#B0/01/97 = 176/01/151 | DRYM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [DryRun Mode] (DRYM) | [Dry run Monit] (DYR)
DRYR | Dry Run restart time delay | 16#3E51 = 15953 | 16#2081/36 | 16#B0/01/9A = 176/01/154 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 60 s | 10 s ... 3600 s | [DryRun Restart Delay] (DRYR) | [Dry run Monit] (DYR) [Settings] (SET)
DRYW | Dry Run Switch Select | 16#3E4F = 15951 | 16#2081/34 | 16#B0/01/98 = 176/01/152 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Switch Select] (DRYW) | [Dry run Monit] (DYR)
DRYX | Dry Run Factor | 16#3E52 = 15954 | 16#2081/37 | 16#B0/01/9B = 176/01/155 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 90 % | 0 % ... 100 % | [Dry Run Factor] (DRYX) | [Dry run Monit] (DYR) [Settings] (SET)
ECI | Energy Consumption Indicator | 16#3EB5 = 16053 | 16#2082/36 | 16#B1/01/36 = 177/01/54 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | 0 ... 32767 | [Energy Cons. Ind.] (ECI) | [Variable Speed Pump] (MPP)
ECO2 | CO2 ratio | 16#2A32 = 10802 | 16#204E/3 | 16#97/01/03 = 151/01/03 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.001 kg/kWh | 0.000 kg/kWh | 0.000 kg/kWh ... 65.535 kg/kWh | [CO2 ratio] (ECO2) | [Energy Saving] (ESA)
ECST | kWh Cost | 16#2A31 = 10801 | 16#204E/2 | 16#97/01/02 = 151/01/02 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [kWh Cost] (ECST) | [Energy Saving] (ESA)
EFY | Efficiency | 16#3EB2 = 16050 | 16#2082/33 | 16#B1/01/33 = 177/01/51 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Efficiency] (EFY) | [Variable Speed Pump] (MPP)
EFYJ | Lowest Efficiency | 16#3EB4 = 16052 | 16#2082/35 | 16#B1/01/35 = 177/01/53 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Lowest Eff.] (EFYJ) | [Variable Speed Pump] (MPP)
EFYK | Highest Efficiency | 16#3EB3 = 16051 | 16#2082/34 | 16#B1/01/34 = 177/01/52 |  | Actual values parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Highest Eff.] (EFYK) | [Variable Speed Pump] (MPP)
EP9 | Status of last error 1 | 16#1C33 = 7219 | 16#202A/14 | 16#85/01/14 = 133/01/20 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 1 Status] (EP9) | [None] (DP9)
EPA | Status of last error 2 | 16#1DBA = 7610 | 16#202E/B | 16#87/01/0B = 135/01/11 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 2 Status] (EPA) | [None] (DPA)
EPB | Status of last error 3 | 16#1DBB = 7611 | 16#202E/C | 16#87/01/0C = 135/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 3 Status] (EPB) | [None] (DPB)
EPC | Status of last error 4 | 16#1DBC = 7612 | 16#202E/D | 16#87/01/0D = 135/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Last Error 4 Status] (EPC) | [None] (DPC)
EPD | State word | 16#1DBD = 7613 | 16#202E/E | 16#87/01/0E = 135/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPD) | [None] (DPD)
EPE | State word | 16#1DBE = 7614 | 16#202E/F | 16#87/01/0F = 135/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPE) | [None] (DPE)
EPF | State word | 16#1DBF = 7615 | 16#202E/10 | 16#87/01/10 = 135/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETA state word] (EPF) | [None] (DPF)
EPI | Energy Performance Indicator | 16#3EB6 = 16054 | 16#2082/37 | 16#B1/01/37 = 177/01/55 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | 0 ... 32767 | [Energy Perf. Ind] (EPI) | [Variable Speed Pump] (MPP)
EPRW | Active Electrical output power estimation | 16#0CDD = 3293 | 16#2002/5E | 16#71/01/5E = 113/01/94 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Acv Elc Out Pwr Estm] (EPRW) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO) [Variable Speed Pump] (MPP)
ERR | Ethernet Error Code | 16#FB0E = 64270 |  |  |  | Fault parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Ethernet Error Code] (ERR) | [PROFINET DIAG] (PRN)
ESAV | Energy Saved | 16#2A34 = 10804 | 16#204E/5 | 16#97/01/05 = 151/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Energy Saved] (ESAV) | [Energy Saving] (ESA)
ETAD | DRIVECOM : Status word | 16#219B = 8603 | 16#2038/4 | 16#8C/01/04 = 140/01/04 |  | Status parameters | R | WORD (BitString16) | -
ETHF | Ethernet embedded fault (ETHF) | 16#1BE0 = 7136 | 16#2029/25 | 16#84/01/89 = 132/01/137 |  | Fault parameters | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535
ETHL | Ethernet error response | 16#1B6D = 7021 | 16#2028/16 | 16#84/01/16 = 132/01/22 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Eth Error Response] (ETHL) | [Embedded modbus TCP] (EMTC) [Communication Module] (COMO)
F2DL | 2 Frequency Threshold | 16#2B04 = 11012 | 16#2050/D | 16#98/01/0D = 152/01/13 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [2 Freq. Threshold] (F2DL) | [Threshold reached] (THRE) [Settings] (SET)
FPBT | Fan operation time | 16#0CC0 = 3264 | 16#2002/41 | 16#71/01/41 = 113/01/65 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [Fan Operation Time] (FPBT) | [Counter Management] (ELT)
FEM | Flow Estimation Mode | 16#3E80 = 16000 | 16#2082/1 | 16#B1/01/01 = 177/01/01 | FEM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disable pump characteristics] NO |  | [Flow Estimation Mode] (FEM) | [Flow estimation] (SFE)
FLCM | Mode Selection | 16#3DE0 = 15840 | 16#2080/29 | 16#B0/01/29 = 176/01/41 | FLCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Inactive] NO |  | [Mode Selection] (FLCM) | [Friction loss comp] (FLC)
FLDA | Alpha | 16#3DE1 = 15841 | 16#2080/2A | 16#B0/01/2A = 176/01/42 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 | 2.0 | 0.0 ... 2.0 | [Alpha] (FLDA) | [Friction loss comp] (FLC) [Settings] (SET)
FLH0 | Static compensation | 16#3DE4 = 15844 | 16#2080/2D | 16#B0/01/2D = 176/01/45 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Static Compensation] (FLH0) | [Friction loss comp] (FLC) [Settings] (SET)
FLH1 | Compensation at Point 1 | 16#3DE2 = 15842 | 16#2080/2B | 16#B0/01/2B = 176/01/43 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Comp. at Point 1] (FLH1) | [Friction loss comp] (FLC) [Settings] (SET)
FLM | Flow limitation Mode | 16#38B3 = 14515 | 16#2073/10 | 16#A9/01/74 = 169/01/116 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Flow limitation Mode] (FLM) | [Flow limitation] (FLM)
FLPD | Friction Loss Delta Pressure | 16#3DE5 = 15845 | 16#2080/2E | 16#B0/01/2E = 176/01/46 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Delta Pressure] (FLPD) | [Friction loss comp] (FLC)
FLQ1 | Flow Rate Working Point | 16#3DE3 = 15843 | 16#2080/2C | 16#B0/01/2C = 176/01/44 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Flow at Point 1] (FLQ1) | [Friction loss comp] (FLC) [Settings] (SET)
FS1A | Installation Flow Sensor Assignment | 16#3D57 = 15703 | 16#207F/4 | 16#AF/01/68 = 175/01/104 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Inst. Flow Assign.] (FS1A) | [Sensors Assignment] (SSC) [High flow monitoring] (HFP) [Sleep menu] (SLP) [Friction loss comp] (FLC) [Flow limitation] (FLM) [Stage/Destage Cond.] (SDCM) [Level Control] (LCC)
FS1C | Total Quantity | 16#3D65 = 15717 | 16#207F/12 | 16#AF/01/76 = 175/01/118 |  | Actual values parameters | R/WS | INT (Signed32) | Refer to programming manual |  | 0 ... 2147483647 | [Total Quantity] (FS1C) | [Application Parameters] (APR)
FS1J | LowestFlow | 16#3EB8 = 16056 | 16#2082/39 | 16#B1/01/39 = 177/01/57 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Lowest Flow] (FS1J) | [Application Parameters] (APR)
FS1K | Highest Flow | 16#3EB7 = 16055 | 16#2082/38 | 16#B1/01/38 = 177/01/56 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Highest Flow] (FS1K) | [Application Parameters] (APR)
FS1V | Installation Flow Value | 16#3D63 = 15715 | 16#207F/10 | 16#AF/01/74 = 175/01/116 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Installation Flow] (FS1V) | [Control] (CTR) [Application Parameters] (APR)
FSPD | Fan speed | 16#0CBF = 3263 | 16#2002/40 | 16#71/01/40 = 113/01/64 |  | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
FTDL | Low Freq. Threshold | 16#2B03 = 11011 | 16#2050/C | 16#98/01/0C = 152/01/12 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Low Freq.Threshold] (FTDL) | [Threshold reached] (THRE) [Settings] (SET)
FTO | Ovld time Before Restart | 16#3857 = 14423 | 16#2072/18 | 16#A9/01/18 = 169/01/24 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Overload T.B.Rest.] (FTO) | [Settings] (SET) [Process overload] (OLD)
FTU | Unld Time Before Restart | 16#384D = 14413 | 16#2072/E | 16#A9/01/0E = 169/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 0 min | 0 min ... 6 min | [Underload T.B.Rest.] (FTU) | [Settings] (SET) [Process underload] (ULD)
GRFL | Ground Fault activation | 16#1B76 = 7030 | 16#2028/1F | 16#84/01/1F = 132/01/31 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 % | -0.1 % | -0.2 % ... 100.0 % | [Ground Fault Activation] (GRFL) | [Ground Fault ] (GRFL)
HEG | Head Dynamic Gain | 16#3E83 = 16003 | 16#2082/4 | 16#B1/01/04 = 177/01/04 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Head Dynamic Gain] (HEG) | [Est. Pump Flow Conf] (SLPF) [Flow estimation] (SFE) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF) [Est. Pump dP Conf] (SLDP) [dP/Head Correction] (DPHC) [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP) [Stage/Destage Cond.] (SDCM)
HEO | Head Static Offset | 16#3E84 = 16004 | 16#2082/5 | 16#B1/01/05 = 177/01/05 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Head Static Offset] (HEO) | [Est. Pump Flow Conf] (SLPF) [Flow estimation] (SFE) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF) [Est. Pump dP Conf] (SLDP) [dP/Head Correction] (DPHC) [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP) [Stage/Destage Cond.] (SDCM)
HFPB | Response to High Flow error | 16#3DF7 = 15863 | 16#2080/40 | 16#B0/01/40 = 176/01/64 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [HighFlowError Resp] (HFPB) | [High flow monitoring] (HFP)
HFPD | High Flow Delay | 16#3DF6 = 15862 | 16#2080/3F | 16#B0/01/3F = 176/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [HighFlowError Delay] (HFPD) | [High flow monitoring] (HFP) [Settings] (SET)
HFPL | High Flow Max Level | 16#3DF5 = 15861 | 16#2080/3E | 16#B0/01/3E = 176/01/62 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [HighFlow MaxLevel] (HFPL) | [High flow monitoring] (HFP) [Settings] (SET)
HFPM | High Flow detection activation | 16#3DF4 = 15860 | 16#2080/3D | 16#B0/01/3D = 176/01/61 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [HighFlow activation] (HFPM) | [High flow monitoring] (HFP)
HS9 | Drive state | 16#1CA1 = 7329 | 16#202B/1E | 16#85/01/82 = 133/01/130 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS9) | [None] (DP9)
HSA | Drive state | 16#1E28 = 7720 | 16#202F/15 | 16#87/01/79 = 135/01/121 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSA) | [None] (DPA)
HSB | Drive state | 16#1E29 = 7721 | 16#202F/16 | 16#87/01/7A = 135/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSB) | [None] (DPB)
HSC | Drive state | 16#1E2A = 7722 | 16#202F/17 | 16#87/01/7B = 135/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSC) | [None] (DPC)
HSD | Drive state | 16#1E2B = 7723 | 16#202F/18 | 16#87/01/7C = 135/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSD) | [None] (DPD)
HSE | Drive state | 16#1E2C = 7724 | 16#202F/19 | 16#87/01/7D = 135/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSE) | [None] (DPE)
HSF | Drive state | 16#1E2D = 7725 | 16#202F/1A | 16#87/01/7E = 135/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HSF) | [None] (DPF)
IC0 | Input Energy (Wh) | 16#2982 = 10626 | 16#204C/1B | 16#96/01/1B = 150/01/27 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh
IC1 | Input Energy (kWh) | 16#2983 = 10627 | 16#204C/1C | 16#96/01/1C = 150/01/28 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh
IC2 | Input Energy (MWh) | 16#2984 = 10628 | 16#204C/1D | 16#96/01/1D = 150/01/29 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh
IC3 | Input Energy (GWh) | 16#2985 = 10629 | 16#204C/1E | 16#96/01/1E = 150/01/30 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh
IC4 | Input Energy (TWh) | 16#2986 = 10630 | 16#204C/1F | 16#96/01/1F = 150/01/31 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh
IDLS | Energy Saving input assignment | 16#3624 = 13860 | 16#206C/3D | 16#A6/01/3D = 166/01/61 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Energy Saving Assign] (IDLS) | [Stop and Go] (STG)
IE0 | Real Input Energy (Wh) | 16#298C = 10636 | 16#204C/25 | 16#96/01/25 = 150/01/37 |  | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Input Energy] (IE0) | [Elec Ener Input Counter] (ELI)
IE1 | Real Input Energy (kWh) | 16#298D = 10637 | 16#204C/26 | 16#96/01/26 = 150/01/38 |  | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Input Energy] (IE1) | [Elec Ener Input Counter] (ELI)
IE2 | Real Input Energy (MWh) | 16#298E = 10638 | 16#204C/27 | 16#96/01/27 = 150/01/39 |  | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Input Energy] (IE2) | [Elec Ener Input Counter] (ELI)
IE3 | Real Input Energy (GWh) | 16#298F = 10639 | 16#204C/28 | 16#96/01/28 = 150/01/40 |  | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Input Energy] (IE3) | [Elec Ener Input Counter] (ELI)
IE4 | Real Input Energy (TWh) | 16#2990 = 10640 | 16#204C/29 | 16#96/01/29 = 150/01/41 |  | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Input Energy] (IE4) | [Elec Ener Input Counter] (ELI)
IL1I | Logic inputs physical image (bit0 = LI1 ...) | 16#1451 = 5201 | 16#2016/2 | 16#7B/01/02 = 123/01/02 |  | I/O parameters | R | WORD (BitString16) | -
INRC | NCR current scaling | 16#2649 = 9801 | 16#2044/2 | 16#92/01/02 = 146/01/02 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRL | LFA inductance scaling | 16#264C = 9804 | 16#2044/5 | 16#92/01/05 = 146/01/05 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRP | NPR power scaling | 16#264A = 9802 | 16#2044/3 | 16#92/01/03 = 146/01/03 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRR | RSA resistance scaling | 16#264B = 9803 | 16#2044/4 | 16#92/01/04 = 146/01/04 | CINR | Configuration and settings | R | WORD (Enumeration) | -
INRT | Torque scaling | 16#264D = 9805 | 16#2044/6 | 16#92/01/06 = 146/01/06 | CINR | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Torque Scaling] (INRT) | [data] (MTD)
INTI | TRA time scaling | 16#264E = 9806 | 16#2044/7 | 16#92/01/07 = 146/01/07 | CINR | Configuration and settings | R | WORD (Enumeration) | -
IP9 | ETI state word | 16#1C3D = 7229 | 16#202A/1E | 16#85/01/1E = 133/01/30 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IP9) | [None] (DP9)
IPA | ETI state word | 16#1DC4 = 7620 | 16#202E/15 | 16#87/01/15 = 135/01/21 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPA) | [None] (DPA)
IPAD | iPar detected error code | 16#FB18 = 64280 |  |  |  | Communication parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 5 | [iPar Error Code] (IPAD) | [PROFINET DIAG] (PRN)
IPB | ETI state word | 16#1DC5 = 7621 | 16#202E/16 | 16#87/01/16 = 135/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPB) | [None] (DPB)
IPC | ETI state word | 16#1DC6 = 7622 | 16#202E/17 | 16#87/01/17 = 135/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPC) | [None] (DPC)
IPD | ETI state word | 16#1DC7 = 7623 | 16#202E/18 | 16#87/01/18 = 135/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPD) | [None] (DPD)
IPE | ETI state word | 16#1DC8 = 7624 | 16#202E/19 | 16#87/01/19 = 135/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPE) | [None] (DPE)
IPF | ETI state word | 16#1DC9 = 7625 | 16#202E/1A | 16#87/01/1A = 135/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [ETI state word] (IPF) | [None] (DPF)
IPPB | Response to Inlet pressure error | 16#3E2A = 15914 | 16#2081/F | 16#B0/01/73 = 176/01/115 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [InletPresError Resp] (IPPB) | [Inlet pressure monitoring] (IPP)
IPPC | Inlet Pressure maximum compensated pressure | 16#3E29 = 15913 | 16#2081/E | 16#B0/01/72 = 176/01/114 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [InletPres Max Comp] (IPPC) | [Inlet pressure monitoring] (IPP) [Settings] (SET)
IPPH | Inlet Pressure high threshold | 16#3E27 = 15911 | 16#2081/C | 16#B0/01/70 = 176/01/112 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [InletPres High Thd] (IPPH) | [Inlet pressure monitoring] (IPP) [Settings] (SET)
IPPL | Inlet Pressure low threshold | 16#3E28 = 15912 | 16#2081/D | 16#B0/01/71 = 176/01/113 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [InletPres Low Thd] (IPPL) | [Inlet pressure monitoring] (IPP) [Settings] (SET)
IPPM | Inlet Pressure monitoring Mode | 16#3E26 = 15910 | 16#2081/B | 16#B0/01/6F = 176/01/111 | IPPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [NO] NO |  | [InletPres Monitoring] (IPPM) | [Inlet pressure monitoring] (IPP)
IPR | Active Electrical input power estimation (100% = drive power) | 16#0C92 = 3218 | 16#2002/13 | 16#71/01/13 = 113/01/19 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | 0 % ... 65535 %
IPRW | Instantaneous active input power | 16#0CDE = 3294 | 16#2002/5F | 16#71/01/5F = 113/01/95 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Active Input Power] (IPRW) | [Elec Ener Input Counter] (ELI)
JACC | Anti-Jam Forward Acceleration | 16#3E37 = 15927 | 16#2081/1C | 16#B0/01/80 = 176/01/128 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 3000 | [Anti-Jam Fwd Acc] (JACC) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JACR | Anti-Jam Reverse Acceleration | 16#3E38 = 15928 | 16#2081/1D | 16#B0/01/81 = 176/01/129 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 3000 | [Anti-Jam Rv Acc] (JACR) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JAMB | Response to Anti-Jam error | 16#3E42 = 15938 | 16#2081/27 | 16#B0/01/8B = 176/01/139 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [Anti-Jam Error Resp] (JAMB) | [Anti-Jam Monit] (JAM)
JAMN | Maximum allowed consecutive Anti-Jam sequences | 16#3E40 = 15936 | 16#2081/25 | 16#B0/01/89 = 176/01/137 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 2 | 1 ... 99 | [Anti-Jam Max Seq] (JAMN) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JAMT | Time interval to define two Anti-Jam sequences as consecutive | 16#3E41 = 15937 | 16#2081/26 | 16#B0/01/8A = 176/01/138 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 60 s | 0 s ... 3600 s | [Anti-Jam Interval] (JAMT) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JATC | Automatic Anti-Jam trigger | 16#3E31 = 15921 | 16#2081/16 | 16#B0/01/7A = 176/01/122 | JATC | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Anti-Jam Auto Trig] (JATC) | [Anti-Jam Monit] (JAM)
JDEC | Anti-Jam Forward Deceleration | 16#3E35 = 15925 | 16#2081/1A | 16#B0/01/7E = 176/01/126 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 3000 | [Anti-Jam Fwd Dec] (JDEC) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JDER | Anti-Jam Reverse Deceleration | 16#3E36 = 15926 | 16#2081/1B | 16#B0/01/7F = 176/01/127 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 30 | 0 ... 3000 | [Anti-Jam Rv Dec] (JDER) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JETC | External Anti-Jam trigger | 16#3E30 = 15920 | 16#2081/15 | 16#B0/01/79 = 176/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Anti-Jam Ext Trig] (JETC) | [Anti-Jam Monit] (JAM)
JFDS | Anti-Jam Forward Speed | 16#3E3B = 15931 | 16#2081/20 | 16#B0/01/84 = 176/01/132 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Anti-Jam Fwd Speed] (JFDS) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JFDT | Anti-Jam Forward Time | 16#3E39 = 15929 | 16#2081/1E | 16#B0/01/82 = 176/01/130 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 1 s | 0 s ... 300 s | [Anti-Jam Fwd Time] (JFDT) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JNBC | Anti-Jam cycle number | 16#3E3E = 15934 | 16#2081/23 | 16#B0/01/87 = 176/01/135 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 1 ... 100 | [Anti-Jam Cycle Nb] (JNBC) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JP | Select the Jockey Pump | 16#3DD6 = 15830 | 16#2080/1F | 16#B0/01/1F = 176/01/31 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Jockey Selection] (JP) | [Jockey pump] (JKP)
JPRD | Delay to start the Jockey Pump | 16#3DD8 = 15832 | 16#2080/21 | 16#B0/01/21 = 176/01/33 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [Delay to start] (JPRD) | [Jockey pump] (JKP) [Settings] (SET)
JPRP | Pressure threshold to start the Jockey Pump | 16#3DD7 = 15831 | 16#2080/20 | 16#B0/01/20 = 176/01/32 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Minimum Pressure] (JPRP) | [Jockey pump] (JKP) [Settings] (SET)
JPRS | Pump reference speed when VSP is selected as Jockey Pump | 16#3DDA = 15834 | 16#2080/23 | 16#B0/01/23 = 176/01/35 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 599.0 Hz | [Reference Speed] (JPRS) | [Jockey pump] (JKP) [Settings] (SET)
JPSP | Pressure threshold to stop the Jockey Pump | 16#3DD9 = 15833 | 16#2080/22 | 16#B0/01/22 = 176/01/34 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Maximum Pressure] (JPSP) | [Jockey pump] (JKP) [Settings] (SET)
JPWD | Delay to wake up the system when pressure feedback stays low | 16#3DDB = 15835 | 16#2080/24 | 16#B0/01/24 = 176/01/36 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 3600 s | [Wake up Delay] (JPWD) | [Jockey pump] (JKP) [Settings] (SET)
JRVS | Anti-Jam Reverse Speed | 16#3E3C = 15932 | 16#2081/21 | 16#B0/01/85 = 176/01/133 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Anti-Jam Rv Speed] (JRVS) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JRVT | Anti-Jam Reverse Time | 16#3E3A = 15930 | 16#2081/1F | 16#B0/01/83 = 176/01/131 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 1 s | 0 s ... 300 s | [Anti-Jam Rv Time] (JRVT) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JTCD | Delay before triggering Anti-Jam in torque mode | 16#3E34 = 15924 | 16#2081/19 | 16#B0/01/7D = 176/01/125 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [Anti-Jam Start Delay] (JTCD) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JTCL | Anti-Jam torque level | 16#3E33 = 15923 | 16#2081/18 | 16#B0/01/7C = 176/01/124 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 110.0 % | 10.0 % ... 150.0 % | [Anti-Jam Torque] (JTCL) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JTCT | Inactive time before triggering Anti-Jam | 16#3E32 = 15922 | 16#2081/17 | 16#B0/01/7B = 176/01/123 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 h | 24 h | 0 h ... 9999 h | [Anti-Jam Trigger Time] (JTCT) | [Anti-Jam Monit] (JAM) [Settings] (SET)
JZST | Anti-Jam stop time between forward and reverse | 16#3E3D = 15933 | 16#2081/22 | 16#B0/01/86 = 176/01/134 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [Anti-Jam Stop Time] (JZST) | [Anti-Jam Monit] (JAM) [Settings] (SET)
L11D | DI11 Delay | 16#0FAB = 4011 | 16#200A/C | 16#75/01/0C = 117/01/12 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI11 Delay] (L11D) | [DI11 Configuration] (DI11)
L12D | DI12 Delay | 16#0FAC = 4012 | 16#200A/D | 16#75/01/0D = 117/01/13 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI12 Delay] (L12D) | [DI12 Configuration] (DI12)
L13D | DI13 Delay | 16#0FAD = 4013 | 16#200A/E | 16#75/01/0E = 117/01/14 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI13 Delay] (L13D) | [DI13 Configuration] (DI13)
L14D | DI14 Delay | 16#0FAE = 4014 | 16#200A/F | 16#75/01/0F = 117/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI14 Delay] (L14D) | [DI14 Configuration] (DI14)
L15D | DI15 delay | 16#0FAF = 4015 | 16#200A/10 | 16#75/01/10 = 117/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI15 Delay] (L15D) | [DI15 Configuration] (DI15)
L16D | DI16 delay | 16#0FB0 = 4016 | 16#200A/11 | 16#75/01/11 = 117/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI16 Delay] (L16D) | [DI16 Configuration] (DI16)
LALR | Last Warning | 16#325A = 12890 | 16#2062/5B | 16#A1/01/5B = 161/01/91 | ALR | Actual values parameters | R | WORD (Enumeration) | - |  |  | [Last Warning] (LALR) | [Diag. data] (DDT)
LCAC | LifeCycle Warning Configuration | 16#3598 = 13720 | 16#206B/15 | 16#A5/01/79 = 165/01/121 | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [LifeCycle Warning] (LCAC) | [Drive warranty mgnt] (DWMA)
LCAD | Life Cycle Date | 16#3599 = 13721 | 16#206B/16 | 16#A5/01/7A = 165/01/122 |  | Actual values parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Warranty expired] (LCAD) | [Drive warranty mgnt] (DWMA)
LCP9 | Motor current | 16#1C51 = 7249 | 16#202A/32 | 16#85/01/32 = 133/01/50 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCP9) | [None] (DP9)
LCPA | Motor current | 16#1DD8 = 7640 | 16#202E/29 | 16#87/01/29 = 135/01/41 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPA) | [None] (DPA)
LCPB | Motor current | 16#1DD9 = 7641 | 16#202E/2A | 16#87/01/2A = 135/01/42 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPB) | [None] (DPB)
LCPC | Motor current | 16#1DDA = 7642 | 16#202E/2B | 16#87/01/2B = 135/01/43 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPC) | [None] (DPC)
LCPD | Motor current | 16#1DDB = 7643 | 16#202E/2C | 16#87/01/2C = 135/01/44 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPD) | [None] (DPD)
LCPE | Motor current | 16#1DDC = 7644 | 16#202E/2D | 16#87/01/2D = 135/01/45 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPE) | [None] (DPE)
LCPF | Motor current | 16#1DDD = 7645 | 16#202E/2E | 16#87/01/2E = 135/01/46 |  | History parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor current] (LCPF) | [None] (DPF)
LDD1 | Log Distribution Data 1 | 16#4010 = 16400 | 16#2086/1 | 16#B3/01/01 = 179/01/01 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 1] (LDD1) | [Log dstrb prm select] (LDP)
LDD2 | Log Distribution Data 2 | 16#4012 = 16402 | 16#2086/3 | 16#B3/01/03 = 179/01/03 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib.Data 2] (LDD2) | [Log dstrb prm select] (LDP)
LDD3 | Log Distribution Data 3 | 16#4014 = 16404 | 16#2086/5 | 16#B3/01/05 = 179/01/05 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 3] (LDD3) | [Log dstrb prm select] (LDP)
LDD4 | Log Distribution Data 4 | 16#4016 = 16406 | 16#2086/7 | 16#B3/01/07 = 179/01/07 | LDD | Configuration and settings | R/W | WORD (Enumeration) | - | [Distribution logging disable] NO |  | [Log Distrib. Data 4] (LDD4) | [Log dstrb prm select] (LDP)
LDEN | Logging Distribution State | 16#4019 = 16409 | 16#2086/A | 16#B3/01/0A = 179/01/10 | LDEN | Configuration and settings | R/W | WORD (Enumeration) | - | [Stop] STOP |  | [Log Distrib State] (LDEN) | [Distributed logging] (DLO)
LDM1 | Distribution data max value 1 | 16#4011 = 16401 | 16#2086/2 | 16#B3/01/02 = 179/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 1] (LDM1) | [Distributed logging] (DLO)
LDM2 | Distribution data max value 2 | 16#4013 = 16403 | 16#2086/4 | 16#B3/01/04 = 179/01/04 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 2] (LDM2) | [Distributed logging] (DLO)
LDM3 | Distribution data max value 3 | 16#4015 = 16405 | 16#2086/6 | 16#B3/01/06 = 179/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 3] (LDM3) | [Distributed logging] (DLO)
LDM4 | Distribution data max value 4 | 16#4017 = 16407 | 16#2086/8 | 16#B3/01/08 = 179/01/08 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 10 ... 65535 | [Dist Max Val 4] (LDM4) | [Distributed logging] (DLO)
LDST | Logging Distribution Sample Time | 16#4018 = 16408 | 16#2086/9 | 16#B3/01/09 = 179/01/09 | LDST | Configuration and settings | R/W | WORD (Enumeration) | - | [1 second] 1S |  | [Log Distrib Spl Time] (LDST) | [Distributed logging] (DLO)
LFL1 | Response to 4-20mA loss on AI1 | 16#1B69 = 7017 | 16#2028/12 | 16#84/01/12 = 132/01/18 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI1 4-20mA loss] (LFL1) | [4-20 mA loss] (LFL)
LFL2 | Response to 4-20mA loss on AI2 | 16#1B5B = 7003 | 16#2028/4 | 16#84/01/04 = 132/01/04 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI2 4-20mA loss] (LFL2) | [4-20 mA loss] (LFL)
LFL4 | Response to 4-20mA loss on AI4 | 16#1B66 = 7014 | 16#2028/F | 16#84/01/0F = 132/01/15 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI4 4-20mA loss] (LFL4) | [4-20 mA loss] (LFL)
LFL5 | Response to 4-20mA loss on AI5 | 16#1B6B = 7019 | 16#2028/14 | 16#84/01/14 = 132/01/20 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ignore] NO |  | [AI5 4-20mA loss] (LFL5) | [4-20 mA loss] (LFL)
LOC | Ovld Threshold Detection | 16#3859 = 14425 | 16#2072/1A | 16#A9/01/1A = 169/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 70 % ... 150 % | [Ovld Detection Thr.] (LOC) | [Settings] (SET) [Process overload] (OLD)
MD0 | Year, month and day of actual fault | 16#1C84 = 7300 | 16#202B/1 | 16#85/01/65 = 133/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD1 | Year, month and day of fault record x (1 is last) | 16#1C85 = 7301 | 16#202B/2 | 16#85/01/66 = 133/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD2 | Year, month and day of fault record x (1 is last) | 16#1C86 = 7302 | 16#202B/3 | 16#85/01/67 = 133/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD3 | Year, month and day of fault record x (1 is last) | 16#1C87 = 7303 | 16#202B/4 | 16#85/01/68 = 133/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD4 | Year, month and day of fault record x (1 is last) | 16#1C88 = 7304 | 16#202B/5 | 16#85/01/69 = 133/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD5 | Year, month and day of fault record x (1 is last) | 16#1C89 = 7305 | 16#202B/6 | 16#85/01/6A = 133/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD6 | Year, month and day of fault record x (1 is last) | 16#1C8A = 7306 | 16#202B/7 | 16#85/01/6B = 133/01/107 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD7 | Year, month and day of fault record x (1 is last) | 16#1C8B = 7307 | 16#202B/8 | 16#85/01/6C = 133/01/108 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD8 | Year, month and day of fault record x (1 is last) | 16#1C8C = 7308 | 16#202B/9 | 16#85/01/6D = 133/01/109 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MD9 | Year, month and day of fault record x (1 is last) | 16#1C8D = 7309 | 16#202B/A | 16#85/01/6E = 133/01/110 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDA | Year, month and day of fault record x (1 is last) | 16#1E14 = 7700 | 16#202F/1 | 16#87/01/65 = 135/01/101 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDB | Year, month and day of fault record x (1 is last) | 16#1E15 = 7701 | 16#202F/2 | 16#87/01/66 = 135/01/102 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDC | Year, month and day of fault record x (1 is last) | 16#1E16 = 7702 | 16#202F/3 | 16#87/01/67 = 135/01/103 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDD | Year, month and day of fault record x (1 is last) | 16#1E17 = 7703 | 16#202F/4 | 16#87/01/68 = 135/01/104 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDE | Year, month and day of fault record x (1 is last) | 16#1E18 = 7704 | 16#202F/5 | 16#87/01/69 = 135/01/105 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
MDF | Year, month and day of fault record x (1 is last) | 16#1E19 = 7705 | 16#202F/6 | 16#87/01/6A = 135/01/106 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
ME0 | Motor energy consumption (Wh) | 16#2969 = 10601 | 16#204C/2 | 16#96/01/02 = 150/01/02 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Motor Consumption] (ME0) | [Mechanical Energy] (MEC)
ME1 | Motor energy consumption (kWh) | 16#296A = 10602 | 16#204C/3 | 16#96/01/03 = 150/01/03 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Motor Consumption] (ME1) | [Mechanical Energy] (MEC)
ME2 | Motor energy consumption (MWh) | 16#296B = 10603 | 16#204C/4 | 16#96/01/04 = 150/01/04 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Motor Consumption] (ME2) | [Mechanical Energy] (MEC)
ME3 | Motor energy consumption (GWh) | 16#296C = 10604 | 16#204C/5 | 16#96/01/05 = 150/01/05 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Motor Consumption] (ME3) | [Mechanical Energy] (MEC)
ME4 | Motor energy consumption (TWh) | 16#296D = 10605 | 16#204C/6 | 16#96/01/06 = 150/01/06 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Motor Consumption] (ME4) | [Mechanical Energy] (MEC)
MOEP | Peak Output Power | 16#2991 = 10641 | 16#204C/2A | 16#96/01/2A = 150/01/42 |  | Status parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Peak Output Power ] (MOEP) | [Elec Ener Output Counter] (ELO)
NFHP | No Flow High Power | 16#3E5B = 15963 | 16#2081/40 | 16#B0/01/A4 = 176/01/164 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [High Power] (NFHP) | [Dry run Monit] (DYR) [Pump low flow Monit] (PLF)
NFHS | No Flow High Speed | 16#3E5A = 15962 | 16#2081/3F | 16#B0/01/A3 = 176/01/163 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [High Speed] (NFHS) | [Dry run Monit] (DYR) [Pump low flow Monit] (PLF)
NFLP | No Flow Low Power | 16#3E59 = 15961 | 16#2081/3E | 16#B0/01/A2 = 176/01/162 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Low Power] (NFLP) | [Dry run Monit] (DYR) [Pump low flow Monit] (PLF)
NFLS | No Flow Low Speed | 16#3E58 = 15960 | 16#2081/3D | 16#B0/01/A1 = 176/01/161 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Low Speed] (NFLS) | [Dry run Monit] (DYR) [Pump low flow Monit] (PLF)
NSM | Number of motor starts | 16#0CBC = 3260 | 16#2002/3D | 16#71/01/3D = 113/01/61 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Nb Of Starts] (NSM) | [Diag. data] (DDT) [Counter Management] (ELT) [Variable Speed Pump] (MPP)
OC0 | Electrical energy consumed by the motor (Wh) | 16#296E = 10606 | 16#204C/7 | 16#96/01/07 = 150/01/07 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh | [Elc Energy Cons] (OC0) | [kWh Counters] (KWC)
OC1 | Electrical energy consumed by the motor (KWh) | 16#296F = 10607 | 16#204C/8 | 16#96/01/08 = 150/01/08 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh | [Elc Energy Cons] (OC1) | [kWh Counters] (KWC)
OC2 | Electrical energy consumed by the motor (MWh) | 16#2970 = 10608 | 16#204C/9 | 16#96/01/09 = 150/01/09 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh | [Elc Energy Cons] (OC2) | [kWh Counters] (KWC)
OC3 | Electrical energy consumed by the motor (GWh) | 16#2971 = 10609 | 16#204C/A | 16#96/01/0A = 150/01/10 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh | [Elc Energy Cons] (OC3) | [kWh Counters] (KWC)
OC4 | Electrical energy consumed by the motor (TWh) | 16#2972 = 10610 | 16#204C/B | 16#96/01/0B = 150/01/11 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh | [Elc Energy Cons] (OC4) | [kWh Counters] (KWC)
OCA7 | Scan output 7 address | 16#3C43 = 15427 | 16#207C/1C | 16#AE/01/1C = 174/01/28 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA8 | Scan output 8 address | 16#3C44 = 15428 | 16#207C/1D | 16#AE/01/1D = 174/01/29 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCA9 | Scan output 9 address | 16#3C45 = 15429 | 16#207C/1E | 16#AE/01/1E = 174/01/30 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAA | Scan output 10 address | 16#3C46 = 15430 | 16#207C/1F | 16#AE/01/1F = 174/01/31 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAB | Scan output 11 address | 16#3C47 = 15431 | 16#207C/20 | 16#AE/01/20 = 174/01/32 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAC | Scan output 12 address | 16#3C48 = 15432 | 16#207C/21 | 16#AE/01/21 = 174/01/33 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAD | Scan output 13 address | 16#3C49 = 15433 | 16#207C/22 | 16#AE/01/22 = 174/01/34 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAE | Scan output 14 address | 16#3C4A = 15434 | 16#207C/23 | 16#AE/01/23 = 174/01/35 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAF | Scan output 15 address | 16#3C4B = 15435 | 16#207C/24 | 16#AE/01/24 = 174/01/36 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCAG | Scan output 16 address | 16#3C4C = 15436 | 16#207C/25 | 16#AE/01/25 = 174/01/37 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OCT | Electrical energy consumed TODAY by the motor (KWh) | 16#297E = 10622 | 16#204C/17 | 16#96/01/17 = 150/01/23 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Today] (OCT) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO)
OCY | Electrical energy consumed YESTERDAY by the motor (KWh) | 16#2980 = 10624 | 16#204C/19 | 16#96/01/19 = 150/01/25 |  | Actual values parameters | R | UINT (Unsigned32) | 1 kWh |  | 0 kWh ... 4294967295 kWh | [Elc Egy Yesterday] (OCY) | [kWh Counters] (KWC) [Elec Ener Output Counter] (ELO)
OE0 | Real energy consumption (Wh) | 16#2978 = 10616 | 16#204C/11 | 16#96/01/11 = 150/01/17 |  | Actual values parameters | R/WS | INT (Signed16) | 1 Wh |  | -999 Wh ... 999 Wh | [Real Consumption] (OE0) | [Elec Ener Output Counter] (ELO)
OE1 | Real energy consumption (kWh) | 16#2979 = 10617 | 16#204C/12 | 16#96/01/12 = 150/01/18 |  | Actual values parameters | R/WS | INT (Signed16) | 1 kWh |  | -999 kWh ... 999 kWh | [Real Consumption] (OE1) | [Elec Ener Output Counter] (ELO)
OE2 | Real energy consumption (MWh) | 16#297A = 10618 | 16#204C/13 | 16#96/01/13 = 150/01/19 |  | Actual values parameters | R/WS | INT (Signed16) | 1 MWh |  | -999 MWh ... 999 MWh | [Real Consumption] (OE2) | [Elec Ener Output Counter] (ELO)
OE3 | Real energy consumption (GWh) | 16#297B = 10619 | 16#204C/14 | 16#96/01/14 = 150/01/20 |  | Actual values parameters | R/WS | INT (Signed16) | 1 GWh |  | -999 GWh ... 999 GWh | [Real Consumption] (OE3) | [Elec Ener Output Counter] (ELO)
OE4 | Real energy consumption (TWh) | 16#297C = 10620 | 16#204C/15 | 16#96/01/15 = 150/01/21 |  | Actual values parameters | R/WS | INT (Signed16) | 1 TWh |  | -999 TWh ... 999 TWh | [Real Consumption] (OE4) | [Elec Ener Output Counter] (ELO)
OFI | Sinus filter activation | 16#0C25 = 3109 | 16#2001/A | 16#70/01/6E = 112/01/110 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sinus Filter Activation] (OFI) | [Motor monitoring] (MOP)
OMA7 | Scan input 7 address | 16#3C2F = 15407 | 16#207C/8 | 16#AE/01/08 = 174/01/08 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA8 | Scan input 8 address | 16#3C30 = 15408 | 16#207C/9 | 16#AE/01/09 = 174/01/09 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMA9 | Scan input 9 address | 16#3C31 = 15409 | 16#207C/A | 16#AE/01/0A = 174/01/10 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAA | Scan input 10 address | 16#3C32 = 15410 | 16#207C/B | 16#AE/01/0B = 174/01/11 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAB | Scan input 11 address | 16#3C33 = 15411 | 16#207C/C | 16#AE/01/0C = 174/01/12 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAC | Scan input 12 address | 16#3C34 = 15412 | 16#207C/D | 16#AE/01/0D = 174/01/13 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAD | Scan input 13 address | 16#3C35 = 15413 | 16#207C/E | 16#AE/01/0E = 174/01/14 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAE | Scan input 14 address | 16#3C36 = 15414 | 16#207C/F | 16#AE/01/0F = 174/01/15 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAF | Scan input 15 address | 16#3C37 = 15415 | 16#207C/10 | 16#AE/01/10 = 174/01/16 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OMAG | Scan input 16 address | 16#3C38 = 15416 | 16#207C/11 | 16#AE/01/11 = 174/01/17 |  | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535
OP0 | Electrical energy produced by the motor (Wh) | 16#2973 = 10611 | 16#204C/C | 16#96/01/0C = 150/01/12 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 Wh |  | 0 Wh ... 999 Wh
OP1 | Electrical energy produced by the motor (KWh) | 16#2974 = 10612 | 16#204C/D | 16#96/01/0D = 150/01/13 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 kWh |  | 0 kWh ... 999 kWh
OP2 | Electrical energy produced by the motor (MWh) | 16#2975 = 10613 | 16#204C/E | 16#96/01/0E = 150/01/14 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 MWh |  | 0 MWh ... 999 MWh
OP3 | Electrical energy produced by the motor (GWh) | 16#2976 = 10614 | 16#204C/F | 16#96/01/0F = 150/01/15 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 GWh |  | 0 GWh ... 999 GWh
OP4 | Electrical energy produced by the motor (TWh) | 16#2977 = 10615 | 16#204C/10 | 16#96/01/10 = 150/01/16 |  | Actual values parameters | R/WS | UINT (Unsigned16) | 1 TWh |  | 0 TWh ... 999 TWh
OPPB | Response to Outlet Pressure error | 16#3DEF = 15855 | 16#2080/38 | 16#B0/01/38 = 176/01/56 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [OutPresError Resp] (OPPB) | [Outlet pressure monitoring] (OPP)
OPPD | Outlet Pressure error delay | 16#3DEE = 15854 | 16#2080/37 | 16#B0/01/37 = 176/01/55 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 3600 s | [OutPresError Delay] (OPPD) | [Outlet pressure monitoring] (OPP) [Settings] (SET)
OPPH | Outlet Pressure maximum level | 16#3DED = 15853 | 16#2080/36 | 16#B0/01/36 = 176/01/54 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [OutPres Max Level] (OPPH) | [Outlet pressure monitoring] (OPP) [Settings] (SET)
OPPL | Outlet Pressure minimum level | 16#3DEC = 15852 | 16#2080/35 | 16#B0/01/35 = 176/01/53 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [OutPres Min Level] (OPPL) | [Outlet pressure monitoring] (OPP) [Settings] (SET)
OPPM | Outlet Pressure monitoring mode | 16#3DEA = 15850 | 16#2080/33 | 16#B0/01/33 = 176/01/51 | OPPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [OutPres Monitoring] (OPPM) | [Outlet pressure monitoring] (OPP)
OPPW | Outlet Pressure digital input assignment | 16#3DEB = 15851 | 16#2080/34 | 16#B0/01/34 = 176/01/52 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [OutPres DI Assign] (OPPW) | [Outlet pressure monitoring] (OPP)
OPRW | Motor mechanical power estimation | 16#0CDC = 3292 | 16#2002/5D | 16#71/01/5D = 113/01/93 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Power Estim Value] (OPRW) | [Mechanical Energy] (MEC) [Dry run Monit] (DYR) [Pump low flow Monit] (PLF)
OTP9 | Motor torque | 16#1CAB = 7339 | 16#202B/28 | 16#85/01/8C = 133/01/140 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTP9) | [None] (DP9)
OTPA | Motor torque | 16#1E32 = 7730 | 16#202F/1F | 16#87/01/83 = 135/01/131 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPA) | [None] (DPA)
OTPB | Motor torque | 16#1E33 = 7731 | 16#202F/20 | 16#87/01/84 = 135/01/132 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPB) | [None] (DPB)
OTPC | Motor torque | 16#1E34 = 7732 | 16#202F/21 | 16#87/01/85 = 135/01/133 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPC) | [None] (DPC)
OTPD | Motor torque | 16#1E35 = 7733 | 16#202F/22 | 16#87/01/86 = 135/01/134 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPD) | [None] (DPD)
OTPE | Motor torque | 16#1E36 = 7734 | 16#202F/23 | 16#87/01/87 = 135/01/135 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPE) | [None] (DPE)
OTPF | Motor torque | 16#1E37 = 7735 | 16#202F/24 | 16#87/01/88 = 135/01/136 |  | History parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Motor Torque ] (OTPF) | [None] (DPF)
PCA | Pump Curve Activation | 16#3D9B = 15771 | 16#207F/48 | 16#AF/01/AC = 175/01/172 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Pump Curve Activate] (PCA) | [Pump characteristics] (PCR)
PCAH | Over-consumption threshold | 16#2A62 = 10850 | 16#204E/33 | 16#97/01/33 = 151/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 200.0 % | [Over-Consumption Thd] (PCAH) | [Elec Ener Output Counter] (ELO)
PCAL | Under-consumption threshold | 16#2A63 = 10851 | 16#204E/34 | 16#97/01/34 = 151/01/52 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Under-Consumption Thd] (PCAL) | [Elec Ener Output Counter] (ELO)
PCAT | Over/Under-consumption time delay | 16#2A64 = 10852 | 16#204E/35 | 16#97/01/35 = 151/01/53 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 min | 1 min | 0 min ... 60 min | [Over/Under-Cons Delay] (PCAT) | [Elec Ener Output Counter] (ELO)
PCBH | BEP Head | 16#3D97 = 15767 | 16#207F/44 | 16#AF/01/A8 = 175/01/168 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head BEP] (PCBH) | [Pump characteristics] (PCR)
PCBP | BEP Power | 16#3D99 = 15769 | 16#207F/46 | 16#AF/01/AA = 175/01/170 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power BEP] (PCBP) | [Pump characteristics] (PCR)
PCBQ | Flow at BEP | 16#3D98 = 15768 | 16#207F/45 | 16#AF/01/A9 = 175/01/169 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow at BEP] (PCBQ) | [Pump characteristics] (PCR)
PCH1 | Head entered at y (for HQ curve) | 16#3D8D = 15757 | 16#207F/3A | 16#AF/01/9E = 175/01/158 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 1] (PCH1) | [Pump characteristics] (PCR)
PCH2 | Head entered at y (for HQ curve) | 16#3D8E = 15758 | 16#207F/3B | 16#AF/01/9F = 175/01/159 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 2] (PCH2) | [Pump characteristics] (PCR)
PCH3 | Head entered at y (for HQ curve) | 16#3D8F = 15759 | 16#207F/3C | 16#AF/01/A0 = 175/01/160 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 3] (PCH3) | [Pump characteristics] (PCR)
PCH4 | Head entered at y (for HQ curve) | 16#3D90 = 15760 | 16#207F/3D | 16#AF/01/A1 = 175/01/161 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 4] (PCH4) | [Pump characteristics] (PCR)
PCH5 | Head entered at y (for HQ curve) | 16#3D91 = 15761 | 16#207F/3E | 16#AF/01/A2 = 175/01/162 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Head 5] (PCH5) | [Pump characteristics] (PCR)
PCM | Select which curve data are managed and will be entered on | 16#3D9A = 15770 | 16#207F/47 | 16#AF/01/AB = 175/01/171 | PCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Disable pump characteristics] NO |  | [Mode] (PCM) | [Pump characteristics] (PCR)
PCP1 | Mechanical power entered at point y | 16#3D92 = 15762 | 16#207F/3F | 16#AF/01/A3 = 175/01/163 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 1] (PCP1) | [Pump characteristics] (PCR)
PCP2 | Mechanical power entered at point y | 16#3D93 = 15763 | 16#207F/40 | 16#AF/01/A4 = 175/01/164 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 2] (PCP2) | [Pump characteristics] (PCR)
PCP3 | Mechanical power entered at point y | 16#3D94 = 15764 | 16#207F/41 | 16#AF/01/A5 = 175/01/165 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 3] (PCP3) | [Pump characteristics] (PCR)
PCP4 | Mechanical power entered at point y | 16#3D95 = 15765 | 16#207F/42 | 16#AF/01/A6 = 175/01/166 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 4] (PCP4) | [Pump characteristics] (PCR)
PCP5 | Mechanical power entered at point y | 16#3D96 = 15766 | 16#207F/43 | 16#AF/01/A7 = 175/01/167 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Power 5] (PCP5) | [Pump characteristics] (PCR)
PCPB | Response to Pump cycle error | 16#3E1F = 15903 | 16#2081/4 | 16#B0/01/68 = 176/01/104 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [PumpCycleError Resp] (PCPB) | [Pumpcycle monitoring] (CSP)
PCPM | Pump cycle monitoring mode | 16#3E1C = 15900 | 16#2081/1 | 16#B0/01/65 = 176/01/101 | PCPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pump Cycle monitoring disabled] NO |  | [PumpCycle Monitor] (PCPM) | [Pumpcycle monitoring] (CSP)
PCPN | Pump cycle maximum allowed starts | 16#3E1D = 15901 | 16#2081/2 | 16#B0/01/66 = 176/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 6 | 1 ... 99 | [PumpCycle MaxStarts] (PCPN) | [Pumpcycle monitoring] (CSP) [Settings] (SET)
PCPT | Pump cycle timeframe | 16#3E1E = 15902 | 16#2081/3 | 16#B0/01/67 = 176/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 60 min | 0 min ... 3600 min | [PumpCycle timeframe] (PCPT) | [Pumpcycle monitoring] (CSP) [Settings] (SET)
PCQ1 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D88 = 15752 | 16#207F/35 | 16#AF/01/99 = 175/01/153 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 1] (PCQ1) | [Pump characteristics] (PCR)
PCQ2 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D89 = 15753 | 16#207F/36 | 16#AF/01/9A = 175/01/154 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 2] (PCQ2) | [Pump characteristics] (PCR)
PCQ3 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8A = 15754 | 16#207F/37 | 16#AF/01/9B = 175/01/155 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 3] (PCQ3) | [Pump characteristics] (PCR)
PCQ4 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8B = 15755 | 16#207F/38 | 16#AF/01/9C = 175/01/156 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 4] (PCQ4) | [Pump characteristics] (PCR)
PCQ5 | Flow rate entered at point x (for HQ and PQ curves) | 16#3D8C = 15756 | 16#207F/39 | 16#AF/01/9D = 175/01/157 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Flow 5] (PCQ5) | [Pump characteristics] (PCR)
PCS | Pump Characteristics Status | 16#3D86 = 15750 | 16#207F/33 | 16#AF/01/97 = 175/01/151 | PCS | Status parameters | R | WORD (Enumeration) | - |  |  | [Status] (PCS) | [Pump characteristics] (PCR)
PCSP | Pump speed for which curves are entered | 16#3D87 = 15751 | 16#207F/34 | 16#AF/01/98 = 175/01/152 |  | Configuration and settings | R/WS | INT (Signed16) | 1 rpm | 0 rpm | 0 rpm ... 32767 rpm | [Pump Speed] (PCSP) | [Pump characteristics] (PCR)
PEG | Power Dynamic Gain | 16#3E85 = 16005 | 16#2082/6 | 16#B1/01/06 = 177/01/06 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Power Dynamic Gain] (PEG) | [Est. Pump Flow Conf] (SLPF) [Flow estimation] (SFE) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF)
PEO | Power Static Offset | 16#3E86 = 16006 | 16#2082/7 | 16#B1/01/07 = 177/01/07 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 0.0 % | -100.0 % ... 100.0 % | [Power Static Offset] (PEO) | [Est. Pump Flow Conf] (SLPF) [Flow estimation] (SFE) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF)
PEV1 | TPDO1 Event mask | 16#17B6 = 6070 | 16#201E/47 | 16#7F/01/47 = 127/01/71 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV2 | TPDO2 Event mask | 16#17B7 = 6071 | 16#201E/48 | 16#7F/01/48 = 127/01/72 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV3 | TPDO3 Event mask | 16#17B8 = 6072 | 16#201E/49 | 16#7F/01/49 = 127/01/73 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PEV4 | TPDO4 Event mask | 16#17B9 = 6073 | 16#201E/4A | 16#7F/01/4A = 127/01/74 |  | Communication parameters | R/WS | WORD (BitString16) | - | 15
PFC5 | DI5 Frequency measured | 16#3412 = 13330 | 16#2067/1F | 16#A3/01/83 = 163/01/131 |  | Actual values parameters | R | UINT (Unsigned32) | 0.01 Hz |  | 0.00 Hz ... 42949672.95 Hz
PFC6 | DI6 Frequency measured | 16#3426 = 13350 | 16#2067/33 | 16#A3/01/97 = 163/01/151 |  | Actual values parameters | R | UINT (Unsigned32) | 0.01 Hz |  | 0.00 Hz ... 42949672.95 Hz
PFEC | Pipe Fill Activation Source | 16#3DB9 = 15801 | 16#2080/2 | 16#B0/01/02 = 176/01/02 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Activation Source] (PFEC) | [Pipe fill] (PFI)
PFHP | Pipe Fill Pressure Level | 16#3DBC = 15804 | 16#2080/5 | 16#B0/01/05 = 176/01/05 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Pipe Fill Pressure] (PFHP) | [Pipe fill] (PFI) [Settings] (SET)
PFHS | Pipe Fill SPeed | 16#3DBB = 15803 | 16#2080/4 | 16#B0/01/04 = 176/01/04 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 25.0 Hz | 0.0 Hz ... 599.0 Hz | [Pipe Fill Speed] (PFHS) | [Pipe fill] (PFI) [Settings] (SET)
PFHT | Pipe Fill TiMe | 16#3DBA = 15802 | 16#2080/3 | 16#B0/01/03 = 176/01/03 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 10 s | 0 s ... 32767 s | [Pipe Fill Time] (PFHT) | [Pipe fill] (PFI) [Settings] (SET)
PFI5 | DI5 Frequency filter | 16#340C = 13324 | 16#2067/19 | 16#A3/01/7D = 163/01/125 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI5 Frequency Filter] (PFI5) | [DI5 Frequency measured] (PFC5) [DI5 Pulse Config] (PAI5)
PFI6 | DI6 Frequency filter | 16#3420 = 13344 | 16#2067/2D | 16#A3/01/91 = 163/01/145 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 1000 ms | [DI6 Frequency Filter] (PFI6) | [DI6 Frequency measured] (PFC6) [DI6 Pulse Config] (PAI6)
PFL | U/F Profile | 16#2598 = 9624 | 16#2042/19 | 16#91/01/19 = 145/01/25 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 30 % | 0 % ... 100 % | [U/F Profile] (PFL) | [Motor control] (DRC)
PFM | Pipe Fill Activation Mode | 16#3DB8 = 15800 | 16#2080/1 | 16#B0/01/01 = 176/01/01 | PFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Activation Mode] (PFM) | [Pipe fill] (PFI)
PFMB | PID Feedback error response | 16#2E9D = 11933 | 16#2059/22 | 16#9C/01/86 = 156/01/134 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [PID Fdbk Error Resp] (PFMB) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM)
PFMD | PID Feedback error delay | 16#2E9C = 11932 | 16#2059/21 | 16#9C/01/85 = 156/01/133 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PID Fdbk Error Delay] (PFMD) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Settings] (SET)
PFMM | PID Feedback monitoring activation | 16#2E9A = 11930 | 16#2059/1F | 16#9C/01/83 = 156/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PID Fdbk Monitoring] (PFMM) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM)
PFMR | PID Feedback Range | 16#2E9B = 11931 | 16#2059/20 | 16#9C/01/84 = 156/01/132 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 3 % | 0 % ... 100 % | [PID Fdbk Range] (PFMR) | [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Feedback Monitoring] (FKM) [Settings] (SET)
PHR | Output phase rotation | 16#3459 = 13401 | 16#2068/2 | 16#A4/01/02 = 164/01/02 | PHR | Configuration and settings | R/WS | WORD (Enumeration) | - | [A - B - C phase rotation] ABC |  | [Output Ph Rotation] (PHR) | [Motor control] (DRC)
PI5J | DI5 Min process | 16#3414 = 13332 | 16#2067/21 | 16#A3/01/85 = 163/01/133 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI5 Min Process] (PI5J) | [PI5 Sensor Config] (IF8) [PI5 Sensor Config] (PF8) [PI5 Sensor Config] (BIP5) [PI5 Sensor Config] (LIP5) [PI5 Sensor Config] (SIF8) [PI5 Sensor Config] (FIF8) [PI5 Sensor Config] (LF8) [PI5 Sensor Config] (NPF8) [PI5 Sensor Config] (HIF8)
PI5K | DI5 Max process | 16#3416 = 13334 | 16#2067/23 | 16#A3/01/87 = 163/01/135 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI5 Max Process] (PI5K) | [PI5 Sensor Config] (IF8) [PI5 Sensor Config] (PF8) [PI5 Sensor Config] (BIP5) [PI5 Sensor Config] (LIP5) [PI5 Sensor Config] (SIF8) [PI5 Sensor Config] (FIF8) [PI5 Sensor Config] (LF8) [PI5 Sensor Config] (NPF8) [PI5 Sensor Config] (HIF8)
PI6J | DI6 Min process | 16#3428 = 13352 | 16#2067/35 | 16#A3/01/99 = 163/01/153 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI6 Min Process] (PI6J) | [PI6 Sensor Config] (IF9) [PI6 Sensor Config] (PF9) [PI6 Sensor Config] (BIP6) [PI6 Sensor Config] (LIP6) [PI6 Sensor Config] (SIF9) [PI6 Sensor Config] (FIF9) [PI6 Sensor Config] (LF9) [PI6 Sensor Config] (NPF9) [PI6 Sensor Config] (HIF9)
PI6K | DI6 Max process | 16#342A = 13354 | 16#2067/37 | 16#A3/01/9B = 163/01/155 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [DI6 Max Process] (PI6K) | [PI6 Sensor Config] (IF9) [PI6 Sensor Config] (PF9) [PI6 Sensor Config] (BIP6) [PI6 Sensor Config] (LIP6) [PI6 Sensor Config] (SIF9) [PI6 Sensor Config] (FIF9) [PI6 Sensor Config] (LF9) [PI6 Sensor Config] (NPF9) [PI6 Sensor Config] (HIF9)
PIH5 | PulseInput DI5 High Frequency | 16#340A = 13322 | 16#2067/17 | 16#A3/01/7B = 163/01/123 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI5 PulseInput High Freq] (PIH5) | [DI5 Frequency measured] (PFC5) [DI5 Pulse Config] (PAI5) [PI5 Sensor Config] (IF8) [PI5 Sensor Config] (PF8) [PI5 Sensor Config] (BIP5) [PI5 Sensor Config] (LIP5) [PI5 Sensor Config] (SIF8) [PI5 Sensor Config] (FIF8) [PI5 Sensor Config] (LF8) [PI5 Sensor Config] (NPF8) [PI5 Sensor Config] (HIF8)
PIH6 | DI6 PulseInput High Frequency | 16#341E = 13342 | 16#2067/2B | 16#A3/01/8F = 163/01/143 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 kHz | 30.00 kHz | 0.00 kHz ... 30.00 kHz | [DI6 PulseInput High Freq] (PIH6) | [DI6 Frequency measured] (PFC6) [DI6 Pulse Config] (PAI6) [PI6 Sensor Config] (IF9) [PI6 Sensor Config] (PF9) [PI6 Sensor Config] (BIP6) [PI6 Sensor Config] (LIP6) [PI6 Sensor Config] (SIF9) [PI6 Sensor Config] (FIF9) [PI6 Sensor Config] (LF9) [PI6 Sensor Config] (NPF9) [PI6 Sensor Config] (HIF9)
PIL5 | DI5 PulseInput Low Frequency | 16#3408 = 13320 | 16#2067/15 | 16#A3/01/79 = 163/01/121 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.01 Hz | 0.00 Hz | 0.00 Hz ... 30000.00 Hz | [DI5 PulseInput Low Freq] (PIL5) | [DI5 Frequency measured] (PFC5) [DI5 Pulse Config] (PAI5) [PI5 Sensor Config] (IF8) [PI5 Sensor Config] (PF8) [PI5 Sensor Config] (BIP5) [PI5 Sensor Config] (LIP5) [PI5 Sensor Config] (SIF8) [PI5 Sensor Config] (FIF8) [PI5 Sensor Config] (LF8) [PI5 Sensor Config] (NPF8) [PI5 Sensor Config] (HIF8)
PIL6 | DI6 PulseInput Low Frequency | 16#341C = 13340 | 16#2067/29 | 16#A3/01/8D = 163/01/141 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.01 Hz | 0.00 Hz | 0.00 Hz ... 30000.00 Hz | [DI6 PulseInput Low Freq] (PIL6) | [DI6 Frequency measured] (PFC6) [DI6 Pulse Config] (PAI6) [PI6 Sensor Config] (IF9) [PI6 Sensor Config] (PF9) [PI6 Sensor Config] (BIP6) [PI6 Sensor Config] (LIP6) [PI6 Sensor Config] (SIF9) [PI6 Sensor Config] (FIF9) [PI6 Sensor Config] (LF9) [PI6 Sensor Config] (NPF9) [PI6 Sensor Config] (HIF9)
PLFA | Pump Low Flow activation delay | 16#3E66 = 15974 | 16#2081/4B | 16#B0/01/AF = 176/01/175 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PumpLF ActivDelay] (PLFA) | [Pump low flow Monit] (PLF) [Settings] (SET)
PLFB | Response to pump Low Flow error | 16#3E68 = 15976 | 16#2081/4D | 16#B0/01/B1 = 176/01/177 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [PumpLF Error Resp] (PLFB) | [Pump low flow Monit] (PLF)
PLFD | Pump Low Flow error delay | 16#3E67 = 15975 | 16#2081/4C | 16#B0/01/B0 = 176/01/176 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 10 s | 0 s ... 3600 s | [PumpLF Error Delay] (PLFD) | [Pump low flow Monit] (PLF) [Settings] (SET)
PLFL | Pump Low Flow minimum level | 16#3E64 = 15972 | 16#2081/49 | 16#B0/01/AD = 176/01/173 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [PumpLF Min Level] (PLFL) | [Pump low flow Monit] (PLF) [Settings] (SET)
PLFM | Pump Low Flow monitoring mode | 16#3E62 = 15970 | 16#2081/47 | 16#B0/01/AB = 176/01/171 | PLFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [PumpLF Monitoring] (PLFM) | [Pump low flow Monit] (PLF)
PLFR | Pump Low Flow restart delay | 16#3E69 = 15977 | 16#2081/4E | 16#B0/01/B2 = 176/01/178 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 3600 s | [PumpLF Restart Delay] (PLFR) | [Pump low flow Monit] (PLF) [Settings] (SET)
PLFW | Pump Low Flow digital input assignment | 16#3E63 = 15971 | 16#2081/48 | 16#B0/01/AC = 176/01/172 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [PumpLF DI Assign] (PLFW) | [Pump low flow Monit] (PLF)
PLFX | Pump Low Flow power factor | 16#3E65 = 15973 | 16#2081/4A | 16#B0/01/AE = 176/01/174 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 110 % | 100 % ... 500 % | [PumpLF Power Factor] (PLFX) | [Pump low flow Monit] (PLF) [Settings] (SET)
PPOA | Priming Pump Assignment | 16#3DCC = 15820 | 16#2080/15 | 16#B0/01/15 = 176/01/21 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Priming Pump Assign] (PPOA) | [Priming pump ctrl] (PPC)
PPSD | Delay before starting the lead pump | 16#3DCD = 15821 | 16#2080/16 | 16#B0/01/16 = 176/01/22 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 30 s | 0 s ... 3600 s | [Priming Time] (PPSD) | [Priming pump ctrl] (PPC) [Settings] (SET)
PS1A | Inlet Pressure Sensor Assignment | 16#3D55 = 15701 | 16#207F/2 | 16#AF/01/66 = 175/01/102 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [InletPres Assign] (PS1A) | [Sensors Assignment] (SSC) [Inlet pressure monitoring] (IPP) [Priming pump ctrl] (PPC)
PS1V | Inlet Pressure Value | 16#3D61 = 15713 | 16#207F/E | 16#AF/01/72 = 175/01/114 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Inlet Press. Value] (PS1V) | [Variable Speed Pump] (MPP) [Control] (CTR) [Application Parameters] (APR)
PS2A | Outlet Pressure Sensor Assignment | 16#3D56 = 15702 | 16#207F/3 | 16#AF/01/67 = 175/01/103 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [OutletPres Assign] (PS2A) | [Sensors Assignment] (SSC) [Outlet pressure monitoring] (OPP) [Pipe fill] (PFI) [Sleep menu] (SLP) [Wake up menu] (WKP)
PS2V | Outlet Pressure | 16#3D62 = 15714 | 16#207F/F | 16#AF/01/73 = 175/01/115 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Outlet Pressure] (PS2V) | [Variable Speed Pump] (MPP) [Control] (CTR) [Application Parameters] (APR)
R3 | R3 Assignment | 16#138B = 5003 | 16#2014/4 | 16#7A/01/04 = 122/01/04 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R3 Assignment] (R3) | [R3 configuration] (R3)
R3D | R3 Delay time | 16#1093 = 4243 | 16#200C/2C | 16#76/01/2C = 118/01/44 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R3 Delay time] (R3D) | [R3 configuration] (R3)
R3H | R3 Holding time | 16#107F = 4223 | 16#200C/18 | 16#76/01/18 = 118/01/24 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R3 Holding time] (R3H) | [R3 configuration] (R3)
R3S | R3 Active level | 16#106B = 4203 | 16#200C/4 | 16#76/01/04 = 118/01/04 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R3 Active at] (R3S) | [R3 configuration] (R3)
R4 | R4 Assignment | 16#138C = 5004 | 16#2014/5 | 16#7A/01/05 = 122/01/05 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R4 Assignment] (R4) | [R4 configuration] (R4)
R4D | R4 Delay time | 16#1094 = 4244 | 16#200C/2D | 16#76/01/2D = 118/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R4 Delay time] (R4D) | [R4 configuration] (R4)
R4H | R4 Holding time | 16#1080 = 4224 | 16#200C/19 | 16#76/01/19 = 118/01/25 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R4 Holding time] (R4H) | [R4 configuration] (R4)
R4S | R4 Active level | 16#106C = 4204 | 16#200C/5 | 16#76/01/05 = 118/01/05 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R4 Active at] (R4S) | [R4 configuration] (R4)
R5 | R5 Assignment | 16#138D = 5005 | 16#2014/6 | 16#7A/01/06 = 122/01/06 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R5 Assignment] (R5) | [R5 configuration] (R5)
R5D | R5 Delay time | 16#1095 = 4245 | 16#200C/2E | 16#76/01/2E = 118/01/46 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R5 Delay time] (R5D) | [R5 configuration] (R5)
R5H | R5 Holding time | 16#1081 = 4225 | 16#200C/1A | 16#76/01/1A = 118/01/26 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R5 Holding time] (R5H) | [R5 configuration] (R5)
R5S | R5 Active at | 16#106D = 4205 | 16#200C/6 | 16#76/01/06 = 118/01/06 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R5 Active at ] (R5S) | [R5 configuration] (R5)
R6 | R6 assignment | 16#138E = 5006 | 16#2014/7 | 16#7A/01/07 = 122/01/07 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R6 Assignment] (R6) | [R6 configuration] (R6)
R6D | R6 activation delay time | 16#1096 = 4246 | 16#200C/2F | 16#76/01/2F = 118/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R6 activ delay time] (R6D) | [R6 configuration] (R6)
R6H | R6 holding delay time | 16#1082 = 4226 | 16#200C/1B | 16#76/01/1B = 118/01/27 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R6 hold delay time] (R6H) | [R6 configuration] (R6)
R6S | R6 status (output active level) | 16#106E = 4206 | 16#200C/7 | 16#76/01/07 = 118/01/07 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R6 status] (R6S) | [R6 configuration] (R6)
RCHT | Flow Limit Thd disable | 16#38B1 = 14513 | 16#2073/E | 16#A9/01/72 = 169/01/114 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [FlowLim Thd Disable] (RCHT) | [Settings] (SET) [Flow limitation] (FLM)
RFP9 | Motor frequency | 16#1C5B = 7259 | 16#202A/3C | 16#85/01/3C = 133/01/60 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFP9) | [None] (DP9)
RFPA | Motor frequency | 16#1DE2 = 7650 | 16#202E/33 | 16#87/01/33 = 135/01/51 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPA) | [None] (DPA)
RFPB | Motor frequency | 16#1DE3 = 7651 | 16#202E/34 | 16#87/01/34 = 135/01/52 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPB) | [None] (DPB)
RFPC | Motor frequency | 16#1DE4 = 7652 | 16#202E/35 | 16#87/01/35 = 135/01/53 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPC) | [None] (DPC)
RFPD | Motor frequency | 16#1DE5 = 7653 | 16#202E/36 | 16#87/01/36 = 135/01/54 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPD) | [None] (DPD)
RFPE | Motor frequency | 16#1DE6 = 7654 | 16#202E/37 | 16#87/01/37 = 135/01/55 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPE) | [None] (DPE)
RFPF | Motor frequency | 16#1DE7 = 7655 | 16#202E/38 | 16#87/01/38 = 135/01/56 |  | History parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Motor frequency] (RFPF) | [None] (DPF)
RHO | Density | 16#3E82 = 16002 | 16#2082/3 | 16#B1/01/03 = 177/01/03 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 kg/m³ | 1000 kg/m³ | 100 kg/m³ ... 10000 kg/m³ | [Liquid Density] (RHO) | [Define system units] (SUC)
RTD | Reference high threshold | 16#2B05 = 11013 | 16#2050/E | 16#98/01/0E = 152/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Reference high Thd] (RTD) | [Threshold reached] (THRE) [Settings] (SET)
RTDL | Reference low threshold | 16#2B06 = 11014 | 16#2050/F | 16#98/01/0F = 152/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [Reference low Thd] (RTDL) | [Threshold reached] (THRE) [Settings] (SET)
RTP9 | Run Elapsed time | 16#1C65 = 7269 | 16#202A/46 | 16#85/01/46 = 133/01/70 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTP9) | [None] (DP9)
RTPA | Run Elapsed time | 16#1DEC = 7660 | 16#202E/3D | 16#87/01/3D = 135/01/61 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPA) | [None] (DPA)
RTPB | Run Elapsed time | 16#1DED = 7661 | 16#202E/3E | 16#87/01/3E = 135/01/62 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPB) | [None] (DPB)
RTPC | Run Elapsed time | 16#1DEE = 7662 | 16#202E/3F | 16#87/01/3F = 135/01/63 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPC) | [None] (DPC)
RTPD | Run Elapsed time | 16#1DEF = 7663 | 16#202E/40 | 16#87/01/40 = 135/01/64 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPD) | [None] (DPD)
RTPE | Run Elapsed time | 16#1DF0 = 7664 | 16#202E/41 | 16#87/01/41 = 135/01/65 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPE) | [None] (DPE)
RTPF | Run Elapsed time | 16#1DF1 = 7665 | 16#202E/42 | 16#87/01/42 = 135/01/66 |  | History parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [Run Elapsed time] (RTPF) | [None] (DPF)
SAI4 | AI4 customer image (1mV, 0.001mA) without filter | 16#14AE = 5294 | 16#2016/5F | 16#7B/01/5F = 123/01/95 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAI5 | AI5 customer image (1mV, 0.001mA) without filter | 16#14B2 = 5298 | 16#2016/63 | 16#7B/01/63 = 123/01/99 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SAO2 | AO2 customer image (1mV, 0.001mA) without filter | 16#14B0 = 5296 | 16#2016/61 | 16#7B/01/61 = 123/01/97 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767
SFP9 | Switching frequency | 16#1CC9 = 7369 | 16#202B/46 | 16#85/01/AA = 133/01/170 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFP9) | [None] (DP9)
SFPA | Switching frequency | 16#1E50 = 7760 | 16#202F/3D | 16#87/01/A1 = 135/01/161 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPA) | [None] (DPA)
SFPB | Switching frequency | 16#1E51 = 7761 | 16#202F/3E | 16#87/01/A2 = 135/01/162 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPB) | [None] (DPB)
SFPC | Switching frequency | 16#1E52 = 7762 | 16#202F/3F | 16#87/01/A3 = 135/01/163 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPC) | [None] (DPC)
SFPD | Switching frequency | 16#1E53 = 7763 | 16#202F/40 | 16#87/01/A4 = 135/01/164 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPD) | [None] (DPD)
SFPE | Switching frequency | 16#1E54 = 7764 | 16#202F/41 | 16#87/01/A5 = 135/01/165 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPE) | [None] (DPE)
SFPF | Switching frequency | 16#1E55 = 7765 | 16#202F/42 | 16#87/01/A6 = 135/01/166 |  | History parameters | R | UINT (Unsigned16) | 1 Hz |  | 0 Hz ... 65535 Hz | [Switching Frequency] (SFPF) | [None] (DPF)
SFS | PID start ref frequency | 16#2EB3 = 11955 | 16#2059/38 | 16#9C/01/9C = 156/01/156 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 500.0 Hz | [PID Start Ref Freq] (SFS) | [Settings] (ST) [Settings] (ST) [Settings] (ST) [Settings] (SET)
SLBS | Sleep Boost Speed | 16#2DEC = 11756 | 16#2057/39 | 16#9B/01/9D = 155/01/157 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Boost Speed] (SLBS) | [Boost] (SBT) [Settings] (SET)
SLBT | Sleep Boost Time | 16#2DED = 11757 | 16#2057/3A | 16#9B/01/9E = 155/01/158 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [Sleep Boost Time] (SLBT) | [Boost] (SBT) [Settings] (SET)
SLE | Sleep Offset Threshold | 16#2DB6 = 11702 | 16#2057/3 | 16#9B/01/67 = 155/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 1.0 Hz | 1.0 Hz ... 1000.0 Hz | [Sleep Offset Thres.] (SLE) | [Settings] (SET) [Stop after speed timeout] (PRSP)
SLFV | Estimated Pump flow value | 16#3E87 = 16007 | 16#2082/8 | 16#B1/01/08 = 177/01/08 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Est. Pump Flow] (SLFV) | [Control] (CTR) [Variable Speed Pump] (MPP) [Est. Pump Flow Conf] (SLPF) [Flow estimation] (SFE) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF)
SLHV | Estimated Pump head value | 16#3E8C = 16012 | 16#2082/D | 16#B1/01/0D = 177/01/13 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Est. Pump Head] (SLHV) | [Variable Speed Pump] (MPP) [dP/Head Correction] (DPHC)
SLNL | Sleep Flow Level | 16#2DE8 = 11752 | 16#2057/35 | 16#9B/01/99 = 155/01/153 |  | Actual values parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Sleep Flow Level] (SLNL) | [Sleep menu] (SLP) [Settings] (SET)
SLPD | Sleep Delay | 16#2DEB = 11755 | 16#2057/38 | 16#9B/01/9C = 155/01/156 |  | Actual values parameters | R/W | INT (Signed16) | 1 s | 20 s | 0 s ... 3600 s | [Sleep Delay] (SLPD) | [Sleep menu] (SLP) [Settings] (SET)
SLPM | Sleep Detection Mode | 16#2DE6 = 11750 | 16#2057/33 | 16#9B/01/97 = 155/01/151 | SLPM | Actual values parameters | R/WS | WORD (Enumeration) | - | [No] NO |  | [Sleep Detect Mode] (SLPM) | [Sleep menu] (SLP)
SLPR | Sleep Power Level | 16#2DEA = 11754 | 16#2057/37 | 16#9B/01/9B = 155/01/155 |  | Actual values parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Sleep Power Level] (SLPR) | [Sleep menu] (SLP) [Settings] (SET)
SLPW | Sleep Switch Assignment | 16#2DE7 = 11751 | 16#2057/34 | 16#9B/01/98 = 155/01/152 | PSLIN | Actual values parameters | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Sleep Switch Assign] (SLPW) | [Sleep menu] (SLP)
SLSL | Sleep Minimum Speed Level | 16#2DE9 = 11753 | 16#2057/36 | 16#9B/01/9A = 155/01/154 |  | Actual values parameters | R/W | INT (Signed16) | 0.1 Hz | 0.0 Hz | 0.0 Hz ... 599.0 Hz | [Sleep Min Speed] (SLSL) | [Sleep menu] (SLP) [Settings] (SET)
SPD | Motor speed | 16#2EE4 = 12004 | 16#205A/5 | 16#9D/01/05 = 157/01/05 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Speed] (SPD) | [Pump Dashboard] (PMT) [Fan Dashboard] (FAN) [Motor parameters] (MMO)
ST00 | Status registers 0 | 16#3EE4 = 16100 | 16#2083/1 | 16#B1/01/65 = 177/01/101 |  | Status parameters | R | WORD (BitString16) | -
ST02 | Status registers 2 | 16#3EE6 = 16102 | 16#2083/3 | 16#B1/01/67 = 177/01/103 |  | Status parameters | R | WORD (BitString16) | -
ST03 | Status registers 3 | 16#3EE7 = 16103 | 16#2083/4 | 16#B1/01/68 = 177/01/104 |  | Status parameters | R | WORD (BitString16) | -
ST04 | Status registers 4 | 16#3EE8 = 16104 | 16#2083/5 | 16#B1/01/69 = 177/01/105 |  | Status parameters | R | WORD (BitString16) | -
ST05 | Status registers 5 | 16#3EE9 = 16105 | 16#2083/6 | 16#B1/01/6A = 177/01/106 |  | Status parameters | R | WORD (BitString16) | -
ST06 | Status registers 6 | 16#3EEA = 16106 | 16#2083/7 | 16#B1/01/6B = 177/01/107 |  | Status parameters | R | WORD (BitString16) | -
ST07 | Status registers 7 | 16#3EEB = 16107 | 16#2083/8 | 16#B1/01/6C = 177/01/108 |  | Status parameters | R | WORD (BitString16) | -
ST08 | Status registers 8 | 16#3EEC = 16108 | 16#2083/9 | 16#B1/01/6D = 177/01/109 |  | Status parameters | R | WORD (BitString16) | -
ST09 | Status registers 9 | 16#3EED = 16109 | 16#2083/A | 16#B1/01/6E = 177/01/110 |  | Status parameters | R | WORD (BitString16) | -
ST11 | Status registers 11 | 16#3EEF = 16111 | 16#2083/C | 16#B1/01/70 = 177/01/112 |  | Status parameters | R | WORD (BitString16) | -
ST12 | Status registers 12 | 16#3EF0 = 16112 | 16#2083/D | 16#B1/01/71 = 177/01/113 |  | Status parameters | R | WORD (BitString16) | -
ST13 | Status registers 13 | 16#3EF1 = 16113 | 16#2083/E | 16#B1/01/72 = 177/01/114 |  | Status parameters | R | WORD (BitString16) | -
ST14 | Status registers 14 | 16#3EF2 = 16114 | 16#2083/F | 16#B1/01/73 = 177/01/115 |  | Status parameters | R | WORD (BitString16) | -
ST15 | Status registers 15 | 16#3EF3 = 16115 | 16#2083/10 | 16#B1/01/74 = 177/01/116 |  | Status parameters | R | WORD (BitString16) | -
ST16 | Status registers 16 | 16#3EF4 = 16116 | 16#2083/11 | 16#B1/01/75 = 177/01/117 |  | Status parameters | R | WORD (BitString16) | -
ST17 | Status registers 17 | 16#3EF5 = 16117 | 16#2083/12 | 16#B1/01/76 = 177/01/118 |  | Status parameters | R | WORD (BitString16) | -
ST18 | Status registers 18 | 16#3EF6 = 16118 | 16#2083/13 | 16#B1/01/77 = 177/01/119 |  | Status parameters | R | WORD (BitString16) | -
ST19 | Status registers 19 | 16#3EF7 = 16119 | 16#2083/14 | 16#B1/01/78 = 177/01/120 |  | Status parameters | R | WORD (BitString16) | -
STOF | STOx Digital Input State | 16#3BDB = 15323 | 16#207B/18 | 16#AD/01/7C = 173/01/124 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535
STP1 | Motor stall max time | 16#2437 = 9271 | 16#203E/48 | 16#8F/01/48 = 143/01/72 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 200.0 s | [Stall Max Time] (STP1) | [Settings] (SET) [Stall monitoring] (STPR)
STP2 | Stall monitoring current level | 16#2438 = 9272 | 16#203E/49 | 16#8F/01/49 = 143/01/73 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | 150.0 % | 0.0 % ... 150.0 % | [Stall Current] (STP2) | [Settings] (SET) [Stall monitoring] (STPR)
STP3 | Stall monitoring frequency level | 16#2439 = 9273 | 16#203E/4A | 16#8F/01/4A = 143/01/74 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | 2.0 Hz | 0.0 Hz ... 500.0 Hz | [Stall Frequency] (STP3) | [Settings] (SET) [Stall monitoring] (STPR)
STPC | Stall monitoring activation | 16#2436 = 9270 | 16#203E/47 | 16#8F/01/47 = 143/01/71 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Stall Monitoring] (STPC) | [Stall monitoring] (STPR)
SUCU | Application Currency Unit | 16#2EF9 = 12025 | 16#205A/1A | 16#9D/01/1A = 157/01/26 | SUCU | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Currency unit list] (SUCU) | [Define system units] (SUC)
SUFR | Application Flow Rate Unit (used as default) | 16#2EF6 = 12022 | 16#205A/17 | 16#9D/01/17 = 157/01/23 | SUFR | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Flow rate unit] (SUFR) | [Define system units] (SUC)
SUPR | Application Pressure Unit (used as default) | 16#2EF5 = 12021 | 16#205A/16 | 16#9D/01/16 = 157/01/22 | SUPR | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [P sensor unit] (SUPR) | [Define system units] (SUC)
SUTP | Application Temperature Unit (used as default) | 16#2EF8 = 12024 | 16#205A/19 | 16#9D/01/19 = 157/01/25 | SUTP | Status parameters | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [Temperature unit] (SUTP) | [Define system units] (SUC)
TBR2 | HMI baud rate | 16#1787 = 6023 | 16#201E/18 | 16#7F/01/18 = 127/01/24 | TBR | Configuration and settings | R/WS | WORD (Enumeration) | - | [19200 bps] 19200 |  | [HMI baud rate] (TBR2) | [Modbus HMI] (MD2)
TDP9 | Drive thermal state | 16#1CB5 = 7349 | 16#202B/32 | 16#85/01/96 = 133/01/150 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDP9) | [None] (DP9)
TDPA | Drive thermal state | 16#1E3C = 7740 | 16#202F/29 | 16#87/01/8D = 135/01/141 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPA) | [None] (DPA)
TDPB | Drive thermal state | 16#1E3D = 7741 | 16#202F/2A | 16#87/01/8E = 135/01/142 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPB) | [None] (DPB)
TDPC | Drive thermal state | 16#1E3E = 7742 | 16#202F/2B | 16#87/01/8F = 135/01/143 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPC) | [None] (DPC)
TDPD | Drive thermal state | 16#1E3F = 7743 | 16#202F/2C | 16#87/01/90 = 135/01/144 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPD) | [None] (DPD)
TDPE | Drive thermal state | 16#1E40 = 7744 | 16#202F/2D | 16#87/01/91 = 135/01/145 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPE) | [None] (DPE)
TDPF | Drive thermal state | 16#1E41 = 7745 | 16#202F/2E | 16#87/01/92 = 135/01/146 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 255 % | [Drive Thermal State] (TDPF) | [None] (DPF)
TFO2 | HMI format | 16#1788 = 6024 | 16#201E/19 | 16#7F/01/19 = 127/01/25 | FOR | Configuration and settings | R/WS | WORD (Enumeration) | - | [8 bits even parity 1 stop bit] 8E1 |  | [HMI format] (TFO2) | [Modbus HMI] (MD2)
TH2A | Thermal warning level for AI2 | 16#33A4 = 13220 | 16#2066/15 | 16#A3/01/15 = 163/01/21 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI2 Th Warn Level] (TH2A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH2B | Response to thermal error for AI2 | 16#33B8 = 13240 | 16#2066/29 | 16#A3/01/29 = 163/01/41 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI2 Th Error Resp] (TH2B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH2F | Thermal error level for AI2 | 16#33AE = 13230 | 16#2066/1F | 16#A3/01/1F = 163/01/31 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI2 Th Error Level] (TH2F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH2S | Activation of the thermal monitoring on AI2 | 16#339A = 13210 | 16#2066/B | 16#A3/01/0B = 163/01/11 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI2 Th Monitoring] (TH2S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH2V | AI2 thermal value | 16#33C2 = 13250 | 16#2066/33 | 16#A3/01/33 = 163/01/51 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI2 Th Value] (TH2V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3A | Thermal warning level for AI3 | 16#33A5 = 13221 | 16#2066/16 | 16#A3/01/16 = 163/01/22 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI3 Th Warn Level] (TH3A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH3B | Response to thermal error for AI3 | 16#33B9 = 13241 | 16#2066/2A | 16#A3/01/2A = 163/01/42 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI3 Th Error Resp] (TH3B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3F | Thermal error level for AI3 | 16#33AF = 13231 | 16#2066/20 | 16#A3/01/20 = 163/01/32 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI3 Th Error Level] (TH3F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH3S | Activation of the thermal monitoring on AI3 | 16#339B = 13211 | 16#2066/C | 16#A3/01/0C = 163/01/12 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI3 Th Monitoring] (TH3S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH3V | AI3 thermal value | 16#33C3 = 13251 | 16#2066/34 | 16#A3/01/34 = 163/01/52 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI3 Th Value] (TH3V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4A | Thermal warning level for AI4 | 16#33A6 = 13222 | 16#2066/17 | 16#A3/01/17 = 163/01/23 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI4 Th Warn Level] (TH4A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH4B | Response to thermal error for AI4 | 16#33BA = 13242 | 16#2066/2B | 16#A3/01/2B = 163/01/43 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI4 Th Error Resp] (TH4B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4F | Thermal error level for AI4 | 16#33B0 = 13232 | 16#2066/21 | 16#A3/01/21 = 163/01/33 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI4 Th Error Level] (TH4F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH4S | Activation of the thermal monitoring on AI4 | 16#339C = 13212 | 16#2066/D | 16#A3/01/0D = 163/01/13 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI4 Th Monitoring] (TH4S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH4V | AI4 thermal value | 16#33C4 = 13252 | 16#2066/35 | 16#A3/01/35 = 163/01/53 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI4 Th Value] (TH4V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5A | Thermal warning level for AI5 | 16#33A7 = 13223 | 16#2066/18 | 16#A3/01/18 = 163/01/24 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI5 Th Warn Level] (TH5A) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH5B | Response to thermal error for AI5 | 16#33BB = 13243 | 16#2066/2C | 16#A3/01/2C = 163/01/44 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [AI5 Th Error Resp] (TH5B) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5F | Thermal error level for AI5 | 16#33B1 = 13233 | 16#2066/22 | 16#A3/01/22 = 163/01/34 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32768 ... 32767 | [AI5 Th Error Level] (TH5F) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Settings] (SET) [Thermal monitoring] (TPP)
TH5S | Activation of the thermal monitoring on AI5 | 16#339D = 13213 | 16#2066/E | 16#A3/01/0E = 163/01/14 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [AI5 Th Monitoring] (TH5S) | [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
TH5V | AI5 thermal value | 16#33C5 = 13253 | 16#2066/36 | 16#A3/01/36 = 163/01/54 |  | Measurement parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [AI5 Th Value] (TH5V) | [Thermal Monitoring] (TPM) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP) [Thermal monitoring] (TPP)
THP9 | Motor thermal state | 16#1C79 = 7289 | 16#202A/5A | 16#85/01/5A = 133/01/90 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THP9) | [None] (DP9)
THPA | Motor thermal state | 16#1E00 = 7680 | 16#202E/51 | 16#87/01/51 = 135/01/81 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPA) | [None] (DPA)
THPB | Motor thermal state | 16#1E01 = 7681 | 16#202E/52 | 16#87/01/52 = 135/01/82 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPB) | [None] (DPB)
THPC | Motor thermal state | 16#1E02 = 7682 | 16#202E/53 | 16#87/01/53 = 135/01/83 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPC) | [None] (DPC)
THPD | Motor thermal state | 16#1E03 = 7683 | 16#202E/54 | 16#87/01/54 = 135/01/84 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPD) | [None] (DPD)
THPE | Motor thermal state | 16#1E04 = 7684 | 16#202E/55 | 16#87/01/55 = 135/01/85 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPE) | [None] (DPE)
THPF | Motor thermal state | 16#1E05 = 7685 | 16#202E/56 | 16#87/01/56 = 135/01/86 |  | History parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 65535 % | [Motor therm state] (THPF) | [None] (DPF)
TJP9 | IGBT junction temp | 16#1CBF = 7359 | 16#202B/3C | 16#85/01/A0 = 133/01/160 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJP9) | [None] (DP9)
TJPA | IGBT junction temp | 16#1E46 = 7750 | 16#202F/33 | 16#87/01/97 = 135/01/151 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPA) | [None] (DPA)
TJPB | IGBT junction temp | 16#1E47 = 7751 | 16#202F/34 | 16#87/01/98 = 135/01/152 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPB) | [None] (DPB)
TJPC | IGBT junction temp | 16#1E48 = 7752 | 16#202F/35 | 16#87/01/99 = 135/01/153 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPC) | [None] (DPC)
TJPD | IGBT junction temp | 16#1E49 = 7753 | 16#202F/36 | 16#87/01/9A = 135/01/154 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPD) | [None] (DPD)
TJPE | IGBT junction temp | 16#1E4A = 7754 | 16#202F/37 | 16#87/01/9B = 135/01/155 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPE) | [None] (DPE)
TJPF | IGBT junction temp | 16#1E4B = 7755 | 16#202F/38 | 16#87/01/9C = 135/01/156 |  | History parameters | R | UINT (Unsigned16) | 1 °C |  | 0 °C ... 255 °C | [IGBT Junction Temp] (TJPF) | [None] (DPF)
TOCT | Type of control | 16#2E8F = 11919 | 16#2059/14 | 16#9C/01/78 = 156/01/120 | TOCT | Configuration and settings | R/WS | WORD (Enumeration) | - | [NA] NA |  | [Type of control] (TOCT) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [Booster Control] (BSC)
TTOB | Ethernet embedded : Time-out | 16#FB9F = 64415 |  |  |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.1 s ... 30.0 s
UIH3 | AI3 voltage scaling parameter of 100% | 16#1148 = 4424 | 16#200E/19 | 16#77/01/19 = 119/01/25 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI3 Max Value] (UIH3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [AI3 configuration] (AI3) [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
UIH4 | AI4 voltage scaling parameter of 100% | 16#1149 = 4425 | 16#200E/1A | 16#77/01/1A = 119/01/26 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI4 Max Value] (UIH4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [AI4 configuration] (AI4) [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
UIH5 | AI5 voltage scaling parameter of 100% | 16#114A = 4426 | 16#200E/1B | 16#77/01/1B = 119/01/27 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AI5 Max Value] (UIH5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [AI5 configuration] (AI5) [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
UIL3 | AI3 voltage scaling parameter of 0% | 16#113E = 4414 | 16#200E/F | 16#77/01/0F = 119/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI3 Min. Value] (UIL3) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3] (AI3C) [AI3 configuration] (AI3) [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
UIL4 | AI4 voltage scaling parameter of 0% | 16#113F = 4415 | 16#200E/10 | 16#77/01/10 = 119/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI4 Min. Value] (UIL4) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4] (AI4C) [AI4 configuration] (AI4) [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
UIL5 | AI5 voltage scaling parameter of 0% | 16#1140 = 4416 | 16#200E/11 | 16#77/01/11 = 119/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AI5 Min. Value] (UIL5) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5] (AI5C) [AI5 configuration] (AI5) [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
ULP9 | DC bus voltage | 16#1C6F = 7279 | 16#202A/50 | 16#85/01/50 = 133/01/80 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULP9) | [None] (DP9)
ULPA | DC bus voltage | 16#1DF6 = 7670 | 16#202E/47 | 16#87/01/47 = 135/01/71 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPA) | [None] (DPA)
ULPB | DC bus voltage | 16#1DF7 = 7671 | 16#202E/48 | 16#87/01/48 = 135/01/72 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPB) | [None] (DPB)
ULPC | DC bus voltage | 16#1DF8 = 7672 | 16#202E/49 | 16#87/01/49 = 135/01/73 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPC) | [None] (DPC)
ULPD | DC bus voltage | 16#1DF9 = 7673 | 16#202E/4A | 16#87/01/4A = 135/01/74 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPD) | [None] (DPD)
ULPE | DC bus voltage | 16#1DFA = 7674 | 16#202E/4B | 16#87/01/4B = 135/01/75 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPE) | [None] (DPE)
ULPF | DC bus voltage | 16#1DFB = 7675 | 16#202E/4C | 16#87/01/4C = 135/01/76 |  | History parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (ULPF) | [None] (DPF)
UOH2 | AQ2 maximum output | 16#1218 = 4632 | 16#2010/21 | 16#78/01/21 = 120/01/33 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 10.0 V | 0.0 V ... 10.0 V | [AQ2 max Output] (UOH2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
UOL2 | AQ2 minimum output | 16#120E = 4622 | 16#2010/17 | 16#78/01/17 = 120/01/23 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 V | 0.0 V | 0.0 V ... 10.0 V | [AQ2 min Output] (UOL2) | [AQ2] (AO2C) [AQ2 configuration] (AO2)
VBUS | DC bus voltage | 16#0CAB = 3243 | 16#2002/2C | 16#71/01/2C = 113/01/44 |  | Measurement parameters | R | UINT (Unsigned16) | 0.1 V |  | 0.0 V ... 6553.5 V | [DC bus voltage] (VBUS) | [Drive parameters] (MPI)
VCB | Catch on fly sensitivity | 16#0C27 = 3111 | 16#2001/C | 16#70/01/70 = 112/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 V | 0.20 V | 0.10 V ... 100.00 V | [Catch on Fly Sensitivity] (VCB) | [Catch on the fly] (FLR)
WUPE | Wake UP Process Error level | 16#2DF0 = 11760 | 16#2057/3D | 16#9B/01/A1 = 155/01/161 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Process Error] (WUPE) | [Wake up menu] (WKP) [Settings] (SET)
WUPF | Wake Up Process level | 16#2DEF = 11759 | 16#2057/3C | 16#9B/01/A0 = 155/01/160 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Process level] (WUPF) | [Wake up menu] (WKP) [Settings] (SET)
WUPM | Wake Up Mode | 16#2DEE = 11758 | 16#2057/3B | 16#9B/01/9F = 155/01/159 | WUPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Feedback] FBK |  | [Wake Up Mode] (WUPM) | [Wake up menu] (WKP)
PREF | Reference Power without drive | 16#2A30 = 10800 | 16#204E/1 | 16#97/01/01 = 151/01/01 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 65535 | [Reference Power] (PREF) | [Energy Saving] (ESA)
EPR | Active Electrical output power estimation | 16#0CE1 = 3297 | 16#2002/62 | 16#71/01/62 = 113/01/98 |  | Actual values parameters | R | INT (Signed16) | 1 % |  | -300 % ... 300 %
AV1J | AIV1 Lowest Process | 16#11AA = 4522 | 16#200F/17 | 16#77/01/7B = 119/01/123 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV1 Lowest Process] (AV1J) | [AIV1 Sensor Config.] (ICV1) [AIV1 Sensor Config.] (OCV1) [AIV1 Sensor Config.] (IFV1) [AIV1 Configuration] (PFV1) [AIV1 Sensor Config.] (LSV1) [AIV1 Sensor Config.] (BIV1) [AIV1 Configuration] (LCV1) [AIV1 Configuration] (LIV1) [AIV1 Sensor Config.] (SIV1) [AIV1 Sensor Config.] (SOV1) [AIV1 Sensor Config.] (WOV1) [AIV1 Sensor Config.] (PF1V) [AIV1 Sensor Config.] (FIV1) [AIV1 Configuration] (PPV1) [AIV1 Sensor Config. ] (LFV1) [AIV1 Sensor Config.] (NPV1) [AIV1 Sensor Config.] (IPV1) [AIV1 Sensor Config.] (OOV1) [AIV1 Sensor Config.] (HIV1)
AV1K | AIV1 Highest Process | 16#11B4 = 4532 | 16#200F/21 | 16#77/01/85 = 119/01/133 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV1 Highest Process] (AV1K) | [AIV1 Sensor Config.] (ICV1) [AIV1 Sensor Config.] (OCV1) [AIV1 Sensor Config.] (IFV1) [AIV1 Configuration] (PFV1) [AIV1 Sensor Config.] (LSV1) [AIV1 Sensor Config.] (BIV1) [AIV1 Configuration] (LCV1) [AIV1 Configuration] (LIV1) [AIV1 Sensor Config.] (SIV1) [AIV1 Sensor Config.] (SOV1) [AIV1 Sensor Config.] (WOV1) [AIV1 Sensor Config.] (PF1V) [AIV1 Sensor Config.] (FIV1) [AIV1 Configuration] (PPV1) [AIV1 Sensor Config. ] (LFV1) [AIV1 Sensor Config.] (NPV1) [AIV1 Sensor Config.] (IPV1) [AIV1 Sensor Config.] (OOV1) [AIV1 Sensor Config.] (HIV1)
SPDM | Motor Mechanical speed | 16#2EEB = 12011 | 16#205A/C | 16#9D/01/0C = 157/01/12 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Motor Mechanical speed] (SPDM) | [Variable Speed Pump] (MPP)
DRC9 | Channel for reference frequency | 16#FB3F = 64319 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRC9) | [None] (DP9)
DRCA | Channel for reference frequency | 16#FB40 = 64320 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCA) | [None] (DPA)
DRCB | Channel for reference frequency | 16#FB41 = 64321 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCB) | [None] (DPB)
DRCC | Channel for reference frequency | 16#FB42 = 64322 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCC) | [None] (DPC)
DRCD | Channel for reference frequency | 16#FB43 = 64323 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCD) | [None] (DPD)
DRCE | Channel for reference frequency | 16#FB44 = 64324 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCE) | [None] (DPE)
DRCF | Channel for reference frequency | 16#FB45 = 64325 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (DRCF) | [None] (DPF)
DCC9 | Command channel | 16#FB4A = 64330 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCC9) | [None] (DP9)
DCCA | Command channel | 16#FB4B = 64331 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCA) | [None] (DPA)
DCCB | Command channel | 16#FB4C = 64332 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCB) | [None] (DPB)
DCCZ | Command channel | 16#FB4D = 64333 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCZ) | [None] (DPC)
DCCD | Command channel | 16#FB4E = 64334 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCD) | [None] (DPD)
DCCE | Command channel | 16#FB4F = 64335 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCE) | [None] (DPE)
DCCF | Command channel | 16#FB50 = 64336 |  |  | CNL | History parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (DCCF) | [None] (DPF)
PFWU | Pipe Fill on wake up | 16#3DBE = 15806 | 16#2080/7 | 16#B0/01/07 = 176/01/07 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [Yes] YES |  | [Pipe Fill on Wake Up] (PFWU) | [Pipe fill] (PFI)
SLPL | Sleep Pressure Level | 16#2DF2 = 11762 | 16#2057/3F | 16#9B/01/A3 = 155/01/163 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Sleep Pressure Level] (SLPL) | [Sleep menu] (SLP) [Settings] (SET)
WUPL | Wake Up Pressure level | 16#2DF3 = 11763 | 16#2057/40 | 16#9B/01/A4 = 155/01/164 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | 0 ... 32767 | [Wake Up Press level] (WUPL) | [Wake up menu] (WKP) [Settings] (SET)
ILCI | Cabinet Input physical state | 16#1453 = 5203 | 16#2016/4 | 16#7B/01/04 = 123/01/04 |  | I/O parameters | R | WORD (BitString16) | -
ILCR | Cabinet IO : Logic inputs real image (bit0 = DI50 ...) | 16#1454 = 5204 | 16#2016/5 | 16#7B/01/05 = 123/01/05 |  | I/O parameters | R | WORD (BitString16) | -
OLCI | Cabinet Ouput physical state | 16#145D = 5213 | 16#2016/E | 16#7B/01/0E = 123/01/14 |  | I/O parameters | R | WORD (BitString16) | -
OLCR | Cabinet IO : Logic outputs real image (bit0 = R60 ...) | 16#145E = 5214 | 16#2016/F | 16#7B/01/0F = 123/01/15 |  | I/O parameters | R/W | WORD (BitString16) | -
PSS | Drive Systems pre-settings status | 16#1F7C = 8060 | 16#2032/3D | 16#89/01/3D = 137/01/61 | PSS | Configuration management | R | WORD (Enumeration) | - |  |  | [Pre-settings Status] (PSS) | [Pre-settings] (PRES)
CBS | Circuit breaker status | 16#352B = 13611 | 16#206A/C | 16#A5/01/0C = 165/01/12 | CBS | Status parameters | R | WORD (Enumeration) | - | [Circuit breaker not configured] NO |  | [CB status] (CBS) | [Circuit breaker] (CCBK)
BPI0 | Power Brick error ID | 16#1E78 = 7800 | 16#2030/1 | 16#88/01/01 = 136/01/01 |  | History parameters | R | WORD (BitString16) | -
BPI1 | Power Brick error ID | 16#1E79 = 7801 | 16#2030/2 | 16#88/01/02 = 136/01/02 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI1) | [None] (DP1)
BPI2 | Power Brick error ID | 16#1E7A = 7802 | 16#2030/3 | 16#88/01/03 = 136/01/03 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI2) | [None] (DP2)
BPI3 | Power Brick error ID | 16#1E7B = 7803 | 16#2030/4 | 16#88/01/04 = 136/01/04 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI3) | [None] (DP3)
BPI4 | Power Brick error ID | 16#1E7C = 7804 | 16#2030/5 | 16#88/01/05 = 136/01/05 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI4) | [None] (DP4)
BPI5 | Power Brick error ID | 16#1E7D = 7805 | 16#2030/6 | 16#88/01/06 = 136/01/06 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI5) | [None] (DP5)
BPI6 | Power Brick error ID | 16#1E7E = 7806 | 16#2030/7 | 16#88/01/07 = 136/01/07 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI6) | [None] (DP6)
BPI7 | Power Brick error ID | 16#1E7F = 7807 | 16#2030/8 | 16#88/01/08 = 136/01/08 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI7) | [None] (DP7)
BPI8 | Power Brick error ID | 16#1E80 = 7808 | 16#2030/9 | 16#88/01/09 = 136/01/09 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI8) | [None] (DP8)
BPI9 | Power Brick error ID | 16#1E81 = 7809 | 16#2030/A | 16#88/01/0A = 136/01/10 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPI9) | [None] (DP9)
BPIA | Power Brick error ID | 16#1E82 = 7810 | 16#2030/B | 16#88/01/0B = 136/01/11 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIA) | [None] (DPA)
BPIB | Power Brick error ID | 16#1E83 = 7811 | 16#2030/C | 16#88/01/0C = 136/01/12 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIB) | [None] (DPB)
BPIC | Power Brick error ID | 16#1E84 = 7812 | 16#2030/D | 16#88/01/0D = 136/01/13 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIC) | [None] (DPC)
BPID | Power Brick error ID | 16#1E85 = 7813 | 16#2030/E | 16#88/01/0E = 136/01/14 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPID) | [None] (DPD)
BPIE | Power Brick error ID | 16#1E86 = 7814 | 16#2030/F | 16#88/01/0F = 136/01/15 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIE) | [None] (DPE)
BPIF | Power Brick error ID | 16#1E87 = 7815 | 16#2030/10 | 16#88/01/10 = 136/01/16 |  | History parameters | R | WORD (BitString16) | - |  |  | [Power Brick Error ID] (BPIF) | [None] (DPF)
BFI0 | AFE Power brick error ID | 16#1E8C = 7820 | 16#2030/15 | 16#88/01/15 = 136/01/21 |  | History parameters | R | WORD (BitString16) | -
BFI1 | AFE Power brick error ID | 16#1E8D = 7821 | 16#2030/16 | 16#88/01/16 = 136/01/22 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI1) | [None] (DP1)
BFI2 | AFE Power brick error ID | 16#1E8E = 7822 | 16#2030/17 | 16#88/01/17 = 136/01/23 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI2) | [None] (DP2)
BFI3 | AFE Power brick error ID | 16#1E8F = 7823 | 16#2030/18 | 16#88/01/18 = 136/01/24 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI3) | [None] (DP3)
BFI4 | AFE Power brick error ID | 16#1E90 = 7824 | 16#2030/19 | 16#88/01/19 = 136/01/25 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI4) | [None] (DP4)
BFI5 | AFE Power brick error ID | 16#1E91 = 7825 | 16#2030/1A | 16#88/01/1A = 136/01/26 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI5) | [None] (DP5)
BFI6 | AFE Power brick error ID | 16#1E92 = 7826 | 16#2030/1B | 16#88/01/1B = 136/01/27 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI6) | [None] (DP6)
BFI7 | AFE Power brick error ID | 16#1E93 = 7827 | 16#2030/1C | 16#88/01/1C = 136/01/28 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI7) | [None] (DP7)
BFI8 | AFE Power brick error ID | 16#1E94 = 7828 | 16#2030/1D | 16#88/01/1D = 136/01/29 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI8) | [None] (DP8)
BFI9 | AFE Power brick error ID | 16#1E95 = 7829 | 16#2030/1E | 16#88/01/1E = 136/01/30 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFI9) | [None] (DP9)
BFIA | AFE Power brick error ID | 16#1E96 = 7830 | 16#2030/1F | 16#88/01/1F = 136/01/31 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIA) | [None] (DPA)
BFIB | AFE Power brick error ID | 16#1E97 = 7831 | 16#2030/20 | 16#88/01/20 = 136/01/32 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIB) | [None] (DPB)
BFIC | AFE Power brick error ID | 16#1E98 = 7832 | 16#2030/21 | 16#88/01/21 = 136/01/33 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIC) | [None] (DPC)
BFID | AFE Power brick error ID | 16#1E99 = 7833 | 16#2030/22 | 16#88/01/22 = 136/01/34 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFID) | [None] (DPD)
BFIE | AFE Power brick error ID | 16#1E9A = 7834 | 16#2030/23 | 16#88/01/23 = 136/01/35 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIE) | [None] (DPE)
BFIF | AFE Power brick error ID | 16#1E9B = 7835 | 16#2030/24 | 16#88/01/24 = 136/01/36 |  | History parameters | R | WORD (BitString16) | - |  |  | [AFE Power brick error ID] (BFIF) | [None] (DPF)
ILN | Mains current | 16#35D7 = 13783 | 16#206B/54 | 16#A5/01/B8 = 165/01/184 |  | Measurement parameters | R | UINT (Unsigned16) | Refer to programming manual |  | 0 ... 65535 | [Mains Current] (ILN) | [Drive parameters] (MPI)
IQRW | Input reactive power | 16#0CE2 = 3298 | 16#2002/63 | 16#71/01/63 = 113/01/99 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Input Reactive Power] (IQRW) | [Elec Ener Input Counter] (ELI)
PWF | Input power factor | 16#35DA = 13786 | 16#206B/57 | 16#A5/01/BB = 165/01/187 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | -3276.7 % ... 3276.7 % | [Input Power Factor] (PWF) | [Elec Ener Input Counter] (ELI)
FAC | Mains frequency | 16#35B6 = 13750 | 16#206B/33 | 16#A5/01/97 = 165/01/151 |  | Measurement parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [Mains Frequency] (FAC) | [Drive parameters] (MPI)
FSBA | AFE : Fan speed | 16#35CA = 13770 | 16#206B/47 | 16#A5/01/AB = 165/01/171 |  | Measurement parameters | R | UINT (Unsigned16) | 1 rpm |  | 0 rpm ... 65535 rpm
FBAT | AFE fan operation time | 16#35CB = 13771 | 16#206B/48 | 16#A5/01/AC = 165/01/172 |  | Actual values parameters | R | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [AFE Fan Operation Time] (FBAT) | [Counter Management] (ELT)
FCT | Cabinet Fan operation time | 16#35CD = 13773 | 16#206B/4A | 16#A5/01/AE = 165/01/174 |  | Actual values parameters | R/WS | UINT (Unsigned32) | 1 h |  | 0 h ... 500000 h | [Cabinet Fan Oper Time] (FCT) | [Counter Management] (ELT)
THDA | AFE : Thermal state | 16#9B22 = 39714 |  |  |  | Measurement parameters | R | UINT (Unsigned16) | 1 % |  | 0 % ... 200 %
BRTH | AFE Run Time | 16#35CF = 13775 | 16#206B/4C | 16#A5/01/B0 = 165/01/176 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
BPTH | AFE Power-On Time | 16#35D1 = 13777 | 16#206B/4E | 16#A5/01/B2 = 165/01/178 |  | Actual values parameters | R | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s
BNSA | AFE Number of starts | 16#35D3 = 13779 | 16#206B/50 | 16#A5/01/B4 = 165/01/180 |  | Actual values parameters | R | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [AFE Nb of starts] (BNSA) | [Counter Management] (ELT)
CLIG | AFE Generator Mode | 16#35D9 = 13785 | 16#206B/56 | 16#A5/01/BA = 165/01/186 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 % | -0.1 % | -0.2 % ... 120.0 % | [AFE Generator Mode] (CLIG) | [Settings] (SET) [Active Front End] (AFE)
TUNT | Autotuning type | 16#259A = 9626 | 16#2042/1B | 16#91/01/1B = 145/01/27 | TUNT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard] STD |  | [Autotuning Type] (TUNT) | [Motor tune] (MTU)
SPD1 | Signed mechanical speed | 16#2EEC = 12012 | 16#205A/D | 16#9D/01/0D = 157/01/13 |  | Actual values parameters | R | INT (Signed32) | Refer to programming manual |  | -100000 ... 100000 | [Signed Mech Speed] (SPD1) | [Motor parameters] (MMO)
FDR0 | FDR error status | 16#FBB0 = 64432 |  |  | EFDR | Configuration management | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR0) | [Fast Device Replacement] (FDR)
FDS0 | FDR operating state | 16#FBB1 = 64433 |  |  | SFDR | Configuration management | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS0) | [Fast Device Replacement] (FDR)
FDA0 | FDR action | 16#FBB2 = 64434 |  |  | FDRA | Configuration management | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA0) | [Fast Device Replacement] (FDR)
FDV0 | Enable FDR function | 16#FBB3 = 64435 |  |  | N_Y | Configuration management | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV0) | [Fast Device Replacement] (FDR)
INF6 | Module identification error (INF6) | 16#1BE1 = 7137 | 16#2029/26 | 16#84/01/8A = 132/01/138 |  | History parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Identification Error (INF6)] (INF6) | [Diag. data] (DDT)
HS1 | HMI status | 16#1C99 = 7321 | 16#202B/16 | 16#85/01/7A = 133/01/122 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS1) | [None] (DP1)
HS2 | HMI status | 16#1C9A = 7322 | 16#202B/17 | 16#85/01/7B = 133/01/123 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS2) | [None] (DP2)
HS3 | HMI status | 16#1C9B = 7323 | 16#202B/18 | 16#85/01/7C = 133/01/124 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS3) | [None] (DP3)
HS4 | HMI status | 16#1C9C = 7324 | 16#202B/19 | 16#85/01/7D = 133/01/125 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS4) | [None] (DP4)
HS5 | HMI status | 16#1C9D = 7325 | 16#202B/1A | 16#85/01/7E = 133/01/126 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS5) | [None] (DP5)
HS6 | HMI status | 16#1C9E = 7326 | 16#202B/1B | 16#85/01/7F = 133/01/127 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS6) | [None] (DP6)
HS7 | HMI status | 16#1C9F = 7327 | 16#202B/1C | 16#85/01/80 = 133/01/128 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS7) | [None] (DP7)
HS8 | HMI status | 16#1CA0 = 7328 | 16#202B/1D | 16#85/01/81 = 133/01/129 | HMIS | History parameters | R | WORD (Enumeration) | - |  |  | [Drive state] (HS8) | [None] (DP8)
OTQN | Motor Torque in Nm | 16#0CC4 = 3268 | 16#2002/45 | 16#71/01/45 = 113/01/69 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Motor Torque (Nm)] (OTQN) | [Motor parameters] (MMO)
TQN | Computed nominal motor torque | 16#25C5 = 9669 | 16#2042/46 | 16#91/01/46 = 145/01/70 |  | Actual values parameters | R | UINT (Unsigned16) | Refer to programming manual | 499 | 1 ... 65535 | [Nom Motor torque] (TQN) | [Motor parameters] (MMO)
UL1 | Mains voltage phase 1-2 | 16#35B3 = 13747 | 16#206B/30 | 16#A5/01/94 = 165/01/148 |  | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 1-2] (UL1) | [Drive parameters] (MPI)
UL2 | Mains voltage phase 2-3 | 16#35B4 = 13748 | 16#206B/31 | 16#A5/01/95 = 165/01/149 |  | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 2-3] (UL2) | [Drive parameters] (MPI)
UL3 | Mains voltage phase 3-1 | 16#35B5 = 13749 | 16#206B/32 | 16#A5/01/96 = 165/01/150 |  | Measurement parameters | R | INT (Signed16) | 0.1 V |  | -3276.7 V ... 3276.7 V | [Mains voltage phase 3-1] (UL3) | [Drive parameters] (MPI)
APPT | Application selection | 16#3D53 = 15699 | 16#207E/64 | 16#AF/01/64 = 175/01/100 | APPT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Generic Pump Control] GPMP |  | [Application Selection] (APPT) | [Macro Configuration] (MCR)
MPC | Motor parameter choice | 16#258E = 9614 | 16#2042/F | 16#91/01/0F = 145/01/15 | MPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Nominal motor Power] NPR |  | [Motor param choice] (MPC) | [data] (MTD)
CRFA | Internal currents filter time | 16#239E = 9118 | 16#203D/13 | 16#8E/01/77 = 142/01/119 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 ms |  | 0.0 ms ... 100.0 ms | [Currents Filter] (CRFA) | [data] (MTD)
RDAE | % error EMF sync | 16#25CC = 9676 | 16#2042/4D | 16#91/01/4D = 145/01/77 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | 0.0 % ... 6553.5 % | [% error EMF sync] (RDAE) | [data] (MTD)
TUNU | Autotuning usage | 16#2593 = 9619 | 16#2042/14 | 16#91/01/14 = 145/01/20 | TUNU | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Autotuning Usage] (TUNU) | [Motor tune] (MTU)
TCR | Level of current for autotuning | 16#259B = 9627 | 16#2042/1C | 16#91/01/1C = 145/01/28 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 % | 0 % | 0 % ... 300 % | [Autotuning Lvl Of Current] (TCR) | [Motor tune] (MTU)
RCL | Alignment Rotational Current Level | 16#3668 = 13928 | 16#206D/1D | 16#A6/01/81 = 166/01/129 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 75 % | 10 % ... 300 % | [Rotational Current Level] (RCL) | [Motor tune] (MTU)
RCIR | RCI alignment with transformer | 16#366A = 13930 | 16#206D/1F | 16#A6/01/83 = 166/01/131 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [RCI With Transformer] (RCIR) | [Motor tune] (MTU)
RCSP | RCI maximum output frequency | 16#366B = 13931 | 16#206D/20 | 16#A6/01/84 = 166/01/132 |  | Configuration and settings | R/WS | INT (Signed16) | 0.1 Hz | RCSP_AUTO | -0.1 Hz ... 500.0 Hz | [RCI Max Freq] (RCSP) | [Motor tune] (MTU)
BOO | Boost | 16#3658 = 13912 | 16#206D/D | 16#A6/01/71 = 166/01/113 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | Refer to programming manual | -100 % ... 100 % | [Boost] (BOO) | [Motor control] (DRC)
FAB | Frequency Boost | 16#3657 = 13911 | 16#206D/C | 16#A6/01/70 = 166/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Freq Boost] (FAB) | [Motor control] (DRC)
TEFF | External feed forward assignment | 16#23AA = 9130 | 16#203D/1F | 16#8E/01/83 = 142/01/131 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [External FeedFwd Assign] (TEFF) | [Spd Loop Optimization] (MCL)
MLTO | MultiDrive Link communication timeout | 16#17C5 = 6085 | 16#201E/56 | 16#7F/01/56 = 127/01/86 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.01 s | 0.25 s | 0.05 s ... 10.00 s | [MDL Comm Timeout] (MLTO) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
TPMM | Maximum power in motor mode | 16#2400 = 9216 | 16#203E/11 | 16#8F/01/11 = 143/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 10 % ... 300 % | [Pmax Motor] (TPMM) | [Torque limitation] (TOL) [Settings] (SET)
TPMG | Maximum power in generator mode | 16#2401 = 9217 | 16#203E/12 | 16#8F/01/12 = 143/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 % | 300 % | 10 % ... 300 % | [Pmax Generator] (TPMG) | [Torque limitation] (TOL) [Settings] (SET)
TWO | Terminal Modbus: Word order | 16#1776 = 6006 | 16#201E/7 | 16#7F/01/07 = 127/01/07 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term word order] (TWO) | [Modbus Fieldbus] (MD1)
TWO2 | Terminal Modbus 2: Word order | 16#178A = 6026 | 16#201E/1B | 16#7F/01/1B = 127/01/27 | TWO | Configuration and settings | R/WS | WORD (Enumeration) | - | [Modbus Word Order ON] HIGH |  | [Term 2 word order] (TWO2) | [Modbus HMI] (MD2)
AV2J | AIV2 Lowest Process | 16#11AB = 4523 | 16#200F/18 | 16#77/01/7C = 119/01/124 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV2 Lowest Process] (AV2J) | [AIV2 Sensor Config.] (ICV2) [AIV2 Sensor Config.] (OCV2) [AIV2 Sensor Config.] (IFV2) [AIV2 Configuration] (PFV2) [AIV2 Sensor Config.] (LSV2) [AIV2 Sensor Config.] (BIV2) [AIV2 Configuration] (LCV2) [AIV2 Configuration] (LIV2) [AIV2 Sensor Config.] (SIV2) [AIV2 Sensor Config.] (SOV2) [AIV2 Sensor Config.] (WOV2) [AIV2 Sensor Config.] (PF2V) [AIV2 Sensor Config.] (FIV2) [AIV2 Sensor Config.] (PPV2) [AIV2 Sensor Config.] (LFV2) [AIV2 Sensor Config.] (NPV2) [AIV2 Sensor Config.] (IPV2) [AIV2 Sensor Config.] (OOV2) [AIV2 Sensor Config.] (HIV2)
AV2K | AIV2 Highest Process | 16#11B5 = 4533 | 16#200F/22 | 16#77/01/86 = 119/01/134 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV2 Highest Process] (AV2K) | [AIV2 Sensor Config.] (ICV2) [AIV2 Sensor Config.] (OCV2) [AIV2 Sensor Config.] (IFV2) [AIV2 Configuration] (PFV2) [AIV2 Sensor Config.] (LSV2) [AIV2 Sensor Config.] (BIV2) [AIV2 Configuration] (LCV2) [AIV2 Configuration] (LIV2) [AIV2 Sensor Config.] (SIV2) [AIV2 Sensor Config.] (SOV2) [AIV2 Sensor Config.] (WOV2) [AIV2 Sensor Config.] (PF2V) [AIV2 Sensor Config.] (FIV2) [AIV2 Sensor Config.] (PPV2) [AIV2 Sensor Config.] (LFV2) [AIV2 Sensor Config.] (NPV2) [AIV2 Sensor Config.] (IPV2) [AIV2 Sensor Config.] (OOV2) [AIV2 Sensor Config.] (HIV2)
AIV2 | AIV2 Image input | 16#14A3 = 5283 | 16#2016/54 | 16#7B/01/54 = 123/01/84 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -10000 ... 10000 | [AIV2 Image input] (AIV2) | [Drive parameters] (MPI)
AIC2 | AI2 network channel | 16#14A4 = 5284 | 16#2016/55 | 16#7B/01/55 = 123/01/85 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AI2 net. Channel] (AIC2) | [Virtual AI2] (AV2) [AIV2 Sensor Config.] (ICV2) [AIV2 Sensor Config.] (OCV2) [AIV2 Sensor Config.] (IFV2) [AIV2 Configuration] (PFV2) [AIV2 Sensor Config.] (LSV2) [AIV2 Sensor Config.] (BIV2) [AIV2 Configuration] (LCV2) [AIV2 Configuration] (LIV2) [AIV2 Sensor Config.] (SIV2) [AIV2 Sensor Config.] (SOV2) [AIV2 Sensor Config.] (WOV2) [AIV2 Sensor Config.] (PF2V) [AIV2 Sensor Config.] (FIV2) [AIV2 Sensor Config.] (PPV2) [AIV2 Sensor Config.] (LFV2) [AIV2 Sensor Config.] (NPV2) [AIV2 Sensor Config.] (IPV2) [AIV2 Sensor Config.] (OOV2) [AIV2 Sensor Config.] (HIV2)
AV3J | AIV3 Lowest Process | 16#11AC = 4524 | 16#200F/19 | 16#77/01/7D = 119/01/125 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV3 Lowest Process] (AV3J) | [AIV3 Sensor Config.] (ICV3) [AIV3 Sensor Config.] (OCV3) [AIV3 Sensor Config.] (IFV3) [AIV3 Configuration] (PFV3) [AIV3 Sensor Config.] (LSV3) [AIV3 Sensor Config.] (BIV3) [AIV3 Configuration] (LCV3) [AIV3 Configuration] (LIV3) [AIV3 Sensor Config.] (SIV3) [AIV3 Sensor Config.] (SOV3) [AIV3 Sensor Config.] (WOV3) [AIV3 Sensor Config.] (PF3V) [AIV3 Sensor Config.] (FIV3) [AIV3 Sensor Config.] (PPV3) [AIV3 Sensor Config.] (LFV3) [AIV3 Sensor Config.] (NPV3) [AIV3 Sensor Config.] (IPV3) [AIV3 Sensor Config.] (OOV3) [AIV3 Sensor Config.] (HIV3)
AV3K | AIV3 Highest Process | 16#11B6 = 4534 | 16#200F/23 | 16#77/01/87 = 119/01/135 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32767 ... 32767 | [AIV3 Highest Process] (AV3K) | [AIV3 Sensor Config.] (ICV3) [AIV3 Sensor Config.] (OCV3) [AIV3 Sensor Config.] (IFV3) [AIV3 Configuration] (PFV3) [AIV3 Sensor Config.] (LSV3) [AIV3 Sensor Config.] (BIV3) [AIV3 Configuration] (LCV3) [AIV3 Configuration] (LIV3) [AIV3 Sensor Config.] (SIV3) [AIV3 Sensor Config.] (SOV3) [AIV3 Sensor Config.] (WOV3) [AIV3 Sensor Config.] (PF3V) [AIV3 Sensor Config.] (FIV3) [AIV3 Sensor Config.] (PPV3) [AIV3 Sensor Config.] (LFV3) [AIV3 Sensor Config.] (NPV3) [AIV3 Sensor Config.] (IPV3) [AIV3 Sensor Config.] (OOV3) [AIV3 Sensor Config.] (HIV3)
AIV3 | AIV3 Image input | 16#14A5 = 5285 | 16#2016/56 | 16#7B/01/56 = 123/01/86 |  | Setpoint parameters | R/W | INT (Signed16) | 1 | 0 | -10000 ... 10000 | [AIV3 Image input] (AIV3) | [Drive parameters] (MPI)
AIC3 | Channel assignment for virtual Analog Input AIV3 | 16#14A6 = 5286 | 16#2016/57 | 16#7B/01/57 = 123/01/87 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [AIV3 Channel Assign] (AIC3) | [Virtual AI3] (AV3) [AIV3 Sensor Config.] (ICV3) [AIV3 Sensor Config.] (OCV3) [AIV3 Sensor Config.] (IFV3) [AIV3 Configuration] (PFV3) [AIV3 Sensor Config.] (LSV3) [AIV3 Sensor Config.] (BIV3) [AIV3 Configuration] (LCV3) [AIV3 Configuration] (LIV3) [AIV3 Sensor Config.] (SIV3) [AIV3 Sensor Config.] (SOV3) [AIV3 Sensor Config.] (WOV3) [AIV3 Sensor Config.] (PF3V) [AIV3 Sensor Config.] (FIV3) [AIV3 Sensor Config.] (PPV3) [AIV3 Sensor Config.] (LFV3) [AIV3 Sensor Config.] (NPV3) [AIV3 Sensor Config.] (IPV3) [AIV3 Sensor Config.] (OOV3) [AIV3 Sensor Config.] (HIV3)
SLFS | Pump system flow | 16#3E95 = 16021 | 16#2082/16 | 16#B1/01/16 = 177/01/22 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Sys Flow] (SLFS) | [Installation] (MPVS) [Est. System Flow Conf] (SLSF) [Est. System Flow Conf] (SLSF) [Est. System Flow Conf] (SLSF)
EPRS | Pump system electrical power | 16#3E97 = 16023 | 16#2082/18 | 16#B1/01/18 = 177/01/24 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Sys Electrical Power] (EPRS) | [Installation] (MPVS)
EFYS | Pump system efficiency indicator | 16#3E98 = 16024 | 16#2082/19 | 16#B1/01/19 = 177/01/25 |  | Actual values parameters | R | INT (Signed16) | 0.1 % |  | 0.0 % ... 100.0 % | [Sys Efficiency Ind] (EFYS) | [Installation] (MPVS)
ECIS | Pump system energy consumption indicator | 16#3E99 = 16025 | 16#2082/1A | 16#B1/01/1A = 177/01/26 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | 0 ... 32767 | [Sys Energy Cons Ind] (ECIS) | [Installation] (MPVS)
EPIS | Pump system performance indicator | 16#3E9A = 16026 | 16#2082/1B | 16#B1/01/1B = 177/01/27 |  | Actual values parameters | R | INT (Signed16) | Refer to programming manual |  | 0 ... 32767 | [Sys Performance Ind] (EPIS) | [Installation] (MPVS)
MPGN | Number of Multipump devices | 16#4075 = 16501 | 16#2087/2 | 16#B3/01/66 = 179/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1 | 0 ... 6 | [Nb of Devices] (MPGN) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
MGID | Multipump device ID selection | 16#4076 = 16502 | 16#2087/3 | 16#B3/01/67 = 179/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 6 | [M/P Device ID] (MGID) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
MPST | Multipump speed mode selection | 16#4078 = 16504 | 16#2087/5 | 16#B3/01/69 = 179/01/105 | MPST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Standard multipump speed control mode] TMC |  | [M/P Speed Mode] (MPST) | [Booster Control] (BSC)
MDLB | Response to Multi-Drive Link communication error | 16#40CC = 16588 | 16#2087/59 | 16#B3/01/BD = 179/01/189 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [MultiDrive ErrorResp] (MDLB) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
MPDB | Response to multipump device error | 16#40CD = 16589 | 16#2087/5A | 16#B3/01/BE = 179/01/190 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [M/P Device ErrorResp] (MPDB) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
MPDT | Multipump master or slave selection | 16#40D5 = 16597 | 16#2087/62 | 16#B3/01/C6 = 179/01/198 | MPDT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Slave] SLAVE |  | [M/P Device Role] (MPDT) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
MPFS | Pump fixed frequency in distributed mode | 16#40D6 = 16598 | 16#2087/63 | 16#B3/01/C7 = 179/01/199 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Pump Fixed Freq] (MPFS) | [Booster Control] (BSC) [Settings] (SET)
BSDH | Booster stage/destage flow hysteresis | 16#40F5 = 16629 | 16#2088/1E | 16#B4/01/1E = 180/01/30 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 3.0 % | 0.0 % ... 100.0 % | [Booster S/D Flow Hyst] (BSDH) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
LCPN | Number of pumps used in level control | 16#410A = 16650 | 16#2088/33 | 16#B4/01/33 = 180/01/51 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 6 | [LevelCtrl Nb of Pumps] (LCPN) | [Level Control] (LCC)
LCDK | Maximum delivery height | 16#4130 = 16688 | 16#2088/59 | 16#B4/01/59 = 180/01/89 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 m | 0.00 m | 0.00 m ... 327.67 m | [Max Delivery Height] (LCDK) | [Level Control] (LCC) [Settings] (SET)
LCDJ | Minimum delivery height | 16#412F = 16687 | 16#2088/58 | 16#B4/01/58 = 180/01/88 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 m | 0.00 m | 0.00 m ... 327.67 m | [Min Delivery Height] (LCDJ) | [Level Control] (LCC) [Settings] (SET)
LCQG | Disturbance flow compensation | 16#4133 = 16691 | 16#2088/5C | 16#B4/01/5C = 180/01/92 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 100.0 % | 0.0 % ... 200.0 % | [Disturb Flow Comp] (LCQG) | [Level Control] (LCC)
LCDT | Level Control stage/destage interval | 16#4138 = 16696 | 16#2088/61 | 16#B4/01/61 = 180/01/97 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 15.0 s | 0.0 s ... 999.9 s | [LevelCtrl S/D Interval] (LCDT) | [Level Control] (LCC) [Settings] (SET)
FDR1 | FDR error status | 16#FBBA = 64442 |  |  | EFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Error Status] (FDR1) | [Fast Device Rep.] (FDRO)
FDS1 | FDR operating state | 16#FBBB = 64443 |  |  | SFDR | Configuration and settings | R | WORD (Enumeration) | - |  |  | [FDR Operating State] (FDS1) | [Fast Device Rep.] (FDRO)
FDA1 | FDR action | 16#FBBC = 64444 |  |  | FDRA | Configuration and settings | R/W | WORD (Enumeration) | - | [NOT ACTIVE] IDLE |  | [FDR Action] (FDA1) | [Fast Device Rep.] (FDRO)
FDV1 | Enable FDR function | 16#FBBD = 64445 |  |  | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Enable FDR] (FDV1) | [Fast Device Rep.] (FDRO)
CIC2 | Incorrect configuration 2 | 16#1C16 = 7190 | 16#2029/5B | 16#84/01/BF = 132/01/191 |  | Fault parameters | R/WS | WORD (BitString16) | -
ST20 | Status registers 20 | 16#3EF8 = 16120 | 16#2083/15 | 16#B1/01/79 = 177/01/121 |  | Status parameters | R | WORD (BitString16) | -
SLDP | Estimated Pump delta pressure value | 16#3E8F = 16015 | 16#2082/10 | 16#B1/01/10 = 177/01/16 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Est. Pump dP] (SLDP) | [Variable Speed Pump] (MPP) [Est. Pump dP Conf] (SLDP) [dP/Head Correction] (DPHC) [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP)
SLDS | Pump system delta pressure | 16#3E9B = 16027 | 16#2082/1C | 16#B1/01/1C = 177/01/28 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Sys Delta Pressure] (SLDS) | [Installation] (MPVS) [Est. System dP Conf] (SLSD) [Est. System dP Conf] (SLSD) [Est. System dP Conf] (SLSD)
SLDK | Estimated Pump delta pressure max | 16#3E91 = 16017 | 16#2082/12 | 16#B1/01/12 = 177/01/18 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32767 ... 32767 | [Est. Pump dP Max] (SLDK) | [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP)
SLDJ | Estimated Pump delta pressure min | 16#3E90 = 16016 | 16#2082/11 | 16#B1/01/11 = 177/01/17 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Est. Pump dP Min] (SLDJ) | [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP) [Est. Pump dP Conf] (SLDP)
BSDT | Booster stage/destage time interval | 16#40D9 = 16601 | 16#2088/2 | 16#B4/01/02 = 180/01/02 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 15.0 s | 0.0 s ... 999.9 s | [Booster S/D Interval] (BSDT) | [Booster Control] (BSC) [Settings] (SET)
OVMA | Overmodulation activation | 16#3634 = 13876 | 16#206C/4D | 16#A6/01/4D = 166/01/77 | OVMA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Default] DEFAULT |  | [Overmodul. Activation] (OVMA) | [Motor control] (DRC)
LPL3 | Level to stop third pump | 16#4121 = 16673 | 16#2088/4A | 16#B4/01/4A = 180/01/74 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 3rd Pump Stop] (LPL3) | [Level settings] (LCL) [Settings] (SET)
BSDM | Booster stage/destage control | 16#40EC = 16620 | 16#2088/15 | 16#B4/01/15 = 180/01/21 | BSDM | Configuration and settings | R/WS | WORD (Enumeration) | - | [None] BFBK |  | [Booster S/D Control] (BSDM) | [Stage/Destage Meth.] (SDMM)
BSRD | Booster stage ramp delay | 16#40EF = 16623 | 16#2088/18 | 16#B4/01/18 = 180/01/24 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 s | 1.0 s | 0.0 s ... 999.9 s | [Boost S Ramp Delay] (BSRD) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
MPLA | Lead pump alternation | 16#407A = 16506 | 16#2087/7 | 16#B3/01/6B = 179/01/107 | MPLA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Deactivated] NO |  | [Lead Pump Altern.] (MPLA) | [System Architecture] (MPQ) [System Architecture] (MPQ)
IFAB | Monitoring circuit B assignment | 16#413D = 16701 | 16#2089/2 | 16#B4/01/66 = 180/01/102 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit B Assign] (IFAB) | [Monitoring circuit B] (CMCB)
IFAC | Monitoring circuit C assignment | 16#413E = 16702 | 16#2089/3 | 16#B4/01/67 = 180/01/103 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit C Assign] (IFAC) | [Monitoring circuit C] (CMCC)
IFAA | Monitoring circuit A assignment | 16#413C = 16700 | 16#2089/1 | 16#B4/01/65 = 180/01/101 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit A Assign] (IFAA) | [Monitoring circuit A] (CMCA)
P24D | Cabinet I/O 24V missing error timeout | 16#414A = 16714 | 16#2089/F | 16#B4/01/73 = 180/01/115 |  | Configuration and settings | R/WS | INT (Signed16) | 1 s | Refer to programming manual | -1 s ... 3000 s | [Cab I/O 24V Timeout] (P24D) | [Error/Warning handling] (CSWM) [Cabinet I/O functions] (CABF)
PSST | Password status | 16#1F72 = 8050 | 16#2032/33 | 16#89/01/33 = 137/01/51 | PSST | Status parameters | R | WORD (Enumeration) | - |  |  | [Password status] (PSST) | [Password] (COD)
BSDC | Booster stage/destage condition | 16#40E2 = 16610 | 16#2088/B | 16#B4/01/0B = 180/01/11 | BSDC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Feedback] FBK |  | [Boost S/D Condition] (BSDC) | [Stage/Destage Cond.] (SDCM)
P1T | Pump 1 Type | 16#409D = 16541 | 16#2087/2A | 16#B3/01/8E = 179/01/142 | PXCT | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 1 Type] (P1T) | [Multipump System] (MPS)
M2CT | Mdb NET frames | 16#178F = 6031 | 16#201E/20 | 16#7F/01/20 = 127/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb NET frames] (M2CT) | [Modbus HMI Diag] (MDH)
CRBA | Current loop default gain | 16#363E = 13886 | 16#206C/57 | 16#A6/01/57 = 166/01/87 |  | Status parameters | R | INT (Signed16) | 1 Hz |  | -32767 Hz ... 32767 Hz | [Cur Loop Default Gain] (CRBA) | [Input Filter] (DCR)
CFRC | Response to cabinet circuit C error | 16#417E = 16766 | 16#2089/43 | 16#B4/01/A7 = 180/01/167 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit C ErrorResp] (CFRC) | [Cabinet circuit C] (CCMC)
FWAP | Update firmware | 16#FFD7 = 65495 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - | [No] NO |  | [Update Firmware] (FWAP) | [Firmware update] (FWUP)
CBSR | Response to Circuit Breaker error | 16#352A = 13610 | 16#206A/B | 16#A5/01/0B = 165/01/11 | CBSR | Configuration and settings | R/WS | WORD (Enumeration) | - | [Error] FLT |  | [CB Error Resp] (CBSR) | [Circuit breaker] (CCBK)
INXP | BACnet instance number | 16#19EA = 6634 | 16#2024/23 | 16#82/01/23 = 130/01/35 |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 | 1 | 0 ... 4194303 | [Instance nb] (INXP) | [BACnet MS/TP] (BACM)
D54D | DI54 delay | 16#0FCC = 4044 | 16#200A/2D | 16#75/01/2D = 117/01/45 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI54 delay] (D54D) | [DI54 configuration] (DI54)
DBS | Delay to close o/p cont. | 16#332D = 13101 | 16#2065/2 | 16#A2/01/66 = 162/01/102 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.15 s | 0.05 s ... 60.00 s | [Delay to motor run] (DBS) | [Output contactor cmd] (OCC)
LPL4 | Level to stop fourth pump | 16#4122 = 16674 | 16#2088/4B | 16#B4/01/4B = 180/01/75 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 4th Pump Stop] (LPL4) | [Level settings] (LCL) [Settings] (SET)
SSDJ | Pump System delta pressure min | 16#3EA0 = 16032 | 16#2082/21 | 16#B1/01/21 = 177/01/33 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Sys dP Min] (SSDJ) | [Est. System dP Conf] (SLSD) [Est. System dP Conf] (SLSD) [Est. System dP Conf] (SLSD)
LPL1 | Level to stop first pump | 16#411F = 16671 | 16#2088/48 | 16#B4/01/48 = 180/01/72 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 1st Pump Stop] (LPL1) | [Level settings] (LCL) [Settings] (SET)
LPL2 | Level to stop second pump | 16#4120 = 16672 | 16#2088/49 | 16#B4/01/49 = 180/01/73 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 2nd Pump Stop] (LPL2) | [Level settings] (LCL) [Settings] (SET)
SSDK | Pump System delta pressure max | 16#3EA1 = 16033 | 16#2082/22 | 16#B1/01/22 = 177/01/34 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32767 ... 32767 | [Sys dP Max] (SSDK) | [Est. System dP Conf] (SLSD) [Est. System dP Conf] (SLSD) [Est. System dP Conf] (SLSD)
DLR | Download rights | 16#1F6A = 8042 | 16#2032/2B | 16#89/01/2B = 137/01/43 | DLR | Configuration and settings | R/W | WORD (Enumeration) | - | [Drive unlocked] DLR1 |  | [Download rights] (DLR) | [Password] (COD)
MPO2 | Command assignment for pump 2 | 16#408A = 16522 | 16#2087/17 | 16#B3/01/7B = 179/01/123 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Pump 2 Cmd Assign] (MPO2) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPO3 | Command assignment for pump 3 | 16#408B = 16523 | 16#2087/18 | 16#B3/01/7C = 179/01/124 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Pump 3 Cmd Assign] (MPO3) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPO1 | Command assignment for pump 1 | 16#4089 = 16521 | 16#2087/16 | 16#B3/01/7A = 179/01/122 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Pump 1 Cmd Assign] (MPO1) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPO6 | Command assignment for pump 6 | 16#408E = 16526 | 16#2087/1B | 16#B3/01/7F = 179/01/127 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Pump 6 Cmd Assign] (MPO6) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPO4 | Command assignment for pump 4 | 16#408C = 16524 | 16#2087/19 | 16#B3/01/7D = 179/01/125 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Pump 4 Cmd Assign] (MPO4) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPO5 | Command assignment for pump 5 | 16#408D = 16525 | 16#2087/1A | 16#B3/01/7E = 179/01/126 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Pump 5 Cmd Assign] (MPO5) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
M1CT | Mdb frame number | 16#177B = 6011 | 16#201E/C | 16#7F/01/0C = 127/01/12 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb Frame Nb] (M1CT) | [Modbus network diag] (MND)
ETXE | Ethernet embedded Tx frames | 16#FBA2 = 64418 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb Tx frames] (ETXE) | [Ethernet Emb Diag] (MPE)
IDLT | Idle mode timeout | 16#3626 = 13862 | 16#206C/3F | 16#A6/01/3F = 166/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | Refer to programming manual | 1 s ... 999 s | [Egy Saving Timeout] (IDLT) | [Stop and Go] (STG)
IDLM | Delay before Energy Saving | 16#3625 = 13861 | 16#206C/3E | 16#A6/01/3E = 166/01/62 |  | Configuration and settings | R/WS | INT (Signed16) | 1 s | Refer to programming manual | -1 s ... 32400 s | [Energy Saving Delay] (IDLM) | [Stop and Go] (STG)
FFSD | Feed Forward stage delay | 16#40F3 = 16627 | 16#2088/1C | 16#B4/01/1C = 180/01/28 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 s | 1.0 s | 0.0 s ... 999.9 s | [FeedFwd Stage Delay] (FFSD) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
APSS | System application state | 16#3E6D = 15981 | 16#2081/52 | 16#B0/01/B6 = 176/01/182 | APPS | Status parameters | R | WORD (Enumeration) | - |  |  | [System App State] (APSS) | [Control] (CTR) [Application Parameters] (APR)
PKTP | Package type | 16#FFD4 = 65492 |  |  | PKTP | Status parameters | R | WORD (Enumeration) | - |  |  | [Package Type] (PKTP) | [Package version] (PFV)
AI1L | Analog input 1 range | 16#1182 = 4482 | 16#200E/53 | 16#77/01/53 = 119/01/83 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI1 range] (AI1L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI1 configuration] (AI1) [AI1 sensor config.] (ICA1) [AI1 Sensor Config.] (OCA1) [AI1 sensor config.] (IF1) [AI1 Sensor config.] (PF1) [AI1 Sensor Config.] (LCS1) [AI1 Sensor Config.] (BIF1) [AI1 Configuration] (LCA1) [AI1 Configuration] (LIF1) [AI1 Sensor config.] (SIF1) [AI1 Sensor Config.] (SOA1) [AI1 Sensor Config.] (WOA1) [AI1 Sensor Config.] (PFA1) [AI1 Installation Flow] (FIF1) [AI1 Configuration] (PPA1) [AI1 Sensor Config.] (LF1) [AI1 Sensor config.] (NPF1) [AI1 sensor config.] (IPA1) [AI1 Sensor config.] (OOA1) [AI1 sensor config.] (HIF1)
LCW1 | Level switch 1 assignment | 16#410B = 16651 | 16#2088/34 | 16#B4/01/34 = 180/01/52 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Level Switch1 Assign] (LCW1) | [Level settings] (LCL)
PSRT | Drive Systems pre-settings unlock | 16#1F7E = 8062 | 16#2032/3F | 16#89/01/3F = 137/01/63 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | [Pre-settings Unlock] (PSRT) | [Pre-settings] (PRES)
CFRA | Response to cabinet circuit A error | 16#417C = 16764 | 16#2089/41 | 16#B4/01/A5 = 180/01/165 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit A ErrorResp] (CFRA) | [Cabinet circuit A] (CCMA)
CFRB | Response to cabinet circuit B error | 16#417D = 16765 | 16#2089/42 | 16#B4/01/A6 = 180/01/166 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [CabinetCircuit B ErrorResp] (CFRB) | [Cabinet circuit B ] (CCMB)
LCTL | Tank Level | 16#4103 = 16643 | 16#2088/2C | 16#B4/01/2C = 180/01/44 |  | Status parameters | R | UINT (Unsigned16) | 0.1 % |  | 0.0 % ... 100.0 % | [Tank Level] (LCTL) | [Control] (CTR) [Application Parameters] (APR)
CRDR | Current loop damping coefficient | 16#363F = 13887 | 16#206C/58 | 16#A6/01/58 = 166/01/88 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 50 % | 1 % ... 800 % | [Cur Loop Damp Coef] (CRDR) | [Input Filter] (DCR)
PVIS | Parameters | 16#FA23 = 64035 |  |  | PVIS | Configuration and settings | R/W | WORD (Enumeration) | - | [Active parameters] ACT |  | [Parameters] (PVIS) | [Visibility] (VIS)
BCWA | Booster working range | 16#40E7 = 16615 | 16#2088/10 | 16#B4/01/10 = 180/01/16 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 2.0 % | 1.0 % ... 100.0 % | [Boost Working range] (BCWA) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
P5OT | Pump 5 running time | 16#40C4 = 16580 | 16#2087/51 | 16#B3/01/B5 = 179/01/181 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Pump 5 Runtime] (P5OT) | [Multipump System] (MPS)
BCS | Booster Status | 16#40DA = 16602 | 16#2088/3 | 16#B4/01/03 = 180/01/03 | BCS | Status parameters | R | WORD (Enumeration) | - |  |  | [Booster Status] (BCS) | [Control] (CTR) [Application Parameters] (APR)
IFMA | Monitoring circuit A error monitoring type | 16#4150 = 16720 | 16#2089/15 | 16#B4/01/79 = 180/01/121 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit A Monitor] (IFMA) | [Monitoring circuit A] (CMCA)
P1OT | Pump 1 running time | 16#40BC = 16572 | 16#2087/49 | 16#B3/01/AD = 179/01/173 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Pump 1 Runtime] (P1OT) | [Multipump System] (MPS)
ARDE | Ethernet rate data | 16#FB9D = 64413 |  |  | RDS | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Ethernet Rate Data] (ARDE) | [Ethernet Emb Diag] (MPE)
FWST | Firmware Update Status | 16#FFDB = 65499 |  |  | FWST | Status parameters | R | WORD (Enumeration) | - |  |  | [Firmware Update Status] (FWST) | [Firmware update diag] (FWUD)
D58D | DI58 delay | 16#0FD0 = 4048 | 16#200A/31 | 16#75/01/31 = 117/01/49 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI58 delay] (D58D) | [DI58 configuration] (DI58)
FS2V | Pump Flow Value | 16#3D64 = 15716 | 16#207F/11 | 16#AF/01/75 = 175/01/117 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Pump Flow] (FS2V) | [Variable Speed Pump] (MPP) [Flow estimation] (SFE)
FS2A | Pump Flow Sensor Assignment | 16#3D58 = 15704 | 16#207F/5 | 16#AF/01/69 = 175/01/105 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Pump Flow Assign.] (FS2A) | [Sensors Assignment] (SSC) [Pump low flow Monit] (PLF)
RHOC | Liquid density used to characterize pump | 16#3D9C = 15772 | 16#207F/49 | 16#AF/01/AD = 175/01/173 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 kg/m³ | 1000 kg/m³ | 100 kg/m³ ... 10000 kg/m³ | [Pump Liquid Density] (RHOC) | [Pump characteristics] (PCR)
MPS | MultiPump function state | 16#407D = 16509 | 16#2087/A | 16#B3/01/6E = 179/01/110 | MPS | Status parameters | R | WORD (Enumeration) | - |  |  | [MultiPump State] (MPS) | [Pump Dashboard] (PMT) [Multipump System] (MPS)
LCLS | Level control low speed | 16#40FB = 16635 | 16#2088/24 | 16#B4/01/24 = 180/01/36 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 Hz | 35.0 Hz | 0.0 Hz ... 500.0 Hz | [LevelCtrl Low Speed] (LCLS) | [Level Control] (LCC) [Settings] (SET)
MPID | Pump ready delay | 16#407B = 16507 | 16#2087/8 | 16#B3/01/6C = 179/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 3600 s | [Pump Ready Delay] (MPID) | [System Architecture] (MPQ) [System Architecture] (MPQ)
P3NS | Pump 3 number of starts | 16#40B4 = 16564 | 16#2087/41 | 16#B3/01/A5 = 179/01/165 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Pump 3 Nb Starts] (P3NS) | [Multipump System] (MPS)
RTHH | Motor run time | 16#0CCA = 3274 | 16#2002/4B | 16#71/01/4B = 113/01/75 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [Motor Run Time] (RTHH) | [Variable Speed Pump] (MPP) [Counter Management] (ELT) [Diag. data] (DDT)
P5NS | Pump 5 number of starts | 16#40B8 = 16568 | 16#2087/45 | 16#B3/01/A9 = 179/01/169 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Pump 5 Nb Starts] (P5NS) | [Multipump System] (MPS)
PKVS | Package version | 16#FFD3 = 65491 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Package Version] (PKVS) | [Package version] (PFV)
P1NS | Pump 1 number of starts | 16#40B0 = 16560 | 16#2087/3D | 16#B3/01/A1 = 179/01/161 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Pump 1 Nb Starts] (P1NS) | [Multipump System] (MPS)
MPI3 | Pump 3 ready to operate assignment | 16#4081 = 16513 | 16#2087/E | 16#B3/01/72 = 179/01/114 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Pump 3 Ready Assign] (MPI3) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPI4 | Pump 4 ready to operate assignment | 16#4082 = 16514 | 16#2087/F | 16#B3/01/73 = 179/01/115 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Pump 4 Ready Assign] (MPI4) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPI5 | Pump 5 ready to operate assignment | 16#4083 = 16515 | 16#2087/10 | 16#B3/01/74 = 179/01/116 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Pump 5 Ready Assign] (MPI5) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPI6 | Pump 6 ready to operate assignment | 16#4084 = 16516 | 16#2087/11 | 16#B3/01/75 = 179/01/117 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Pump 6 Ready Assign] (MPI6) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
ETXO | Ethernet option Tx frames | 16#FBD4 = 64468 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Tx frames] (ETXO) | [Ethernet Module Diag] (MTE)
R60S | R60 Active at | 16#10CC = 4300 | 16#200D/1 | 16#76/01/65 = 118/01/101 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R60 Active at] (R60S) | [R60 configuration] (R60)
R60D | R60 Delay time | 16#10CD = 4301 | 16#200D/2 | 16#76/01/66 = 118/01/102 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R60 Delay time] (R60D) | [R60 configuration] (R60)
LFR1 | Modbus reference frequency | 16#2149 = 8521 | 16#2037/16 | 16#8B/01/7A = 139/01/122 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Modbus Ref Freq] (LFR1) | [Freq. ref. word map] (RWI)
LFR2 | CANopen reference frequency | 16#214A = 8522 | 16#2037/17 | 16#8B/01/7B = 139/01/123 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [CAN Ref Freq] (LFR2) | [Freq. ref. word map] (RWI)
LFR3 | Communication module reference frequency | 16#214B = 8523 | 16#2037/18 | 16#8B/01/7C = 139/01/124 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Com Module Ref Freq] (LFR3) | [Freq. ref. word map] (RWI)
LFR5 | Embedded ethernet reference frequency | 16#214D = 8525 | 16#2037/1A | 16#8B/01/7E = 139/01/126 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Ethernet Embd Ref Freq] (LFR5) | [Freq. ref. word map] (RWI)
P2NS | Pump 2 number of starts | 16#40B2 = 16562 | 16#2087/3F | 16#B3/01/A3 = 179/01/163 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Pump 2 Nb Starts] (P2NS) | [Multipump System] (MPS)
BSS | Booster stage speed | 16#40E3 = 16611 | 16#2088/C | 16#B4/01/0C = 180/01/12 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Booster Stg Speed] (BSS) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
BSD | Booster stage delay | 16#40E5 = 16613 | 16#2088/E | 16#B4/01/0E = 180/01/14 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.0 s ... 999.9 s | [Booster Stg Delay] (BSD) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
DCRF | DC bus ripple estimated frequency | 16#363A = 13882 | 16#206C/53 | 16#A6/01/53 = 166/01/83 |  | Status parameters | R | INT (Signed16) | 0.1 Hz |  | -3276.7 Hz ... 3276.7 Hz | [DC Bus Rip Est Freq] (DCRF) | [Input Filter] (DCR)
MMN | BACnet max master module address | 16#19E8 = 6632 | 16#2024/21 | 16#82/01/21 = 130/01/33 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 1 | 1 ... 127 | [Max master address] (MMN) | [BACnet MS/TP] (BACM)
R64D | R64 Delay time | 16#10D9 = 4313 | 16#200D/E | 16#76/01/72 = 118/01/114 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R64 Delay time] (R64D) | [R64 configuration] (R64)
P6OT | Pump 6 running time | 16#40C6 = 16582 | 16#2087/53 | 16#B3/01/B7 = 179/01/183 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Pump 6 Runtime] (P6OT) | [Multipump System] (MPS)
MPPC | Pump cycling mode | 16#4079 = 16505 | 16#2087/6 | 16#B3/01/6A = 179/01/106 | MPPC | Configuration and settings | R/WS | WORD (Enumeration) | - | [Pump runtime] RTIME |  | [Pump Cycling Mode] (MPPC) | [System Architecture] (MPQ) [System Architecture] (MPQ)
NMTS | Canopen NMT state | 16#17A9 = 6057 | 16#201E/3A | 16#7F/01/3A = 127/01/58 | NMTS | Status parameters | R | WORD (Enumeration) | - |  |  | [Canopen NMT state] (NMTS) | [CANopen map] (CNM)
EMDT | Energy Dashboard | 16#FA31 = 64049 |  |  | EMDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Instantaneous kW trend] CVE
P2S | Pump 2 State | 16#40A8 = 16552 | 16#2087/35 | 16#B3/01/99 = 179/01/153 | PXS | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 2 State] (P2S) | [Multipump System] (MPS)
TFDA | Motor winding A delay after Run | 16#416B = 16747 | 16#2089/30 | 16#B4/01/94 = 180/01/148 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorWinding A Delay] (TFDA) | [Motor winding A] (CTIA)
P5S | Pump 5 State | 16#40AB = 16555 | 16#2087/38 | 16#B3/01/9C = 179/01/156 | PXS | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 5 State] (P5S) | [Multipump System] (MPS)
R61S | R61 Active at | 16#10CF = 4303 | 16#200D/4 | 16#76/01/68 = 118/01/104 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R61 Active at] (R61S) | [R61 configuration] (R61)
R61D | R61 Delay time | 16#10D0 = 4304 | 16#200D/5 | 16#76/01/69 = 118/01/105 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R61 Delay time] (R61D) | [R61 configuration] (R61)
R61H | R61 Holding time | 16#10D1 = 4305 | 16#200D/6 | 16#76/01/6A = 118/01/106 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R61 Holding time] (R61H) | [R61 configuration] (R61)
RP24 | Receive PDO2-4 | 16#32E0 = 13024 | 16#2064/19 | 16#A2/01/19 = 162/01/25 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-4] (RP24) | [PDO2 image] (P02)
RP21 | Receive PDO2-1 | 16#32DD = 13021 | 16#2064/16 | 16#A2/01/16 = 162/01/22 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-1] (RP21) | [PDO2 image] (P02)
RP22 | Receive PDO2-2 | 16#32DE = 13022 | 16#2064/17 | 16#A2/01/17 = 162/01/23 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-2] (RP22) | [PDO2 image] (P02)
RP23 | Receive PDO2-3 | 16#32DF = 13023 | 16#2064/18 | 16#A2/01/18 = 162/01/24 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO2-3] (RP23) | [PDO2 image] (P02)
MDPC | MultiDrive Link pairing code | 16#40A5 = 16549 | 16#2087/32 | 16#B3/01/96 = 179/01/150 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 255 | [MDL Pairing Code] (MDPC) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
CMDT | Control Screen Selection | 16#FA58 = 64088 |  |  | CMDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Parameters List] NO
CMDC | Command channel | 16#FA28 = 64040 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Command Channel] (CMDC) | [Communication map] (CMM)
CBEP | Circuit breaker start pulse activated | 16#352C = 13612 | 16#206A/D | 16#A5/01/0D = 165/01/13 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [CB start pulse activated] (CBEP) | [Circuit breaker] (CCBK)
TFDB | Motor winding B delay after Run | 16#416C = 16748 | 16#2089/31 | 16#B4/01/95 = 180/01/149 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorWinding B Delay] (TFDB) | [Motor winding B] (CTIB)
TFDC | Motor bearing A delay after Run | 16#416D = 16749 | 16#2089/32 | 16#B4/01/96 = 180/01/150 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorBearing A Delay] (TFDC) | [Motor bearing A] (CTIC)
TFDD | Motor bearing B delay after Run | 16#416E = 16750 | 16#2089/33 | 16#B4/01/97 = 180/01/151 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MotorBearing B Delay] (TFDD) | [Motor bearing B] (CTID)
RP32 | Receive PDO3-2 | 16#32CA = 13002 | 16#2064/3 | 16#A2/01/03 = 162/01/03 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-2] (RP32) | [PDO3 image] (P03)
FOR | BACnet module frame format | 16#19CC = 6604 | 16#2024/5 | 16#82/01/05 = 130/01/05 | FOR | Configuration and settings | R/W | WORD (Enumeration) | - |  |  | [Frame format] (FOR) | [BACnet MS/TP] (BACM)
LAC | Access Level | 16#0BBE = 3006 | 16#2000/7 | 16#70/01/07 = 112/01/07 | LAC | Configuration and settings | R/W | WORD (Enumeration) | - | [Standard access] STD |  | [Access Level] (LAC) | [My preferences] (MYP)
CBT3 | Circuit Breaker Switch-on delay | 16#3530 = 13616 | 16#206A/11 | 16#A5/01/11 = 165/01/17 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB Switch-on delay] (CBT3) | [Circuit breaker] (CCBK)
CBT2 | Circuit Breaker stop pulse time | 16#352F = 13615 | 16#206A/10 | 16#A5/01/10 = 165/01/16 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB stop pulse time] (CBT2) | [Circuit breaker] (CCBK)
R62D | R62 Delay time | 16#10D3 = 4307 | 16#200D/8 | 16#76/01/6C = 118/01/108 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R62 Delay time] (R62D) | [R62 configuration] (R62)
R62H | R62 Holding time | 16#10D4 = 4308 | 16#200D/9 | 16#76/01/6D = 118/01/109 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R62 Holding time] (R62H) | [R62 configuration] (R62)
COM1 | Modbus com. status | 16#FA2F = 64047 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM1) | [Modbus Fieldbus] (MD1)
COM2 | Mdb com stat | 16#FA30 = 64048 |  |  | COM1 | Status parameters | R | WORD (Enumeration) | - |  |  | [Mdb com stat] (COM2) | [Modbus HMI] (MD2)
P3S | Pump 3 State | 16#40A9 = 16553 | 16#2087/36 | 16#B3/01/9A = 179/01/154 | PXS | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 3 State] (P3S) | [Multipump System] (MPS)
P3T | Pump 3 Type | 16#409F = 16543 | 16#2087/2C | 16#B3/01/90 = 179/01/144 | PXCT | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 3 Type] (P3T) | [Multipump System] (MPS)
RP34 | Receive PDO3-4 | 16#32CC = 13004 | 16#2064/5 | 16#A2/01/05 = 162/01/05 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-4] (RP34) | [PDO3 image] (P03)
RP33 | Receive PDO3-3 | 16#32CB = 13003 | 16#2064/4 | 16#A2/01/04 = 162/01/04 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-3] (RP33) | [PDO3 image] (P03)
RP31 | Receive PDO3-1 | 16#32C9 = 13001 | 16#2064/2 | 16#A2/01/02 = 162/01/02 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO3-1] (RP31) | [PDO3 image] (P03)
CBDP | Circuit breaker stop pulse activated | 16#352D = 13613 | 16#206A/E | 16#A5/01/0E = 165/01/14 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [CB stop pulse activated] (CBDP) | [Circuit breaker] (CCBK)
REC1 | RX Error Counter | 16#17AB = 6059 | 16#201E/3C | 16#7F/01/3C = 127/01/60 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [RX Error Counter] (REC1) | [CANopen map] (CNM)
R62S | R62 Active at | 16#10D2 = 4306 | 16#200D/7 | 16#76/01/6B = 118/01/107 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R62 Active at] (R62S) | [R62 configuration] (R62)
PPFD | Primed Condition Delay | 16#3DD1 = 15825 | 16#2080/1A | 16#B0/01/1A = 176/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 60 s | [Primed Condition Delay] (PPFD) | [Priming pump ctrl] (PPC) [Settings] (SET)
AV3A | AIV3 assignment | 16#12FF = 4863 | 16#2012/40 | 16#79/01/40 = 121/01/64 | CSA | Configuration and settings | R | WORD (Enumeration) | - |  |  | [AIV3 assignment] (AV3A) | [AIV3 assignment] (AV3A) [Virtual AI3] (AV3)
R63 | R63 Assignment | 16#13B3 = 5043 | 16#2014/2C | 16#7A/01/2C = 122/01/44 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R63 Assignment] (R63) | [R63 configuration] (R63)
R62 | R62 Assignment | 16#13B2 = 5042 | 16#2014/2B | 16#7A/01/2B = 122/01/43 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R62 Assignment] (R62) | [R62 configuration] (R62)
R61 | R61 Assignment | 16#13B1 = 5041 | 16#2014/2A | 16#7A/01/2A = 122/01/42 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R61 Assignment] (R61) | [R61 configuration] (R61)
R60 | R60 Assignment | 16#13B0 = 5040 | 16#2014/29 | 16#7A/01/29 = 122/01/41 | PSL | Configuration and settings | R | WORD (Enumeration) | - | Refer to programming manual |  | [R60 Assignment] (R60) | [R60 configuration] (R60)
AV3T | Configuration of virtual analog input AIV3 | 16#14AA = 5290 | 16#2016/5B | 16#7B/01/5B = 123/01/91 | AVOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [+/- 8192] INEG |  | [AIV3 Type] (AV3T) | [Virtual AI3] (AV3)
R66 | R66 Assignment | 16#13B6 = 5046 | 16#2014/2F | 16#7A/01/2F = 122/01/47 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R66 Assignment] (R66) | [R66 configuration] (R66)
R65 | R65 Assignment | 16#13B5 = 5045 | 16#2014/2E | 16#7A/01/2E = 122/01/46 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R65 Assignment] (R65) | [R65 configuration] (R65)
R64 | R64 Assignment | 16#13B4 = 5044 | 16#2014/2D | 16#7A/01/2D = 122/01/45 | PSL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [R64 Assignment] (R64) | [R64 configuration] (R64)
P4T | Pump 4 Type | 16#40A0 = 16544 | 16#2087/2D | 16#B3/01/91 = 179/01/145 | PXCT | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 4 Type] (P4T) | [Multipump System] (MPS)
P4S | Pump 4 State | 16#40AA = 16554 | 16#2087/37 | 16#B3/01/9B = 179/01/155 | PXS | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 4 State] (P4S) | [Multipump System] (MPS)
BCOA | Booster override range | 16#40E8 = 16616 | 16#2088/11 | 16#B4/01/11 = 180/01/17 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Boost Override range] (BCOA) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
TEC1 | TX Error Counter | 16#17AA = 6058 | 16#201E/3B | 16#7F/01/3B = 127/01/59 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [TX Error Counter] (TEC1) | [CANopen map] (CNM)
IPAT | iPar autosave timer | 16#FB16 = 64278 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 0 ... 9999 | [iPar Autosave Timer] (IPAT) | [Profinet] (PNC)
IPAV | iPar service activation | 16#FB12 = 64274 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Activation] (IPAV) | [Profinet] (PNC)
IPAS | iPar autosave activation | 16#FB13 = 64275 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Autosave Act] (IPAS) | [Profinet] (PNC)
MPI1 | Pump 1 ready to operate assignment | 16#407F = 16511 | 16#2087/C | 16#B3/01/70 = 179/01/112 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Pump 1 Ready Assign] (MPI1) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
MPI2 | Pump 2 ready to operate assignment | 16#4080 = 16512 | 16#2087/D | 16#B3/01/71 = 179/01/113 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Pump 2 Ready Assign] (MPI2) | [Pumps Configuration] (PUMP) [Pumps Configuration] (PUMP)
R63S | R63 Active at | 16#10D5 = 4309 | 16#200D/A | 16#76/01/6E = 118/01/110 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R63 Active at] (R63S) | [R63 configuration] (R63)
R63H | R63 Holding time | 16#10D7 = 4311 | 16#200D/C | 16#76/01/70 = 118/01/112 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R63 Holding time] (R63H) | [R63 configuration] (R63)
R63D | R63 Delay time | 16#10D6 = 4310 | 16#200D/B | 16#76/01/6F = 118/01/111 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R63 Delay time] (R63D) | [R63 configuration] (R63)
KLCK | Display Terminal locked | 16#FA12 = 64018 |  |  |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 min | 5 min | 0 min ... 10 min | [Display Terminal locked] (KLCK) | [LCD settings] (CNL)
PMDT | Pump Screen | 16#FA57 = 64087 |  |  | PMDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Parameters List] NO
TP21 | Transmit PDO2-1 | 16#32E7 = 13031 | 16#2064/20 | 16#A2/01/20 = 162/01/32 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-1] (TP21) | [PDO2 image] (P02)
M1EC | Mdb NET CRC errors | 16#177A = 6010 | 16#201E/B | 16#7F/01/0B = 127/01/11 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mb NET CRC errors] (M1EC) | [Modbus network diag] (MND)
AV2A | AIV2 assignment | 16#12FE = 4862 | 16#2012/3F | 16#79/01/3F = 121/01/63 | CSA | Configuration and settings | R | WORD (Enumeration) | - |  |  | [AIV2 assignment] (AV2A) | [AIV2 assignment] (AV2A) [Virtual AI2] (AV2)
LCTK | Full Tank Level Sensor Value | 16#4102 = 16642 | 16#2088/2B | 16#B4/01/2B = 180/01/43 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Full Tank Level] (LCTK) | [Level Control] (LCC)
LCTJ | Empty Tank Level Sensor Value | 16#4101 = 16641 | 16#2088/2A | 16#B4/01/2A = 180/01/42 |  | Configuration and settings | R/WS | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Empty Tank Level] (LCTJ) | [Level Control] (LCC)
LCTV | Tank volume to be filled or emptied | 16#40FA = 16634 | 16#2088/23 | 16#B4/01/23 = 180/01/35 |  | Configuration and settings | R/WS | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 32767 | [Tank Volume] (LCTV) | [Level Control] (LCC)
AV2T | Configuration of virtual analog input AIV2 | 16#14A8 = 5288 | 16#2016/59 | 16#7B/01/59 = 123/01/89 | AVOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [+/- 8192] INEG |  | [AIV2 Type] (AV2T) | [Virtual AI2] (AV2)
LPL5 | Level to stop fifth pump | 16#4123 = 16675 | 16#2088/4C | 16#B4/01/4C = 180/01/76 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 5th Pump Stop] (LPL5) | [Level settings] (LCL) [Settings] (SET)
LPL6 | Level to stop sixth pump | 16#4124 = 16676 | 16#2088/4D | 16#B4/01/4D = 180/01/77 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 6th Pump Stop] (LPL6) | [Level settings] (LCL) [Settings] (SET)
VLIM | Output voltage limitation | 16#3637 = 13879 | 16#206C/50 | 16#A6/01/50 = 166/01/80 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 V | VLIM_DEFAULT | 0 V ... 9999 V | [Output Voltage Limit] (VLIM) | [Motor control] (DRC)
LCW2 | Level switch 2 assignment | 16#410C = 16652 | 16#2088/35 | 16#B4/01/35 = 180/01/53 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Level Switch2 Assign] (LCW2) | [Level settings] (LCL)
WUPD | Wake Up delay | 16#2DF4 = 11764 | 16#2057/41 | 16#9B/01/A5 = 155/01/165 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [Wake Up Delay] (WUPD) | [Wake up menu] (WKP)
WPXF | Pump operating point filter | 16#3EBC = 16060 | 16#2082/3D | 16#B1/01/3D = 177/01/61 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.00 s ... 60.00 s | [Pump Op Point Filter] (WPXF) | [Est. Pump Flow Conf] (SLPF) [Est. Pump dP Conf] (SLDP) [Pump characteristics] (PCR) [dP/Head Correction] (DPHC) [Est. Pump Flow Conf] (SLPF) [Est. Pump dP Conf] (SLDP) [Est. Pump Flow Conf] (SLPF) [Est. Pump dP Conf] (SLDP) [Settings] (SET) [Flow estimation] (SFE) [Stage/Destage Cond.] (SDCM)
R64S | R64 Active at | 16#10D8 = 4312 | 16#200D/D | 16#76/01/71 = 118/01/113 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R64 Active at] (R64S) | [R64 configuration] (R64)
R64H | R64 Holding time | 16#10DA = 4314 | 16#200D/F | 16#76/01/73 = 118/01/115 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R64 Holding time] (R64H) | [R64 configuration] (R64)
CFDC | Cabinet circuit C delay after Run | 16#416A = 16746 | 16#2089/2F | 16#B4/01/93 = 180/01/147 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit C Delay] (CFDC) | [Cabinet circuit C] (CCMC)
CFDB | Cabinet circuit B delay after Run | 16#4169 = 16745 | 16#2089/2E | 16#B4/01/92 = 180/01/146 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit B Delay] (CFDB) | [Cabinet circuit B ] (CCMB)
CFDA | Cabinet circuit A delay after Run | 16#4168 = 16744 | 16#2089/2D | 16#B4/01/91 = 180/01/145 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [CabinetCircuit A Delay] (CFDA) | [Cabinet circuit A] (CCMA)
P4NS | Pump 4 number of starts | 16#40B6 = 16566 | 16#2087/43 | 16#B3/01/A7 = 179/01/167 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Pump 4 Nb Starts] (P4NS) | [Multipump System] (MPS)
P5T | Pump 5 Type | 16#40A1 = 16545 | 16#2087/2E | 16#B3/01/92 = 179/01/146 | PXCT | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 5 Type] (P5T) | [Multipump System] (MPS)
PLID | Lead Pump | 16#40D4 = 16596 | 16#2087/61 | 16#B3/01/C5 = 179/01/197 | PNID | Status parameters | R | WORD (Enumeration) | - |  |  | [Lead Pump] (PLID) | [Multipump System] (MPS)
D53D | DI53 delay | 16#0FCB = 4043 | 16#200A/2C | 16#75/01/2C = 117/01/44 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI53 delay] (D53D) | [DI53 configuration] (DI53)
MIF | BACnet maximum information frames | 16#19E9 = 6633 | 16#2024/22 | 16#82/01/22 = 130/01/34 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 | 10 | 1 ... 100 | [Max info frames] (MIF) | [BACnet MS/TP] (BACM)
IM00 | IP Mode Ethernet Embd | 16#FB90 = 64400 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [IP Mode Ether. Embd] (IM00) | [Embd Eth Config] (ETE)
CBT1 | Circuit Breaker start pulse time | 16#352E = 13614 | 16#206A/F | 16#A5/01/0F = 165/01/15 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB start pulse time] (CBT1) | [Circuit breaker] (CCBK)
CBT5 | Circuit Breaker Disable stop delay | 16#3532 = 13618 | 16#206A/13 | 16#A5/01/13 = 165/01/19 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 60.0 s | 0.0 s ... 360.0 s | [CB Disable stop delay] (CBT5) | [Circuit breaker] (CCBK)
CBT4 | Circuit Breaker Switch-off delay | 16#3531 = 13617 | 16#206A/12 | 16#A5/01/12 = 165/01/18 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 0.1 s | 0.5 s | 0.1 s ... 60.0 s | [CB Switch-off delay] (CBT4) | [Circuit breaker] (CCBK)
RP14 | Receive PDO1-4 | 16#32F4 = 13044 | 16#2064/2D | 16#A2/01/2D = 162/01/45 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-4] (RP14) | [PDO1 image] (P01)
RP11 | Receive PDO1-1 | 16#32F1 = 13041 | 16#2064/2A | 16#A2/01/2A = 162/01/42 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-1] (RP11) | [PDO1 image] (P01)
RP13 | Receive PDO1-3 | 16#32F3 = 13043 | 16#2064/2C | 16#A2/01/2C = 162/01/44 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-3] (RP13) | [PDO1 image] (P01)
RP12 | Receive PDO1-2 | 16#32F2 = 13042 | 16#2064/2B | 16#A2/01/2B = 162/01/43 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Receive PDO1-2] (RP12) | [PDO1 image] (P01)
MMID | Active master ID | 16#40AF = 16559 | 16#2087/3C | 16#B3/01/A0 = 179/01/160 | PNID | Status parameters | R | WORD (Enumeration) | - |  |  | [Active Master ID] (MMID) | [Multipump System] (MPS)
IPM | IP mode | 16#FAFA = 64250 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | Refer to programming manual |  | [IP mode] (IPM) | [Profinet] (PNC)
LCW4 | Level switch 4 assignment | 16#410E = 16654 | 16#2088/37 | 16#B4/01/37 = 180/01/55 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Level Switch4 Assign] (LCW4) | [Level settings] (LCL)
LCRX | Level control random factor | 16#40F9 = 16633 | 16#2088/22 | 16#B4/01/22 = 180/01/34 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [LvlCtrl Random Factor] (LCRX) | [Level Control] (LCC) [Settings] (SET)
D56D | DI56 delay | 16#0FCE = 4046 | 16#200A/2F | 16#75/01/2F = 117/01/47 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI56 delay] (D56D) | [DI56 configuration] (DI56)
LCW3 | Level switch 3 assignment | 16#410D = 16653 | 16#2088/36 | 16#B4/01/36 = 180/01/54 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Level Switch3 Assign] (LCW3) | [Level settings] (LCL)
CFAC | Cabinet circuit C assignment | 16#4142 = 16706 | 16#2089/7 | 16#B4/01/6B = 180/01/107 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit C Assign] (CFAC) | [Cabinet circuit C] (CCMC)
LCW6 | Level switch 6 assignment | 16#4110 = 16656 | 16#2088/39 | 16#B4/01/39 = 180/01/57 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Level Switch6 Assign] (LCW6) | [Level settings] (LCL)
LCW5 | Level switch 5 assignment | 16#410F = 16655 | 16#2088/38 | 16#B4/01/38 = 180/01/56 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Level Switch5 Assign] (LCW5) | [Level settings] (LCL)
MPFB | Response to Multipump error | 16#407C = 16508 | 16#2087/9 | 16#B3/01/6D = 179/01/109 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MultiPump ErrorResp] (MPFB) | [System Architecture] (MPQ) [System Architecture] (MPQ)
TLP | BACnet fieldbus timeout | 16#19CD = 6605 | 16#2024/6 | 16#82/01/06 = 130/01/06 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 1.0 s ... 60.0 s | [Fieldbus timeout] (TLP) | [BACnet MS/TP] (BACM)
TFCR | BACnet received frame counter | 16#1A05 = 6661 | 16#2024/3E | 16#82/01/3E = 130/01/62 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Rx frame count] (TFCR) | [BACnet MS/TP] (BACM)
TFCT | BACnet transmitted frame counter | 16#1A08 = 6664 | 16#2024/41 | 16#82/01/41 = 130/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Tx frame count] (TFCT) | [BACnet MS/TP] (BACM)
LCWH | Maximum level switch assignment | 16#40FF = 16639 | 16#2088/28 | 16#B4/01/28 = 180/01/40 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Max Lvl Switch Assign] (LCWH) | [Level Control] (LCC)
LCWL | Minimum level switch assignment | 16#40FE = 16638 | 16#2088/27 | 16#B4/01/27 = 180/01/39 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Min Lvl Switch Assign] (LCWL) | [Level Control] (LCC)
AV1A | AIV1 assignment | 16#12FD = 4861 | 16#2012/3E | 16#79/01/3E = 121/01/62 | CSA | Configuration and settings | R | WORD (Enumeration) | - |  |  | [AIV1 assignment] (AV1A) | [AIV1 assignment] (AV1A) [Virtual AI1] (AV1)
AV1T | Configuration of virtual analog input AIV1 | 16#14A7 = 5287 | 16#2016/58 | 16#7B/01/58 = 123/01/88 | AVOT | Configuration and settings | R/WS | WORD (Enumeration) | - | [+/- 8192] INEG |  | [AIV1 Type] (AV1T) | [Virtual AI1] (AV1)
FFTG | Feed Forward disturbance time | 16#2ED3 = 11987 | 16#2059/58 | 16#9C/01/BC = 156/01/188 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 3.0 s | 0.0 s ... 99.9 s | [FeedFwd Disturb Time] (FFTG) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
P6S | Pump 6 State | 16#40AC = 16556 | 16#2087/39 | 16#B3/01/9D = 179/01/157 | PXS | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 6 State] (P6S) | [Multipump System] (MPS)
P4OT | Pump 4 running time | 16#40C2 = 16578 | 16#2087/4F | 16#B3/01/B3 = 179/01/179 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Pump 4 Runtime] (P4OT) | [Multipump System] (MPS)
R60H | R60 Holding time | 16#10CE = 4302 | 16#200D/3 | 16#76/01/67 = 118/01/103 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R60 Holding time] (R60H) | [R60 configuration] (R60)
NBRP | Number of RX PDO | 16#330F = 13071 | 16#2064/48 | 16#A2/01/48 = 162/01/72 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of RX PDO] (NBRP) | [CANopen map] (CNM)
R65S | R65 Active at | 16#10DB = 4315 | 16#200D/10 | 16#76/01/74 = 118/01/116 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R65 Active at] (R65S) | [R65 configuration] (R65)
R65H | R65 Holding time | 16#10DD = 4317 | 16#200D/12 | 16#76/01/76 = 118/01/118 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R65 Holding time] (R65H) | [R65 configuration] (R65)
R65D | R65 Delay time | 16#10DC = 4316 | 16#200D/11 | 16#76/01/75 = 118/01/117 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R65 Delay time] (R65D) | [R65 configuration] (R65)
IM10 | Ethernet option IP mode | 16#FBC2 = 64450 |  |  | IPM | Configuration and settings | R/W | WORD (Enumeration) | - | [DHCP] DHCP |  | [ETH Option IP Mode] (IM10) | [Eth Module Config] (ETO)
LRL4 | Level to start fourth pump | 16#4118 = 16664 | 16#2088/41 | 16#B4/01/41 = 180/01/65 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 4th Pump Start] (LRL4) | [Level settings] (LCL) [Settings] (SET)
LRL5 | Level to start fifth pump | 16#4119 = 16665 | 16#2088/42 | 16#B4/01/42 = 180/01/66 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 5th Pump Start] (LRL5) | [Level settings] (LCL) [Settings] (SET)
LRL2 | Level to start second pump | 16#4116 = 16662 | 16#2088/3F | 16#B4/01/3F = 180/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 2nd Pump Start] (LRL2) | [Level settings] (LCL) [Settings] (SET)
LRL1 | Level to start first pump | 16#4115 = 16661 | 16#2088/3E | 16#B4/01/3E = 180/01/62 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 1st Pump Start] (LRL1) | [Level settings] (LCL) [Settings] (SET)
PPWA | Primed Switch Assignment | 16#3DCF = 15823 | 16#2080/18 | 16#B0/01/18 = 176/01/24 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Primed Switch Assign] (PPWA) | [Priming pump ctrl] (PPC)
TFRC | Response to motor bearing A error | 16#4181 = 16769 | 16#2089/46 | 16#B4/01/AA = 180/01/170 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorBearing A ErrorResp] (TFRC) | [Motor bearing A] (CTIC)
TFRD | Response to motor bearing B error | 16#4182 = 16770 | 16#2089/47 | 16#B4/01/AB = 180/01/171 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorBearing B ErrorResp] (TFRD) | [Motor bearing B] (CTID)
D52D | DI52 delay | 16#0FCA = 4042 | 16#200A/2B | 16#75/01/2B = 117/01/43 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI52 delay] (D52D) | [DI52 configuration] (DI52)
ERXO | Ethernet option Rx frames | 16#FBD2 = 64466 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt Rx frames] (ERXO) | [Ethernet Module Diag] (MTE)
MPSN | Number of staged pumps | 16#40CF = 16591 | 16#2087/5C | 16#B3/01/C0 = 179/01/192 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Nb of Staged Pumps] (MPSN) | [Pump Dashboard] (PMT) [Multipump System] (MPS)
P1S | Pump 1 State | 16#40A7 = 16551 | 16#2087/34 | 16#B3/01/98 = 179/01/152 | PXS | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 1 State] (P1S) | [Multipump System] (MPS)
ERXE | Ethernet embedded Rx frames | 16#FBA0 = 64416 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb Rx frames] (ERXE) | [Ethernet Emb Diag] (MPE)
BDBS | Booster destage bypass speed | 16#40F0 = 16624 | 16#2088/19 | 16#B4/01/19 = 180/01/25 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Boost D bypass Spd] (BDBS) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
BDBT | Booster destage bypass time | 16#40F1 = 16625 | 16#2088/1A | 16#B4/01/1A = 180/01/26 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 1.0 s | 0.0 s ... 999.9 s | [Boost D bypass Time] (BDBT) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
P6T | Pump 6 Type | 16#40A2 = 16546 | 16#2087/2F | 16#B3/01/93 = 179/01/147 | PXCT | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 6 Type] (P6T) | [Multipump System] (MPS)
EN70 | Motor control param. 70 | 16#2563 = 9571 | 16#2041/48 | 16#90/01/AC = 144/01/172 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | 0 | -32768 ... 65535 | [Motor control 70] (EN70) | [Mot. ctrl hidden menu] (MCW)
BCPN | Booster number of pumps | 16#40DB = 16603 | 16#2088/4 | 16#B4/01/04 = 180/01/04 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 6 | [Booster Nb Of Pumps] (BCPN) | [Booster Control] (BSC)
PPIL | Primed Inlet Pressure Level | 16#3DD0 = 15824 | 16#2080/19 | 16#B0/01/19 = 176/01/25 |  | Configuration and settings | R/W | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Primed Inlet Level] (PPIL) | [Priming pump ctrl] (PPC) [Settings] (SET)
MPPN | Number of pumps | 16#4077 = 16503 | 16#2087/4 | 16#B3/01/68 = 179/01/104 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 | 1 | 1 ... 32767 | [Nb Of Pumps] (MPPN) | [System Architecture] (MPQ) [System Architecture] (MPQ)
RCA | Output contactor fdbk | 16#332F = 13103 | 16#2065/4 | 16#A2/01/68 = 162/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Output contact fdbk] (RCA) | [Output contactor cmd] (OCC)
IPPW | Inlet Pressure digital input assignment | 16#3E2C = 15916 | 16#2081/11 | 16#B0/01/75 = 176/01/117 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [InPres DI Assign] (IPPW) | [Inlet pressure monitoring] (IPP)
IPPD | Inlet Pressure error delay | 16#3E2D = 15917 | 16#2081/12 | 16#B0/01/76 = 176/01/118 |  | Configuration and settings | R/W | INT (Signed16) | 1 s | 0 s | 0 s ... 3600 s | [InPresError Delay] (IPPD) | [Inlet pressure monitoring] (IPP)
MPAN | Number of available pumps | 16#40CE = 16590 | 16#2087/5B | 16#B3/01/BF = 179/01/191 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Available Pumps] (MPAN) | [Pump Dashboard] (PMT) [Multipump System] (MPS)
TP13 | Transmit PDO1-3 | 16#32FD = 13053 | 16#2064/36 | 16#A2/01/36 = 162/01/54 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-3] (TP13) | [PDO1 image] (P01)
TP12 | Transmit PDO1-2 | 16#32FC = 13052 | 16#2064/35 | 16#A2/01/35 = 162/01/53 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-2] (TP12) | [PDO1 image] (P01)
TP11 | Transmit PDO1-1 | 16#32FB = 13051 | 16#2064/34 | 16#A2/01/34 = 162/01/52 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-1] (TP11) | [PDO1 image] (P01)
TP14 | Transmit PDO1-4 | 16#32FE = 13054 | 16#2064/37 | 16#A2/01/37 = 162/01/55 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO1-4] (TP14) | [PDO1 image] (P01)
R66D | R66 Delay time | 16#10DF = 4319 | 16#200D/14 | 16#76/01/78 = 118/01/120 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 60000 ms | [R66 Delay time] (R66D) | [R66 configuration] (R66)
R66H | R66 Holding time | 16#10E0 = 4320 | 16#200D/15 | 16#76/01/79 = 118/01/121 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 0 ms | 0 ms ... 9999 ms | [R66 Holding time] (R66H) | [R66 configuration] (R66)
R66S | R66 Active at | 16#10DE = 4318 | 16#200D/13 | 16#76/01/77 = 118/01/119 | NPL | Configuration and settings | R/WS | WORD (Enumeration) | - | [1] POS |  | [R66 Active at] (R66S) | [R66 configuration] (R66)
IFAD | Monitoring circuit D assignment | 16#413F = 16703 | 16#2089/4 | 16#B4/01/68 = 180/01/104 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MonitorCircuit D Assign] (IFAD) | [Monitoring circuit D] (CMCD)
D51D | DI51 delay | 16#0FC9 = 4041 | 16#200A/2A | 16#75/01/2A = 117/01/42 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI51 delay] (D51D) | [DI51 configuration] (DI51)
SSFJ | Pump System flow min | 16#3E9E = 16030 | 16#2082/1F | 16#B1/01/1F = 177/01/31 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Sys Flow Min] (SSFJ) | [Est. System Flow Conf] (SLSF) [Est. System Flow Conf] (SLSF) [Est. System Flow Conf] (SLSF)
SSFK | Pump System flow max | 16#3E9F = 16031 | 16#2082/20 | 16#B1/01/20 = 177/01/32 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32767 ... 32767 | [Sys Flow Max] (SSFK) | [Est. System Flow Conf] (SLSF) [Est. System Flow Conf] (SLSF) [Est. System Flow Conf] (SLSF)
EERE | Ethernet embedded error frames | 16#FBA4 = 64420 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH emb error frames] (EERE) | [Ethernet Emb Diag] (MPE)
P2OT | Pump 2 running time | 16#40BE = 16574 | 16#2087/4B | 16#B3/01/AF = 179/01/175 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Pump 2 Runtime] (P2OT) | [Multipump System] (MPS)
EERO | Ethernet option error frames | 16#FBD6 = 64470 |  |  |  | Configuration and settings | R/W | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [ETH opt error frames] (EERO) | [Ethernet Module Diag] (MTE)
FFDD | Feed Forward destage delay | 16#40F4 = 16628 | 16#2088/1D | 16#B4/01/1D = 180/01/29 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [FeedFwd Destage Delay] (FFDD) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
LCNT | Level control sensor type | 16#40F7 = 16631 | 16#2088/20 | 16#B4/01/20 = 180/01/32 | LCNT | Configuration and settings | R/WS | WORD (Enumeration) | - | [Level Switches] SW |  | [LevelCtrl Sensor Type] (LCNT) | [Level Control] (LCC)
TFAA | Motor winding A assignment | 16#4143 = 16707 | 16#2089/8 | 16#B4/01/6C = 180/01/108 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorWinding A Assign] (TFAA) | [Motor winding A] (CTIA)
TFAC | Motor bearing A assignment | 16#4145 = 16709 | 16#2089/A | 16#B4/01/6E = 180/01/110 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorBearing A Assign] (TFAC) | [Motor bearing A] (CTIC)
TFAB | Motor winding B assignment | 16#4144 = 16708 | 16#2089/9 | 16#B4/01/6D = 180/01/109 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorWinding B Assign] (TFAB) | [Motor winding B] (CTIB)
TFAD | Motor bearing B assignment | 16#4146 = 16710 | 16#2089/B | 16#B4/01/6F = 180/01/111 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [MotorBearing B Assign] (TFAD) | [Motor bearing B] (CTID)
BPHH | AFE Power-On Time | 16#35BE = 13758 | 16#206B/3B | 16#A5/01/9F = 165/01/159 |  | Status parameters | R | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [AFE Power-On Time] (BPHH) | [Counter Management] (ELT)
LCQT | Disturbance flow response time | 16#4134 = 16692 | 16#2088/5D | 16#B4/01/5D = 180/01/93 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 1.00 s | 0.00 s ... 10.00 s | [Disturb Flow resp time] (LCQT) | [Level Control] (LCC) [Settings] (SET)
TP24 | Transmit PDO2-4 | 16#32EA = 13034 | 16#2064/23 | 16#A2/01/23 = 162/01/35 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-4] (TP24) | [PDO2 image] (P02)
TP22 | Transmit PDO2-2 | 16#32E8 = 13032 | 16#2064/21 | 16#A2/01/21 = 162/01/33 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-2] (TP22) | [PDO2 image] (P02)
TP23 | Transmit PDO2-3 | 16#32E9 = 13033 | 16#2064/22 | 16#A2/01/22 = 162/01/34 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO2-3] (TP23) | [PDO2 image] (P02)
BCKL | Red Backlight | 16#FA13 = 64019 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [Red Backlight] (BCKL) | [LCD settings] (CNL)
AI4L | Analog input 4 range | 16#1185 = 4485 | 16#200E/56 | 16#77/01/56 = 119/01/86 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI4 range] (AI4L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI4 configuration] (AI4) [AI4 sensor config.] (ICA4) [AI4 Sensor Config.] (OCA4) [AI4 sensor config.] (IF4) [AI4 Sensor config.] (PF4) [AI4 Sensor Config.] (LCS4) [AI4 Sensor Config.] (BIF4) [AI4 Configuration] (LCA4) [AI4 Configuration] (LIF4) [AI4 Sensor config.] (SIF4) [AI4 Sensor Config.] (SOA4) [AI4 Sensor Config.] (WOA4) [AI4 Sensor Config.] (PFA4) [AI4 Installation Flow] (FIF4) [AI4 Configuration] (PPA4) [AI4 Sensor Config.] (LF4) [AI4 Sensor config.] (NPF4) [AI4 sensor config.] (IPA4) [AI4 Sensor config.] (OOA4) [AI4 sensor config.] (HIF4)
FFG | Feed Forward disturbance gain | 16#2ED2 = 11986 | 16#2059/57 | 16#9C/01/BB = 156/01/187 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 20.0 % | 0.0 % ... 100.0 % | [FeedFwd Disturb Gain] (FFG) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
CFAA | Cabinet circuit A assignment | 16#4140 = 16704 | 16#2089/5 | 16#B4/01/69 = 180/01/105 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit A Assign] (CFAA) | [Cabinet circuit A] (CCMA)
CFAB | Cabinet circuit B assignment | 16#4141 = 16705 | 16#2089/6 | 16#B4/01/6A = 180/01/106 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [CabinetCircuit B Assign] (CFAB) | [Cabinet circuit B ] (CCMB)
FWER | Firmware Update error code | 16#FFD6 = 65494 |  |  | FWER | Status parameters | R | WORD (Enumeration) | - |  |  | [Firmware Update Error] (FWER) | [Firmware update diag] (FWUD)
NBTP | Number of TX PDO | 16#330E = 13070 | 16#2064/47 | 16#A2/01/47 = 162/01/71 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Number of TX PDO] (NBTP) | [CANopen map] (CNM)
BDS | Booster destage speed | 16#40E4 = 16612 | 16#2088/D | 16#B4/01/0D = 180/01/13 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Booster Dstg Spd] (BDS) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
IFRA | Response to monitoring circuit A error | 16#4178 = 16760 | 16#2089/3D | 16#B4/01/A1 = 180/01/161 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit A ErrorResp] (IFRA) | [Monitoring circuit A] (CMCA)
P6NS | Pump 6 number of starts | 16#40BA = 16570 | 16#2087/47 | 16#B3/01/AB = 179/01/171 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 |  | 0 ... 4294967295 | [Pump 6 Nb Starts] (P6NS) | [Multipump System] (MPS)
BDRD | Booster destage ramp delay | 16#40F2 = 16626 | 16#2088/1B | 16#B4/01/1B = 180/01/27 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 s | 0.0 s | 0.0 s ... 999.9 s | [Boost D Ramp Delay] (BDRD) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
MDT | HMI displayed value type | 16#FA20 = 64032 |  |  | MDT | Configuration and settings | R/W | WORD (Enumeration) | - | [Digital values] DEC |  | [Display value type] (MDT) | [Display screen type] (MSC)
D50D | DI50 delay | 16#0FC8 = 4040 | 16#200A/29 | 16#75/01/29 = 117/01/41 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI50 delay] (D50D) | [DI50 configuration] (DI50)
LCPM | Level control stop mode | 16#40FC = 16636 | 16#2088/25 | 16#B4/01/25 = 180/01/37 | LCPM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Each pump stopped individually] INDIV |  | [LevelCtrl Stop Mode] (LCPM) | [Level Control] (LCC)
MPME | Multi-pump master enable assignment | 16#4088 = 16520 | 16#2087/15 | 16#B3/01/79 = 179/01/121 | PSLIN | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not assigned] NO |  | [Master Enable Assign] (MPME) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
DCRA | DC bus ripple amplitude | 16#3639 = 13881 | 16#206C/52 | 16#A6/01/52 = 166/01/82 |  | Status parameters | R | INT (Signed16) | 1 V |  | -32767 V ... 32767 V | [DC Bus Rip Amp Val] (DCRA) | [Input Filter] (DCR)
IFDD | Monitoring circuit D delay after Run | 16#4167 = 16743 | 16#2089/2C | 16#B4/01/90 = 180/01/144 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit D Delay] (IFDD) | [Monitoring circuit D] (CMCD)
IFDA | Monitoring circuit A delay after Run | 16#4164 = 16740 | 16#2089/29 | 16#B4/01/8D = 180/01/141 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit A Delay] (IFDA) | [Monitoring circuit A] (CMCA)
IFDC | Monitoring circuit C delay after Run | 16#4166 = 16742 | 16#2089/2B | 16#B4/01/8F = 180/01/143 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit C Delay] (IFDC) | [Monitoring circuit C] (CMCC)
IFDB | Monitoring circuit B delay after Run | 16#4165 = 16741 | 16#2089/2A | 16#B4/01/8E = 180/01/142 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 s | 0 s | 0 s ... 300 s | [MonitorCircuit B Delay] (IFDB) | [Monitoring circuit B] (CMCB)
TP31 | Transmit PDO3-1 | 16#32D3 = 13011 | 16#2064/C | 16#A2/01/0C = 162/01/12 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-1] (TP31) | [PDO3 image] (P03)
TP33 | Transmit PDO3-3 | 16#32D5 = 13013 | 16#2064/E | 16#A2/01/0E = 162/01/14 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-3] (TP33) | [PDO3 image] (P03)
TP32 | Transmit PDO3-2 | 16#32D4 = 13012 | 16#2064/D | 16#A2/01/0D = 162/01/13 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-2] (TP32) | [PDO3 image] (P03)
TP34 | Transmit PDO3-4 | 16#32D6 = 13014 | 16#2064/F | 16#A2/01/0F = 162/01/15 |  | Configuration and settings | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Transmit PDO3-4] (TP34) | [PDO3 image] (P03)
IFRD | Response to monitoring circuit D error | 16#417B = 16763 | 16#2089/40 | 16#B4/01/A4 = 180/01/164 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit D ErrorResp] (IFRD) | [Monitoring circuit D] (CMCD)
IFI | Use of an input filer | 16#3640 = 13888 | 16#206C/59 | 16#A6/01/59 = 166/01/89 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Input Filter] (IFI) | [Input Filter] (DCR)
AI5L | AI5 Lowest Process | 16#1186 = 4486 | 16#200E/57 | 16#77/01/57 = 119/01/87 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI5 Lowest Process] (AI5L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI5 configuration] (AI5) [AI5 sensor config.] (ICA5) [AI5 Sensor Config.] (OCA5) [AI5 sensor config.] (IF5) [AI5 Sensor config.] (PF5) [AI5 Sensor Config.] (LCS5) [AI5 Sensor Config.] (BIF5) [AI5 Configuration] (LCA5) [AI5 Configuration] (LIF5) [AI5 Sensor config.] (SIF5) [AI5 Sensor Config.] (SOA5) [AI5 Sensor Config.] (WOA5) [AI5 Sensor Config.] (PFA5) [AI5 Installation Flow] (FIF5) [AI5 Configuration] (PPA5) [AI5 Sensor Config.] (LF5) [AI5 Sensor config.] (NPF5) [AI5 sensor config.] (IPA5) [AI5 Sensor config.] (OOA5) [AI5 sensor config.] (HIF5)
LHL4 | Level to reach fourth pump high speed | 16#412C = 16684 | 16#2088/55 | 16#B4/01/55 = 180/01/85 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 4th Pump HSP] (LHL4) | [Level settings] (LCL) [Settings] (SET)
LHL5 | Level to reach fifth pump high speed | 16#412D = 16685 | 16#2088/56 | 16#B4/01/56 = 180/01/86 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 5th Pump HSP] (LHL5) | [Level settings] (LCL) [Settings] (SET)
LHL6 | Level to reach sixth pump high speed | 16#412E = 16686 | 16#2088/57 | 16#B4/01/57 = 180/01/87 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 6th Pump HSP] (LHL6) | [Level settings] (LCL) [Settings] (SET)
LHL1 | Level to reach first pump high speed | 16#4129 = 16681 | 16#2088/52 | 16#B4/01/52 = 180/01/82 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 1st Pump HSP] (LHL1) | [Level settings] (LCL) [Settings] (SET)
LHL2 | Level to reach second pump high speed | 16#412A = 16682 | 16#2088/53 | 16#B4/01/53 = 180/01/83 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 2nd Pump HSP] (LHL2) | [Level settings] (LCL) [Settings] (SET)
LRL3 | Level to start third pump | 16#4117 = 16663 | 16#2088/40 | 16#B4/01/40 = 180/01/64 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 3rd Pump Start] (LRL3) | [Level settings] (LCL) [Settings] (SET)
BRHH | AFE Run Time | 16#35BC = 13756 | 16#206B/39 | 16#A5/01/9D = 165/01/157 |  | Status parameters | R | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [AFE Run Time] (BRHH) | [Counter Management] (ELT)
D57D | DI57 delay | 16#0FCF = 4047 | 16#200A/30 | 16#75/01/30 = 117/01/48 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI57 delay] (D57D) | [DI57 configuration] (DI57)
FCSI | Source configuration | 16#FA51 = 64081 |  |  | FCSI | Configuration and settings | R/WS | WORD (Enumeration) | - | [Macro configuration] INI |  | [Config. Source] (FCSI) | [Factory settings] (FCS)
LCFB | Level control error response | 16#40FD = 16637 | 16#2088/26 | 16#B4/01/26 = 180/01/38 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Ramp stop] RMP |  | [LevelCtrl Error Resp] (LCFB) | [Level Control] (LCC)
RFCC | Channel for reference frequency | 16#FA29 = 64041 |  |  | CNL | Status parameters | R | WORD (Enumeration) | - |  |  | [Ref Freq Channel] (RFCC) | [Communication map] (CMM)
SLFK | Estimated Pump flow max | 16#3E89 = 16009 | 16#2082/A | 16#B1/01/0A = 177/01/10 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | Refer to programming manual | -32767 ... 32767 | [Est. Pump Flow Max] (SLFK) | [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF)
SLFJ | Estimated Pump flow min | 16#3E88 = 16008 | 16#2082/9 | 16#B1/01/09 = 177/01/09 |  | Configuration and settings | R | INT (Signed16) | Refer to programming manual | 0 | -32767 ... 32767 | [Est. Pump Flow Min] (SLFJ) | [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF) [Est. Pump Flow Conf] (SLPF)
PTHH | Power-on time | 16#0CCC = 3276 | 16#2002/4D | 16#71/01/4D = 113/01/77 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 0.1 h |  | 0.0 h ... 429496729.5 h | [Power-on time] (PTHH) | [Counter Management] (ELT)
BSBT | Booster stage bypass time | 16#40EE = 16622 | 16#2088/17 | 16#B4/01/17 = 180/01/23 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 3.0 s | 0.0 s ... 999.9 s | [Boost S Bypass Time] (BSBT) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
TFRA | Response to motor winding A error | 16#417F = 16767 | 16#2089/44 | 16#B4/01/A8 = 180/01/168 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorWinding A ErrorResp] (TFRA) | [Motor winding A] (CTIA)
TFMD | Motor bearing B monitoring | 16#415A = 16730 | 16#2089/1F | 16#B4/01/83 = 180/01/131 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorBearing B Monitor] (TFMD) | [Motor bearing B] (CTID)
TFMA | Motor winding A monitoring | 16#4157 = 16727 | 16#2089/1C | 16#B4/01/80 = 180/01/128 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorWinding A Monitor] (TFMA) | [Motor winding A] (CTIA)
TFRB | Response to motor winding B error | 16#4180 = 16768 | 16#2089/45 | 16#B4/01/A9 = 180/01/169 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MotorWinding B ErrorResp] (TFRB) | [Motor winding B] (CTIB)
TFMC | Motor bearing A monitoring | 16#4159 = 16729 | 16#2089/1E | 16#B4/01/82 = 180/01/130 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorBearing A Monitor] (TFMC) | [Motor bearing A] (CTIC)
TFMB | Motor winding B monitoring | 16#4158 = 16728 | 16#2089/1D | 16#B4/01/81 = 180/01/129 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MotorWinding B Monitor] (TFMB) | [Motor winding B] (CTIB)
IFMB | Monitoring circuit B error monitoring type | 16#4151 = 16721 | 16#2089/16 | 16#B4/01/7A = 180/01/122 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit B Monitor] (IFMB) | [Monitoring circuit B] (CMCB)
IFMC | Monitoring circuit C error monitoring type | 16#4152 = 16722 | 16#2089/17 | 16#B4/01/7B = 180/01/123 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit C Monitor] (IFMC) | [Monitoring circuit C] (CMCC)
IPAE | iPar service status | 16#FB17 = 64279 |  |  | IPAE | Configuration and settings | R/W | WORD (Enumeration) | - | [Idle State] IDLE |  | [iPar Status] (IPAE) | [PROFINET DIAG] (PRN)
IPAF | iPar response to detected error | 16#FB15 = 64277 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [Yes] YES |  | [iPar Error Response] (IPAF) | [Profinet] (PNC)
IFMD | Monitoring circuit D error monitoring type | 16#4153 = 16723 | 16#2089/18 | 16#B4/01/7C = 180/01/124 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [MonitorCircuit D Monitor] (IFMD) | [Monitoring circuit D] (CMCD)
MPPD | Multi-pump power-on master delay | 16#40A6 = 16550 | 16#2087/33 | 16#B3/01/97 = 179/01/151 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 s | 30 s | 0 s ... 120 s | [PwrOn Master Delay] (MPPD) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
LCSV | Level Sensor Value | 16#3D69 = 15721 | 16#207F/16 | 16#AF/01/7A = 175/01/122 |  | Status parameters | R | INT (Signed16) | Refer to programming manual |  | -32767 ... 32767 | [Level Sensor Value] (LCSV) | [Application Parameters] (APR)
LCST | Level control strategy | 16#40F8 = 16632 | 16#2088/21 | 16#B4/01/21 = 180/01/33 | LCST | Configuration and settings | R/WS | WORD (Enumeration) | - | [Switches] TRAD |  | [LevelCtrl Strategy] (LCST) | [Level Control] (LCC)
LCSA | Level Sensor Assignment | 16#3D68 = 15720 | 16#207F/15 | 16#AF/01/79 = 175/01/121 | PSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Not configured] NO |  | [Level Sensor Assign] (LCSA) | [Sensors Assignment] (SSC) [Level Control] (LCC)
AI2L | Analog input 2 range | 16#1183 = 4483 | 16#200E/54 | 16#77/01/54 = 119/01/84 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI2 range] (AI2L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI2 configuration] (AI2) [AI2 sensor config.] (ICA2) [AI2 Sensor Config.] (OCA2) [AI2 sensor config.] (IF2) [AI2 Sensor config.] (PF2) [AI2 Sensor Config.] (LCS2) [AI2 Sensor Config.] (BIF2) [AI2 Configuration] (LCA2) [AI2 Configuration] (LIF2) [AI2 Sensor config.] (SIF2) [AI2 Sensor Config.] (SOA2) [AI2 Sensor Config.] (WOA2) [AI2 Sensor Config.] (PFA2) [AI2 Installation Flow] (FIF2) [AI2 Configuration] (PPA2) [AI2 Sensor Config.] (LF2) [AI2 Sensor config.] (NPF2) [AI2 sensor config.] (IPA2) [AI2 Sensor config.] (OOA2) [AI2 sensor config.] (HIF2)
CRB | Current loop configured gain | 16#363D = 13885 | 16#206C/56 | 16#A6/01/56 = 166/01/86 |  | Configuration and settings | R/WS | INT (Signed16) | 1 Hz | 0 Hz | 0 Hz ... 65535 Hz | [Cur Loop Config Gain] (CRB) | [Input Filter] (DCR)
EFC | BACnet incorrect frame counter | 16#1A06 = 6662 | 16#2024/3F | 16#82/01/3F = 130/01/63 |  | Configuration and settings | R/W | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Incorrect frame count] (EFC) | [BACnet MS/TP] (BACM)
LCS | Level Control Status | 16#4100 = 16640 | 16#2088/29 | 16#B4/01/29 = 180/01/41 | LCS | Status parameters | R | WORD (Enumeration) | - |  |  | [LevelCtrl Status] (LCS) | [Control] (CTR) [Application Parameters] (APR)
M2EC | Mdb NET CRC errors | 16#178E = 6030 | 16#201E/1F | 16#7F/01/1F = 127/01/31 |  | Status parameters | R | UINT (Unsigned16) | 1 |  | 0 ... 65535 | [Mdb NET CRC errors] (M2EC) | [Modbus HMI Diag] (MDH)
LCM | Level control mode | 16#40F6 = 16630 | 16#2088/1F | 16#B4/01/1F = 180/01/31 | LCM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Deactivated] NO |  | [LevelCtrl Mode] (LCM) | [Level Control] (LCC)
PNTD | Next Destaged Pump | 16#40D3 = 16595 | 16#2087/60 | 16#B3/01/C4 = 179/01/196 | PNID | Status parameters | R | WORD (Enumeration) | - |  |  | [Next Destaged Pump] (PNTD) | [Multipump System] (MPS)
PNTS | Next Staged Pump | 16#40D2 = 16594 | 16#2087/5F | 16#B3/01/C3 = 179/01/195 | PNID | Status parameters | R | WORD (Enumeration) | - |  |  | [Next Staged Pump] (PNTS) | [Multipump System] (MPS)
SCSI | Save configuration | 16#FA50 = 64080 |  |  | SCS | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Save Configuration] (SCSI) | [Factory settings] (FCS)
DCRC | DC bus ripple configuration | 16#363C = 13884 | 16#206C/55 | 16#A6/01/55 = 166/01/85 | DCRC | Configuration and settings | R/WS | WORD (Enumeration) | - | Refer to programming manual |  | [DC Bus Ripple Config] (DCRC) | [Input Filter] (DCR)
FWCL | Abort firmware update | 16#FFD5 = 65493 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [Abort Firmware Update] (FWCL) | [Firmware update] (FWUP)
DCRD | DC bus ripple time counter | 16#363B = 13883 | 16#206C/54 | 16#A6/01/54 = 166/01/84 |  | Status parameters | R | UINT (Unsigned16) | 1 h |  | 0 h ... 65535 h | [DC Bus Rip Counter] (DCRD) | [Input Filter] (DCR)
RCRP | RCI round number | 16#366C = 13932 | 16#206D/21 | 16#A6/01/85 = 166/01/133 |  | Configuration and settings | R/WS | INT (Signed16) | 1 | RCSP_AUTO | -1 ... 32767 | [RCI Round Nb] (RCRP) | [Motor tune] (MTU)
D59D | DI59 delay | 16#0FD1 = 4049 | 16#200A/32 | 16#75/01/32 = 117/01/50 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI59 delay] (D59D) | [DI59 configuration] (DI59)
RWPO | Reset Option Web Password | 16#FBD9 = 64473 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Reset OptWeb Pwd] (RWPO) | [Webserver] (WBS)
RWPE | Reset Embedded Web | 16#FBA7 = 64423 |  |  | N_Y | Configuration and settings | R | WORD (Enumeration) | - |  |  | [Reset EmbWeb] (RWPE) | [Webserver] (WBS)
CFMA | Cabinet circuit A monitoring type | 16#4154 = 16724 | 16#2089/19 | 16#B4/01/7D = 180/01/125 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit A Monitor] (CFMA) | [Cabinet circuit A] (CCMA)
CFMB | Cabinet circuit B monitoring type | 16#4155 = 16725 | 16#2089/1A | 16#B4/01/7E = 180/01/126 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit B Monitor] (CFMB) | [Cabinet circuit B ] (CCMB)
CFMC | Cabinet circuit C monitoring type | 16#4156 = 16726 | 16#2089/1B | 16#B4/01/7F = 180/01/127 | IFM | Configuration and settings | R/WS | WORD (Enumeration) | - | [Always active] ALL |  | [CabinetCircuit C Monitor] (CFMC) | [Cabinet circuit C] (CCMC)
P3OT | Pump 3 running time | 16#40C0 = 16576 | 16#2087/4D | 16#B3/01/B1 = 179/01/177 |  | Configuration and settings | R/WS | UINT (Unsigned32) | 1 s |  | 0 s ... 4294967295 s | [Pump 3 Runtime] (P3OT) | [Multipump System] (MPS)
MPSA | Pump System architecture selection | 16#4074 = 16500 | 16#2087/1 | 16#B3/01/65 = 179/01/101 | MPSA | Configuration and settings | R/WS | WORD (Enumeration) | - | [Mono-Pump] NO |  | [Pump System Archi] (MPSA) | [System Architecture] (MPQ) [System Architecture] (MPQ)
BCM | Booster Control | 16#40D8 = 16600 | 16#2088/1 | 16#B4/01/01 = 180/01/01 | N_Y | Configuration and settings | R/WS | WORD (Enumeration) | - | [No] NO |  | [Booster Control] (BCM) | [Booster Control] (BSC)
MPCP | Pump auto cycling | 16#40D7 = 16599 | 16#2087/64 | 16#B3/01/C8 = 179/01/200 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 h | 0.0 h | 0.0 h ... 24.0 h | [Pump Auto Cycling] (MPCP) | [System Architecture] (MPQ) [System Architecture] (MPQ)
TAFI | DC injection angle | 16#2903 = 10499 | 16#204A/64 | 16#95/01/64 = 149/01/100 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ° | 0 ° | 0 ° ... 360 ° | [DC injection angle] (TAFI) | [Mot. ctrl hidden menu] (MCW)
ICFG | iPAR local configuration | 16#FB14 = 64276 |  |  | N_Y | Configuration and settings | R/W | WORD (Enumeration) | - | [No] NO |  | [iPar Local Conf] (ICFG) | [Profinet] (PNC)
BDD | Booster destage delay | 16#40E6 = 16614 | 16#2088/F | 16#B4/01/0F = 180/01/15 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 10.0 s | 0.0 s ... 999.9 s | [Booster Dstg Delay] (BDD) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
BDF | Booster destage flow | 16#40E9 = 16617 | 16#2088/12 | 16#B4/01/12 = 180/01/18 |  | Configuration and settings | R/W | UINT (Unsigned16) | Refer to programming manual | 0 | 0 ... 32767 | [Booster Dstg Flow] (BDF) | [Stage/Destage Cond.] (SDCM) [Settings] (SET)
BSBS | Booster stage bypass speed | 16#40ED = 16621 | 16#2088/16 | 16#B4/01/16 = 180/01/22 |  | Configuration and settings | R/W | INT (Signed16) | 0.1 Hz | Refer to programming manual | 0.0 Hz ... 500.0 Hz | [Booster Stg Bypass Spd] (BSBS) | [Stage/Destage Meth.] (SDMM) [Settings] (SET)
MPMD | Multi-pump master activation delay | 16#409C = 16540 | 16#2087/29 | 16#B3/01/8D = 179/01/141 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 s | 0.0 s | 0.0 s ... 99.9 s | [Master Act Delay] (MPMD) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
MPMA | Multi-pump master activated assignment | 16#4092 = 16530 | 16#2087/1F | 16#B3/01/83 = 179/01/131 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Master Active Assign] (MPMA) | [Multidrive Config] (MPVC) [Multidrive Config] (MPVC)
IFRC | Response to monitoring circuit C error | 16#417A = 16762 | 16#2089/3F | 16#B4/01/A3 = 180/01/163 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit C ErrorResp] (IFRC) | [Monitoring circuit C] (CMCC)
IFRB | Response to monitoring circuit B error | 16#4179 = 16761 | 16#2089/3E | 16#B4/01/A2 = 180/01/162 | ECFG | Configuration and settings | R/WS | WORD (Enumeration) | - | [Freewheel stop] YES |  | [MonitorCircuit B ErrorResp] (IFRB) | [Monitoring circuit B] (CMCB)
OCC | Output contactor control assignment | 16#3330 = 13104 | 16#2065/5 | 16#A2/01/69 = 162/01/105 | CSLOUT | Configuration and settings | R/WS | WORD (Enumeration) | - |  |  | [Out. Contactor Assign] (OCC) | [Output contactor cmd] (OCC)
AI3L | Analog input 3 range | 16#1184 = 4484 | 16#200E/55 | 16#77/01/55 = 119/01/85 | AIOL | Configuration and settings | R/WS | WORD (Enumeration) | - | [Positive only] POS |  | [AI3 range] (AI3L) | [PID Feedback] (FDB) [PID Feedback] (FDB) [PID Feedback] (FDB) [AI3 configuration] (AI3) [AI3 sensor config.] (ICA3) [AI3 Sensor Config.] (OCA3) [AI3 sensor config.] (IF3) [AI3 Sensor config.] (PF3) [AI3 Sensor Config.] (LCS3) [AI3 Sensor Config.] (BIF3) [AI3 Configuration] (LCA3) [AI3 Configuration] (LIF3) [AI3 Sensor config.] (SIF3) [AI3 Sensor Config.] (SOA3) [AI3 Sensor Config.] (WOA3) [AI3 Sensor Config.] (PFA3) [AI3 Installation Flow] (FIF3) [AI3 Configuration] (PPA3) [AI3 Sensor Config.] (LF3) [AI3 Sensor config.] (NPF3) [AI3 sensor config.] (IPA3) [AI3 Sensor config.] (OOA3) [AI3 sensor config.] (HIF3)
P2T | Pump 2 Type | 16#409E = 16542 | 16#2087/2B | 16#B3/01/8F = 179/01/143 | PXCT | Status parameters | R | WORD (Enumeration) | - |  |  | [Pump 2 Type] (P2T) | [Multipump System] (MPS)
D55D | DI55 delay | 16#0FCD = 4045 | 16#200A/2E | 16#75/01/2E = 117/01/46 |  | Configuration and settings | R/WS | UINT (Unsigned16) | 1 ms | 5 ms | 0 ms ... 200 ms | [DI55 delay] (D55D) | [DI55 configuration] (DI55)
DAS | Delay to open contactor | 16#332E = 13102 | 16#2065/3 | 16#A2/01/67 = 162/01/103 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.01 s | 0.10 s | 0.00 s ... 5.00 s | [Delay to open cont.] (DAS) | [Output contactor cmd] (OCC)
LRL6 | Level to start sixth pump | 16#411A = 16666 | 16#2088/43 | 16#B4/01/43 = 180/01/67 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 6th Pump Start] (LRL6) | [Level settings] (LCL) [Settings] (SET)
ULR | Upload rights | 16#1F69 = 8041 | 16#2032/2A | 16#89/01/2A = 137/01/42 | ULR | Configuration and settings | R/W | WORD (Enumeration) | - | [Upload access allowed] ULR0 |  | [Upload rights] (ULR) | [Password] (COD)
LHL3 | Level to reach third pump high speed | 16#412B = 16683 | 16#2088/54 | 16#B4/01/54 = 180/01/84 |  | Configuration and settings | R/W | UINT (Unsigned16) | 0.1 % | 0.0 % | 0.0 % ... 100.0 % | [Level 3rd Pump HSP] (LHL3) | [Level settings] (LCL) [Settings] (SET)
RTC | Alignment Rotational Torque Current | 16#3669 = 13929 | 16#206D/1E | 16#A6/01/82 = 166/01/130 |  | Configuration and settings | R/WS | INT (Signed16) | 1 % | 0 % | 0 % ... 300 % | [Rotational Torque Current] (RTC) | [Motor tune] (MTU)

## Enumerations
List ID | Value | Display | Description
ACT | 0 | [Not Done] (TAB) | Not done
| 1 | [Pending] (PEND) | Test is pending
| 2 | [In Progress] (PROG) | Test in progress
| 3 | [Error] (FAIL) | Error detected
| 4 | [Autotuning Done] (DONE) | Autotuning Done
ACTION | 0 | [No action] (NO) | No action
| 1 | [Apply Autotuning] (YES) | Apply autotuning
| 2 | [Erase Autotuning] (CLR) | Erase autotuning
ADC | 0 | [No] (NO) | No DC injection
| 1 | [Yes] (YES) | DC injection
| 2 | [Continuous] (CT) | Continuous DC injection
AIOL | 0 | [0 - 100%] (POS) | Positive only
| 1 | [+/- 100%] (POSNEG) | Positive and negative
AIOT | 1 | [Voltage] (10U) | Voltage
| 2 | [Current] (0A) | Current
| 5 | [Voltage +/-] (N10U) | AI bipolar volts selected
| 7 | [PTC MANAGEMENT] (PTC) | PTC MANAGEMENT
| 8 | [KTY] (KTY) | KTY
| 9 | [PT1000] (1PT3) | PT1000
| 10 | [PT100] (1PT2) | PT100
| 11 | [Water Prob] (LEVEL) | Water Prob
| 12 | [3 PT1000] (3PT3) | 3 PT1000
| 13 | [3 PT100] (3PT2) | 3 PT100
| 14 | [PT1000 in 3 wires] (1PT33) | PT1000 in 3 wires
| 15 | [PT100 in 3 wires] (1PT23) | PT100 in 3 wires
| 16 | [3 PT1000 in 3 wires] (3PT33) | 3 PT1000 in 3 wires
| 17 | [3 PT100 in 3 wires] (3PT23) | 3 PT100 in 3 wires
ALR | 0 | [No Warning stored] (NOA) | No Warning stored
| 1 | [Fallback Frequency] (FRF) | Fallback Frequency reaction
| 2 | [Speed Maintained] (RLS) | Speed maintained
| 3 | [Type of stop] (STT) | Type of stop
| 4 | [Ref Frequency Warning] (SRA) | Reference Frequency Warning
| 5 | [Life Cycle Warn 1] (LCA1) | Life Cycle Warning 1
| 6 | [Life Cycle Warn 2] (LCA2) | Life Cycle Warning 2
| 7 | [Dry Run Warning] (DRYA) | Dry run warning
| 8 | [Low Flow Warning] (LFA) | Low Flow Warning
| 9 | [High Flow Warning] (HFPA) | High flow warning
| 10 | [InPress Warning] (IPPA) | Inlet Pressure Warning
| 11 | [Low OutPres Warn] (OPLA) | Outlet Pressure Low warning
| 12 | [High OutPres Warn] (OPHA) | Outlet Pressure High warning
| 13 | [PumpCycle warning] (PCPA) | Pump cycle warning
| 14 | [Anti-Jam Warning] (JAMA) | Anti-Jam warning
| 15 | [Pump Low Flow ] (PLFA) | Pump Low Flow
| 16 | [LowPres Warning] (LPA) | Low pressure warning
| 17 | [Flow Limit activated] (FSA) | Flow Limit activated
| 18 | [PID error Warning] (PEE) | PID error Warning
| 19 | [PID Feedback Warn] (PFA) | PID feedback Warning
| 20 | [PID High Fdbck Warn] (PFAH) | PID High Feedback Warning
| 21 | [PID Low Fdbck Warn] (PFAL) | PID Low Feedback Warning
| 22 | [Regulation Warning] (PISH) | Regulation Warning
| 26 | [AI2 Th Warning] (TP2A) | AI2 thermal sensor warning
| 27 | [AI3 Th Warning] (TP3A) | AI3 thermal sensor warning
| 28 | [AI4 Th Warning] (TP4A) | AI4 thermal sensor warning
| 29 | [AI5 Th Warning] (TP5A) | AI5 thermal sensor warning
| 30 | [AI1 4-20 Loss Warning] (AP1) | AI1 4-20 loss Warning
| 31 | [AI2 4-20 Loss Warning] (AP2) | AI2 4-20 loss Warning
| 32 | [AI3 4-20 Loss Warning] (AP3) | AI3 4-20 loss Warning
| 33 | [AI4 4-20 Loss Warning] (AP4) | AI4 4-20 loss Warning
| 34 | [AI5 4-20 Loss Warning] (AP5) | AI5 4-20 loss Warning
| 35 | [Drive Thermal Warning] (THA) | Drive thermal state Warning
| 36 | [IGBT Thermal Warning] (TJA) | IGBT thermal Warning
| 37 | [Fan Counter Warning] (FCTA) | Fan Counter Warning
| 38 | [Fan Feedback Warning] (FFDA) | Fan Feedback Warning
| 40 | [Ext. Error Warning] (EFA) | External error warning
| 41 | [Undervoltage Warning] (USA) | Undervoltage Warning
| 42 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 43 | [Forced Run] (ERN) | Drive in forced run
| 44 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 45 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 47 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 48 | [High Speed Reached] (FLA) | High Speed Reached
| 49 | [Ref Freq High Thd reached] (RTAH) | Reference frequency high threshold reached
| 50 | [Ref Freq Low Thd reached] (RTAL) | Reference frequency low threshold reached
| 51 | [2nd Freq Thd Reached] (F2A) | 2nd Frequency Threshold Reached
| 52 | [Current Thd Reached] (CTA) | Current Threshold Reached
| 53 | [Low Current Reached] (CTAL) | Low Current Threshold Reached
| 54 | [High Torque Warning] (TTHA) | High torque Warning
| 55 | [Low Torque Warning] (TTLA) | Low torque Warning
| 56 | [Process Undld Warning] (ULA) | Process underload Warning
| 57 | [Process Overload Warning] (OLA) | Process Overload Warning
| 60 | [Drv Therm Thd reached] (TAD) | Drive thermal threshold reached
| 61 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 65 | [Power High Threshold] (PTHA) | Power high threshold reached
| 66 | [Power Low Threshold] (PTHL) | Power Low threshold reached
| 67 | [Cust Warning 1] (CAS1) | Customer Warning 1
| 68 | [Cust Warning 2] (CAS2) | Customer Warning 2
| 69 | [Cust Warning 3] (CAS3) | Customer Warning 3
| 70 | [Cust Warning 4] (CAS4) | Customer Warning 4
| 71 | [Cust Warning 5] (CAS5) | Customer Warning 5
| 72 | [AFE Mains Undervoltage ] (URA) | AFE Mains undervoltage
| 73 | [Power Cons Warning] (POWD) | Power Consumption Warning
| 74 | [Switch OutPres Warn] (OPSA) | Output Pressure High switch warning
| 75 | [Ethernet Internal Warning] (INWM) | Ethernet Internal Warning
| 78 | [MP Capacity Warn] (MPCA) | Multi-Pump available capacity warning
| 79 | [Lead Pump Warn] (MPLA) | Lead pump not available
| 80 | [High Level Warning] (LCHA) | High Level Warning
| 81 | [Low Level Warning] (LCLA) | Low Level Warning
| 82 | [Level Switch Warning] (LCWA) | Level Switch Warning
| 97 | [MonitorCircuit A Warn] (IWA) | Monitoring circuit A warning
| 98 | [MonitorCircuit B Warn] (IWB) | Monitoring circuit B warning
| 99 | [MonitorCircuit C Warn] (IWC) | Monitoring circuit C warning
| 100 | [MonitorCircuit D Warn] (IWD) | Monitoring circuit D warning
| 101 | [CabinetCircuit A Warn] (CWA) | Cabinet circuit A warning
| 102 | [CabinetCircuit B Warn] (CWB) | Cabinet circuit B warning
| 103 | [CabinetCircuit C Warn] (CWC) | Cabinet circuit C warning
| 104 | [MotorWinding A Warn] (TWA) | Motor winding A warning
| 105 | [MotorWinding B Warn] (TWB) | Motor winding B warning
| 106 | [MotorBearing A Warn] (TWC) | Motor bearing A warning
| 107 | [MotorBearing B Warn] (TWD) | Motor bearing B warning
| 108 | [Circuit Breaker Warn] (CBW) | Circuit breaker warning
| 109 | [Cab I/O 24V Warn] (P24C) | Cabinet I/O 24V missing warning
| 113 | [AFE Motor Limitation] (CLIM) | AFE Motor Limitation
| 114 | [AFE Generator Limitation] (CLIG) | AFE Generator Limitation
| 115 | [AFE Sensor thermal state] (THSA) | AFE Sensor thermal state
| 116 | [AFE IGBT thermal state] (THJA) | AFE IGBT thermal state
| 117 | [Cabinet Fan Fdbck Warn] (FFCA) | Cabinet fan feedback warning
| 118 | [Cabinet Fan Counter Warn] (FCCA) | Cabinet fan counter warning
| 119 | [Cabinet Overheat Warn] (CHA) | Cabinet overheat warning
| 120 | [CMI Jumper Warn] (CMIJ) | CMI jumper warning
| 121 | [AFE Fan Counter Warn] (FCBA) | AFE fan counter warning
| 122 | [AFE Fan Fdbck Warn] (FFBA) | AFE fan feedback warning
| 124 | [M/P Device Warn] (MPDA) | Multipump device warning
| 134 | [Temp Sens AI2 Warn] (TS2A) | Temperature sensor AI2 warning
| 135 | [Temp Sens AI3 Warn] (TS3A) | Temperature sensor AI3 warning
| 136 | [Temp Sens AI4 Warn] (TS4A) | Temperature sensor AI4 warning
| 137 | [Temp Sens AI5 Warn] (TS5A) | Temperature sensor AI5 warning
| 138 | [DC Bus Ripple Warn] (DCRW) | DC bus ripple warning
APPS | 0 | [Running ] (RUN) | Running
| 1 | [Stop] (STOP) | Stop
| 2 | [Local Mode Active] (LOCAL) | Local mode is active
| 3 | [Channel 2 Active] (OVER) | Channel 2 Active
| 4 | [Manual Mode Active] (MANU) | Manual mode is active
| 5 | [PID Active] (AUTO) | PID Active
| 6 | [Anti-Jam In progress] (AJAM) | Anti-Jam is in progress
| 7 | [Flow limit In progress] (FLIM) | Flow limit In progress
| 8 | [PipeFill In progress] (FILL) | PipeFill is in progress
| 9 | [Jockey Pump Active] (JOCKEY) | Jockey Pump is active
| 10 | [Boost In progress] (BOOST) | Boost is in progress
| 11 | [Sleep Active] (SLEEP) | Sleep mode is active
| 12 | [Priming Pump Active] (PRIM) | Priming pump is active
| 13 | [InletPres Comp Active] (COMP) | Inlet Pressure Compensation is in progress
| 15 | [Undefined] (UNDEF) | Undefined
APPT | 0 | [Generic Pump Control] (GPMP) | Generic Pump Control
| 1 | [Pump Level Control] (LEVEL) | Pump level control application
| 2 | [Pump Booster Control] (BOOST) | Pump Booster control application
| 3 | [Generic Fan Control] (FAN) | Generic fan control application
AST | 5 | [PSI align.] (PSI) | Pulse Signal Injection
| 6 | [PSIO align.] (PSIO) | Pulse Signal Injection - Optimized
| 7 | [Rotational Current Injection] (RCI) | Rotational Current Injection
| 254 | [No align.] (NO) | NO alignment
AUT | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
AVOT | 0 | [+/- 8192] (INEG) | +/- 8192
| 1 | [+/- 100%] (PNEG) | +/- 100%
BCS | 0 | [None] (NONE) | Not configured
| 1 | [Inactive] (NACT) | Inactive
| 2 | [Running] (RUN) | Running
| 3 | [Stage Pending] (STGP) | Stage Pending
| 4 | [Destage pending] (DSTGP) | Destage pending
| 5 | [Staging] (STG) | Staging
| 6 | [Destaging] (DSTG) | Destage in progress
BDCO | 38 | [50 kbps] (50K) | Baud rate 50kbps
| 52 | [125 kbps] (125K) | Baud rate 125kbps
| 60 | [250 kbps] (250K) | Baud rate 250kbps
| 68 | [500 kbps] (500K) | Baud rate 500kbps
| 76 | [1 Mbps] (1M) | Baud rate 1Mbps
BFR | 0 | [50Hz IEC] (50Hz) | 50Hz Motor frequency
| 1 | [60Hz NEMA] (60Hz) | 60Hz Motor frequency
BMP | 0 | [Stop] (STOP) | Cmd/ref clear on c/over
| 1 | [Bumpless] (BUMP) | Cmd/ref copied on c/over
| 2 | [Disabled] (DIS) | Disabled
BOA | 0 | [Inactive] (NO) | Inactive
| 1 | [Dynamic] (DYNA) | Dynamic
| 2 | [Static] (STAT) | Static
| 3 | [Constant] (CSTE) | Constant
BRA | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
| 2 | [High Torque] (DYNA) | High torque
BSDC | 0 | [Speed] (SPD) | Speed
| 1 | [Feedback] (FBK) | Feedback
| 2 | [Speed+Flow] (SPFL) | Speed+Flow
| 3 | [Feedback+Flow] (FBFL) | Feedback+Flow
| 5 | [Energy Optimized ] (OPT) | Energy Optimized
BSDM | 0 | [Speed] (BSPD)
| 1 | [Feedback] (BFBK)
| 2 | [Advanced] (ADVC)
BSP | 0 | [Standard] (BSD) | Standard ref template
| 1 | [Pedestal] (BLS) | Pedestal at LSP
| 2 | [Deadband] (BNS) | Deadband at LSP
| 4 | [Deadband at 0%] (BNS0) | Deadband at 0 speed
CAR | 0 | [No Warning Clearing] (NO) | No Warning clearing
| 1 | [Clear Event 1 Warning] (RA1) | Clear Event 1 Warning
| 2 | [Clear Event 2 Warning] (RA2) | Clear Event 2 Warning
| 3 | [Clear Event 3 Warning] (RA3) | Clear Event 3 Warning
| 4 | [Clear Event 4 Warning] (RA4) | Clear Event 4 Warning
| 5 | [Clear Event 5 Warning] (RA5) | Clear Event 5 Warning
CBS | 0 | [CB Not Configured] (NO) | Circuit breaker not configured
| 1 | [CB Invalid Config ] (CBCI) | Circuit breaker configuration invalid
| 2 | [CB In Start Pulse] (CBST) | Circuit breaker in start pulse
| 3 | [CB Not Closed] (CBNC) | Circuit breaker not closed
| 4 | [CB Open] (CBOS) | Circuit breaker open
| 5 | [CB In Stop Pulse] (CBSP) | Circuit breaker in stop pulse
| 6 | [CB Not Open] (CBNO) | Circuit breaker not open
| 7 | [CB Closed] (CBCS) | Circuit breaker closed
| 8 | [CB stop disable] (CBSD) | Circuit breaker stop is disable
CBSR | 0 | [Error] (FLT) | Error
| 1 | [Warning] (WAR) | Warning
CCA | 0 | [Not Configured] (NO) | Not Configured
| 1 | [Counter] (CPT) | Counter
| 2 | [Date and Time] (DT) | Date and Time
CCS | 0 | [Mains/Control ON] (0) | Mains or Control Supply ON
| 1 | [Mains Supply ON] (1) | Mains Supply ON
| 2 | [Drive is Running] (2) | Drive in Running State
CDX | 1 | [Terminals] (TER) | Terminal block
| 3 | [HMI] (LCC) | Local HMI
| 10 | [Modbus] (MDB) | Modbus communication
| 20 | [CANopen] (CAN) | CANopen communication
| 30 | [Com. Module] (NET) | Ext. communication Module
| 40 | [Ethernet] (ETH) | Ethernet
CFPS | 0 | [None] (NO) | Not Assigned
| 1 | [Set No.1] (CFP1) | Parameter set 1
| 2 | [Set No.2] (CFP2) | Parameter set 2
| 3 | [Set No.3] (CFP3) | Parameter set 3
CHCF | 1 | [Not separ.] (SIM) | Combined channel mode
| 2 | [Separate] (SEP) | Separated channel mode
| 3 | [I/O profile] (IO) | I/O mode
CINR | 20 | [0.001] (0001) | 0.001
| 30 | [0.01] (001) | 0.01
| 40 | [0.1] (01) | 0.1
| 50 | [1] (1) | 1
| 60 | [10] (10) | 10
CIOA | 0 | [20/70] (20) | 20/70
| 1 | [21/71] (21) | 21/71
| 2 | [100/101] (100) | 100/101
| 3 | [Unconfig.] (UNCG) | Unconfigured
CMDT | 0 | [Parameters List] (NO) | Parameters List
| 1 | [PID Feedback] (PFT) | PID Feedback Trend view
| 2 | [Outlet Pressure] (OPT) | Outlet Pressure Trend view
| 3 | [Inlet Pressure] (IPT) | Inlet Pressure Trend view
| 4 | [Installation Flow] (IFT) | Installation Flow Trend view
CNFS | 0 | [In progress] (NO) | In progress
| 1 | [Config. No.0] (CNF0) | Configuration set 1
CNL | 0 | [Terminals] (TER) | Terminal block
| 2 | [HMI] (LCC) | Local HMI
| 3 | [Modbus] (MDB) | Modbus communication 1
| 6 | [CANopen] (CAN) | CANopen communication
| 9 | [Com. Module] (NET) | Ext. communication Module
| 11 | [Ethernet Module] (ETH) | Ethernet option module
| 15 | [PC tool] (PWS) | PC tool
COFM | 0 | [Measured] (HWCOF) | Measured
| 1 | [Computed] (SWCOF) | Computed
COM1 | 0 | [R0T0] (R0T0)
| 1 | [R0T1] (R0T1)
| 2 | [R1T0] (R1T0)
| 3 | [R1T1] (R1T1)
COP | 0 | [No] (NO) | No copy
| 1 | [Reference Frequency] (SP) | Copy reference frequency
| 2 | [Command] (CD) | Copy command
| 3 | [Cmd + Ref Frequency] (ALL) | Copy command & reference frequency
CSA | 0 | [No] (NO) | Not assigned
| 1 | [AQ1 assignment] (AO1) | AQ1 assignment
| 2 | [AQ2 assignment] (AO2) | AQ2 assignment
| 129 | [Ref Frequency 1] (AIFR1) | Reference frequency 1
| 130 | [Ref Frequency 2] (AIFR2) | Reference frequency 2
| 131 | [Ref Frequency 2 Summing] (AISA2) | Reference frequency 2 Summing
| 132 | [PID feedback] (AIPIF) | PI controller feedback
| 137 | [Subtract Ref Freq 2] (AIDA2) | Subtract Reference Frequency 2
| 138 | [Manual PID ref.] (AIPIM) | Manual PID reference
| 139 | [PID Ref Frequency] (AIFPI) | PID reference frequency
| 160 | [Ref Frequency 3 Summing] (AISA3) | Reference frequency 3 Summing
| 161 | [Ref Frequency 1B] (AIFR1B) | Reference frequency 1B
| 162 | [Subtract Ref Freq 3] (AIDA3) | Subtract Reference Frequency 3
| 163 | [Forced local] (AIFLOC) | Forced loc mode channel
| 164 | [Ref Frequency 2 multiplier] (AIMA2) | Reference frequency 2 multiplier
| 165 | [Ref Frequency 3 multiplier] (AIMA3) | Reference frequency 3 multiplier
| 168 | [Virtual AI1 Channel ] (AIAIC1) | Virtual AI1 channel
| 170 | [Virtual AI2 Channel] (AIAIC2) | Virtual AI2 Channel
| 171 | [Virtual AI3 Channel] (AIAIC3) | Virtual AI3 Channel
| 205 | [External Feed Forward] (AITEFF) | External feed forward
| 340 | [InletPres Sensor] (PS1A) | Intlet Pressure sensor source
| 341 | [OutletPres Sensor] (PS2A) | Outlet Pressure sensor source
| 342 | [Inst Flow Sensor] (FS1A) | Installation flow sensor source
| 343 | [Pump Flow Sensor] (FS2A) | Pump flow sensor source
| 344 | [LevelCtrl Sensor] (LCSA) | Level Control Sensor
CSLFN | 0 | [No] (NO) | No
| 181 | [Preset Speed 1] (FNPS1) | Preset Speed 1
| 182 | [Preset Speed 2] (FNPS2) | Preset Speed 2
| 183 | [PID Ref Freq 1] (FNPR1) | PID reference frequency 1
| 184 | [PID Ref Freq 2] (FNPR2) | PID reference frequency 2
| 185 | [+speed] (FNUSP) | Increase speed
| 186 | [-speed] (FNDSP) | Decrease speed
CSLOUT | 0 | [No] (NO) | No
| 146 | [R2] (R2) | Relay R2
| 147 | [R3] (R3) | Relay R3
| 148 | [R4] (R4) | Relay R4
| 149 | [R5] (R5) | Relay R5
| 150 | [R6] (R6) | Relay R6
| 163 | [DQ11 Digital Output ] (DO11) | DQ11 Digital Output
| 164 | [DQ12 Digital Output ] (DO12) | DQ12 Digital Output
| 200 | [VSP] (VSP) | VSP
| 209 | [R60] (R60) | Relay R60
| 210 | [R61] (R61) | Relay R61
| 211 | [R62] (R62) | Relay R62
| 212 | [R63] (R63) | Relay R63
| 213 | [R64] (R64) | Relay R64
| 214 | [R65] (R65) | Relay R65
| 215 | [R66] (R66) | Relay R66
CTT | 3 | [U/F VC Standard] (STD) | U/F VC Standard motor law
| 4 | [U/F VC 5pts] (UF5) | U/F VC 5 point voltage/frequency
| 6 | [U/F VC Quad.] (UFQ) | U/F VC Quadratic
| 10 | [SYN_U VC] (SYNU) | SYN_U VC law
| 11 | [U/F VC Energy Sav.] (ECO) | U/F VC Energy Sav.
| 12 | [Reluctance Motor] (SRVC) | Reluctance Motor
DCRC | 0 | [Ignore] (NO) | Ignore monitoring
| 1 | [Warning] (WARN) | Warning triggered
| 2 | [Error] (FLT) | Error triggered
DLR | 0 | [Locked drv] (DLR0) | Drive Locked
| 1 | [Unlock. drv] (DLR1) | Drive unlocked
| 2 | [Not allowed] (DLR2) | Download not allowed
| 3 | [Lock/unlock] (DLR3) | Combined Lock/Unlock
DOTD | 0 | [Freewheel stop] (NST) | Drive freewheel stop
| 1 | [Ramp stop] (RMP) | Ramp stop
DPMA | 1 | [Master 1] (1) | Master 1
| 2 | [Master 2] (2) | Master 2
DRT | 0 | [Normal Duty] (NORMAL) | Normal duty
| 1 | [Heavy Duty] (HIGH) | High duty
DRYM | 0 | [No] (NO) | No
| 1 | [Switch] (SWT) | Switch
| 2 | [Power] (PWR) | Power
DUR | 0 | [5 minutes] (5) | 5 minutes
| 1 | [10 minutes] (10) | 10 minutes
| 2 | [30 minutes] (30) | 30 minutes
| 3 | [1 hour] (1H) | 1 hour
| 4 | [2 hours] (2H) | 2 hours
| 5 | [3 hours] (3H) | 3 hours
| 6 | [Unlimited] (CT) | Unlimited
ECFG | 0 | [Ignore] (NO) | Ignore
| 1 | [Freewheel Stop] (YES) | Freewheel stop
| 2 | [Per STT] (STT) | Per STT
| 4 | [Fallback Speed] (LFF) | Fallback speed
| 5 | [Speed maintained] (RLS) | Speed maintained
| 6 | [Ramp stop] (RMP) | Ramp stop
| 7 | [Fast stop] (FST) | Fast stop
| 8 | [DC injection] (DCI) | DC injection
EFDR | 0 | [No Error] (NO) | No error
| 1 | [Server Timeout] (TOUT) | Server timeout
| 2 | [Server No File] (SNF) | Server no file
| 3 | [Server Corrupt File] (CRPT) | Server corrupt file
| 4 | [Server Empty File] (EPTY) | Server empty file
| 5 | [Drive Invalid File] (HINV) | Drive invalid file
| 6 | [CRC Error] (CRC) | CRC error
| 7 | [Version Incompatibility] (VRM) | Version incompatibility
| 9 | [Drive No File] (HNF) | Drive no file
| 10 | [Server Reading Size] (SIZE) | Server reading Size
| 11 | [Drive Opening File] (OPEN) | Drive opening file
| 12 | [Drive Reading File] (READ) | Drive reading file
| 13 | [Incompatibility] (SCNT) | Incompatibility
| 14 | [Drive Invalid Name] (NINV) | Drive invalid name
| 15 | [Server Incorrect File Size] (FSIZ) | Server incorrect file size
| 16 | [Drive Writing File] (HWF) | Drive writing file
| 17 | [Server Writing File] (SWF) | Server writing file
EMDT | 0 | [KW Counter] (KWCT) | KW Counter
| 1 | [Instant. kW trend] (CVE) | Instantaneous kW trend
| 2 | [Daily kWh report] (HSD) | Daily kWh report
| 3 | [Weekly kWh report] (HSW) | Weekly kWh report
| 4 | [Monthly kWh report] (HSM) | Monthly kWh report
| 5 | [Yearly kWh report] (HSY) | Yearly kWh report
FCS | 0 | [No] (NO) | No
| 1 | [Recall customer parameter set 0] (REC0) | Recall customer parameter set 0
| 2 | [Recall customer parameter set 1] (REC1) | Recall customer parameter set 1
| 3 | [Recall customer parameter set 2] (REC2) | Recall customer parameter set 2
| 4 | [Recall customer parameter set 3] (REC3) | Recall customer parameter set 3
| 64 | [Recall default parameter set] (INI) | Recall default parameter set
| 71 | [Recall OEM default parameter set] (INI1) | Recall OEM default parameter set
FCSI | 0 | [Macro Config] (INI) | Macro configuration
| 2 | [Config 1] (CFG1) | Configuration 1
| 3 | [Config 2] (CFG2) | Configuration 2
| 4 | [Config 3] (CFG3) | Config 3
FDRA | 0 | [NOT ACTIVE] (IDLE) | NOT ACTIVE
| 1 | [SAVE] (SAVE) | SAVE
| 2 | [REST] (REST) | REST
FEM | 0 | [No] (NO) | Disable pump characteristics
| 1 | [HQ] (HQ) | Enable Head vs Flow curve
| 2 | [PQ] (PQ) | Activate Power vs Flow curve
FFM | 0 | [Standard] (STD) | Standard
| 1 | [Always] (RUN) | Always
| 2 | [Never] (STP) | Never
| 3 | [Economy] (ECO) | Economy
FLCM | 0 | [Inactive] (NO) | Inactive
| 1 | [Display] (MON) | Display
| 2 | [Compensation] (COMP) | Compensation
FLR | 0 | [Not Configured] (NO) | Not configured
| 1 | [Yes On Freewheel] (YES) | Yes on freewheel
| 2 | [Yes Always] (ALL) | Yes always
FOR | 2 | [8-O-1] (8O1) | 8bit odd parity 1stop bit
| 3 | [8-E-1] (8E1) | 8 bits even parity 1 stop bit
| 4 | [8-N-1] (8N1) | 8bit no parity 1stop bit
| 5 | [8-N-2] (8N2) | 8bit no parity 2stop bits
FWER | 0 | [No Error] (NO) | No error
| 1 | [Lock Error] (LOCK) | Lock error
| 2 | [Package Error] (MD5) | Package error
| 3 | [Package compatibility error] (COMP) | Package compatibility error
| 4 | [Ask error] (ASK) | Ask error
| 5 | [Reset Drive Error] (RESET) | Reset drive error
| 6 | [Conf Saving Warning] (SAVE) | Configuration saving warning
| 7 | [Conf Loading Warning] (LOAD) | Conf loading warning
| 8 | [Post Script Warning] (SCP) | Post Script warning
| 9 | [Package Description Error] (DES) | Package Description error
| 10 | [Package not found] (PKG) | Package not found
| 11 | [Power Supply error] (SPWR) | Power Supply error
| 12 | [Boot M3 error] (BTM3) | Boot M3 error
| 13 | [Boot C28 error] (BTC28) | Boot C28 error
| 14 | [M3 Error] (M3) | M3 error
| 15 | [C28 error] (C28) | C28 error
| 16 | [CPLD error] (CPLD) | CPLD error
| 17 | [Boot Power Error] (PWR) | Boot power error
| 18 | [Emb. Eth Boot Error] (EMBT) | Embedded ethernet boot error
| 19 | [Emb. Eth Error] (EMIL) | Embedded ethernet error
| 20 | [Emb. Eth Web Error] (EMWB) | Embedded ethernet WebServer error
| 21 | [Module Eth Boot Error] (OPTBT) | Module ethernet boot error
| 22 | [Module Eth Error] (OPTIL) | Module ethernet error
| 23 | [Module Eth Web Error] (OPTWB) | Module ethernet WebServer error
| 24 | [Password enabled] (PSWD) | Password enabled
| 25 | [Flash Error] (MEM) | Flash error
| 26 | [Package error] (IFO) | Package error
| 27 | [Wait] (WAIT) | Wait
FWST | 0 | [Inactive] (CHECK) | Firmware update inactive
| 1 | [PwrUpd in progress] (POWER) | Power update in progress
| 2 | [PwrUpd Pending] (PEND) | Power update pending
| 3 | [Ready] (RDY) | Firmware update ready
| 4 | [Inactive] (NO) | Firmware update inactive
| 5 | [Succeeded] (SUCCD) | Firmware update succeded
| 6 | [Update Error] (FAILED) | Update Error
| 7 | [In Progress] (PROG) | Firmware update in progress
| 8 | [Requested] (RQSTD) | Firmware update requested
| 9 | [Transfer In Progress] (TRLD) | Transfer In Progress
| 10 | [Transfer Done] (TROK) | Transfer Done
| 11 | [Package cleared] (CLEAR) | Package cleared
| 12 | [Warning] (SUCWR) | Firmware update succeded with warnings
| 13 | [Drive State Error] (FLSTA) | Drive State Error
| 14 | [Package Error] (FLPKG) | Package Error
| 15 | [Saving conf] (SAVE) | Saving current configuration
| 16 | [Post Script] (POST) | Post Script
HMIS | 0 | [Autotuning] (TUN) | Drive automatic tuning
| 1 | [In DC inject.] (DCB) | DC injection
| 2 | [Ready] (RDY) | Ready
| 3 | [Freewheel] (NST) | Freewheel stop
| 4 | [Running] (RUN) | Running
| 5 | [Accelerating] (ACC) | Accelerating
| 6 | [Decelerating] (DEC) | Decelerating
| 7 | [Current limitation] (CLI) | In current limitation
| 8 | [Fast stop] (FST) | Fast stop
| 11 | [No Mains Voltage] (NLP) | No Mains voltage
| 13 | [control.stop] (CTL) | Control stopping
| 14 | [Dec. adapt.] (OBR) | Dec ramp adaptation
| 15 | [Output cut] (SOC) | Output cut
| 17 | [Undervoltage Warning] (USA) | Undervoltage Warning
| 18 | [TC Mode Active] (TC) | TC Mode active
| 19 | [In autotest] (ST) | In autotest
| 20 | [Autotest error] (FA) | Autotest error
| 21 | [Autotest OK] (OK) | Autotest OK
| 22 | [EEprom test] (EP) | EEprom test
| 23 | [Operating State "Fault" ] (FLT) | Operating state "Fault"
| 25 | [DCP Flashing Mode] (DCP) | DCP Flashing Mode
| 30 | [STO active] (STO) | STO active
| 35 | [Energy Saving] (IDLE) | Energy Saving
| 36 | [Firmware Update] (FWUP) | Firmware Update
| 37 | [AFE Mains Undervoltage ] (URA) | AFE Mains undervoltage
IFM | 0 | [Always Active] (ALL) | Always active
| 1 | [Ready & Run State] (RRY) | Ready and Run state
| 2 | [Run State] (RUN) | Run state
INHS | 0 | [Disabled] (NO) | Disabled
| 1 | [Forced Run FW] (FRD) | Forced Run in forward direction
| 2 | [Forced Run RV] (RRS) | Forced Run in reverse direction
INR | 0 | [0.01] (001) | hundredths of seconds
| 1 | [0.1] (01) | Tenths of seconds
| 2 | [1] (1) | seconds
IPAE | 0 | [Idle State] (IDLE) | Idle State
| 1 | [Init] (INIT) | Init
| 2 | [Configuration] (CONF) | Configuration
| 3 | [Ready] (RDY) | Ready
| 4 | [Operational] (OPE) | Operational
| 5 | [Not Configured] (UCFG) | Not Configured
| 6 | [Unrecoverable Error] (UREC) | Unrecoverable error
IPM | 0 | [Fixed] (MANU) | Fixed address
| 1 | [BOOTP] (BOOTP) | BOOTP
| 2 | [DHCP] (DHCP) | DHCP
| 3 | [DCP] (DCP) | DCP
IPPM | 0 | [No] (NO) | NO
| 1 | [Warning] (ALARM) | Warning
| 2 | [Compensation] (COMP) | Compensation
JATC | 0 | [No] (NO) | No
| 1 | [Start] (START) | Start
| 2 | [Time] (TIME) | Time
| 3 | [Torque] (TORQUE) | Torque
LAC | 0 | [Basic] (BAS) | Basic access
| 1 | [Standard] (STD) | Standard access
| 3 | [Expert] (EPR) | Expert access
| 4 | [Services] (SER) | Services
LCM | 0 | [No] (NO) | Deactivated
| 1 | [Filling] (FILL) | Filling Mode
| 2 | [Emptying] (EMPTY) | Emptying Mode
LCNT | 0 | [Level Switches] (SW) | Level Switches
| 1 | [Level Sensor] (LEVEL) | Level Sensor
| 2 | [Pressure sensor] (PRES) | Pressure sensor
LCPM | 0 | [Simultaneous Stop] (COMM) | All pumps stopped simultaneously
| 1 | [Individual Stop] (INDIV) | Each pump stopped individually
LCS | 0 | [None] (NONE) | Not configured
| 1 | [Inactive] (NACT) | Inactive
| 2 | [Filling] (FILL) | Filling in progress
| 3 | [Emptying] (EMPTY) | Emptying in progress
| 4 | [Low Level] (LOW) | Low Level
| 5 | [High Level] (HIGH) | High Level
LCST | 0 | [Switches] (TRAD) | Switches
| 1 | [Standard] (BASIC) | Standard
| 2 | [Energy Optimized] (ADV) | Energy Optimized
LDD | 0 | [Distrib. Log. DISABLE] (NO) | Distribution logging disable
| 1 | [Motor Frequency] (RFR) | Motor frequency
| 2 | [Motor Current] (LCR) | Motor current
| 3 | [Motor Speed] (SPD) | Motor Speed
| 4 | [Motor Voltage] (UOP) | Motor voltage
| 5 | [Motor Mech. Power] (OPRW) | Motor mechanical power
| 6 | [Input Elec. Power] (IPRW) | Input Electrical Power
| 7 | [Output Elec. Power] (EPRW) | Output Electrical Power
| 8 | [Motor Torque] (OTR) | Motor torque
| 9 | [Mains Voltage] (ULN) | Mains Voltage
| 10 | [DC BUS Voltage] (VBUS) | DC BUS Voltage
| 11 | [PID feedback] (RPF) | PID Feedback
| 12 | [AI2 Th Value] (TH2V) | AI2 thermal value
| 13 | [AI3 Th Value] (TH3V) | AI3 thermal value
| 14 | [AI4 Th Value] (TH4V) | AI4 thermal value
| 15 | [AI5 Th Value] (TH5V) | AI5 thermal value
| 16 | [Drive Thermal State] (THD) | Drive Thermal State
| 17 | [Motor Thermal State] (THR) | Motor Thermal State
| 18 | [Installation Flow] (FS1V) | Installation Flow
| 19 | [Pump Flow] (FS2V) | Pump Flow
| 20 | [Inlet Pressure] (PS1V) | Inlet Pressure
| 21 | [Outlet Pressure] (PS2V) | Outlet Pressure
| 22 | [Energy Consum. Ind.] (ECI) | Energy consumption indicator
| 23 | [Pump efficiency] (EFY) | Pump efficiency
| 24 | [Energy Perf. Ind.] (EPI) | Energy Performance Indicator
| 25 | [Mains Current] (ILN) | Mains Current
| 26 | [Input Reactive Power] (IQRW) | Input reactive power
| 27 | [Input Power Factor] (PWF) | Input power factor
| 28 | [AI1 Th Value] (TH1V) | AI1 thermal value
| 29 | [DBR Thermal State] (THB) | DBR thermal state
LDEN | 0 | [Stop] (STOP) | Stop
| 1 | [Start] (START) | Start
| 2 | [Always] (ALWAYS) | Always
| 3 | [Reset] (RESET) | Reset
| 4 | [Clear] (CLEAR) | Clear
| 5 | [Error] (ERROR) | Error
LDST | 2 | [200 ms] (200MS) | 200 ms
| 10 | [1 second] (1S) | 1 second
| 20 | [2 seconds] (2S) | 2 seconds
| 50 | [5 seconds] (5S) | 5 seconds
LFT | 0 | [No Error] (NOF) | No error detected
| 2 | [EEPROM Control] (EEF1) | EEPROM control
| 3 | [Incorrect Configuration] (CFF) | Incorrect configuration
| 4 | [Invalid Configuration] (CFI) | Invalid configuration
| 5 | [Modbus Com Interruption] (SLF1) | Modbus communication interruption
| 6 | [Internal Link Error] (ILF) | Internal communication interruption with option module
| 7 | [Fieldbus Com Interrupt] (CNF) | Fieldbus communication interruption
| 8 | [External Error] (EPF1) | External detected error
| 9 | [Overcurrent] (OCF) | Overcurrent
| 10 | [Precharge Capacitor] (CRF1) | Precharge capacitor
| 13 | [AI2 4-20mA loss] (LFF2) | AI2 4-20mA loss
| 15 | [Input Overheating] (IHF) | Input Overheating
| 16 | [Drive Overheating] (OHF) | Drive overheating
| 17 | [Motor Overload] (OLF) | Motor overload
| 18 | [DC Bus Overvoltage] (OBF) | DC bus overvoltage
| 19 | [Supply Mains Overvoltage] (OSF) | Supply mains overvoltage
| 20 | [Single output phase loss] (OPF1) | Single output phase loss
| 21 | [Input phase loss] (PHF) | Input phase loss
| 22 | [Supply Mains UnderV] (USF) | Supply mains undervoltage
| 23 | [Motor short circuit] (SCF1) | Motor short circuit
| 24 | [Motor Overspeed] (SOF) | Motor overspeed
| 25 | [Autotuning Error] (TNF) | Autotuning detected error
| 26 | [Internal Error 1] (INF1) | Internal Error 1 (Rating)
| 27 | [Internal Error 2] (INF2) | Internal Error 2 (Soft)
| 28 | [Internal Error 3] (INF3) | Internal Error 3 (Intern Comm)
| 29 | [Internal Error 4] (INF4) | Internal Error 4 (Manufacturing)
| 30 | [EEPROM Power] (EEF2) | EEPROM power
| 32 | [Ground Short Circuit] (SCF3) | Ground short circuit
| 33 | [Output Phase Loss] (OPF2) | Output phase loss
| 34 | [CANopen Com Interrupt] (COF) | CANopen communication interruption
| 37 | [Internal Error 7] (INF7) | Internal Error 7 (Init)
| 38 | [Fieldbus Error] (EPF2) | External error detected by Fieldbus
| 40 | [Internal Error 8] (INF8) | Internal error 8 (Switching Supply)
| 42 | [PC Com Interruption] (SLF2) | PC communication interruption
| 45 | [HMI Com Interruption] (SLF3) | HMI communication interruption
| 51 | [Internal Error 9] (INF9) | Internal Error 9 (Measure)
| 52 | [Internal Error 10] (INFA) | Internal Error 10 (Mains)
| 53 | [Internal Error 11] (INFB) | Internal Error 11 (Temperature)
| 54 | [IGBT Overheating] (TJF) | IGBT overheating
| 55 | [IGBT Short Circuit] (SCF4) | IGBT short circuit
| 56 | [Motor Short Circuit] (SCF5) | Motor short circuit
| 58 | [Out Contact Closed Error] (FCF1) | Output contactor closed error
| 59 | [Out Contact Opened Error] (FCF2) | Output contactor opened error
| 60 | [Internal Error 12] (INFC) | Internal Error 12 (Internal current supply)
| 64 | [Input Contactor] (LCF) | input contactor
| 68 | [Internal Error 6] (INF6) | Internal Error 6 (Option)
| 69 | [Internal Error 14] (INFE) | Internal Error 14 (CPU)
| 71 | [AI3 4-20mA loss] (LFF3) | AI3 4-20mA loss
| 72 | [AI4 4-20mA loss] (LFF4) | AI4 4-20mA loss
| 73 | [Boards Compatibility] (HCF) | Boards compatibility
| 77 | [Conf Transfer Error] (CFI2) | Configuration transfer error
| 79 | [AI5 4-20 mA loss] (LFF5) | AI5 4-20 mA loss
| 99 | [Channel Switch Error] (CSF) | Channel switching detected error
| 100 | [Process Underload] (ULF) | Process Underload
| 101 | [Process Overload] (OLC) | Process overload
| 105 | [Angle error] (ASF) | Angle error
| 106 | [AI1 4-20 mA loss] (LFF1) | AI1 4-20 mA loss
| 107 | [Safety Function Error] (SAFF) | Safety function detected error
| 110 | [AI2 Th Level Error] (TH2F) | AI2 thermal level error
| 111 | [AI2 Thermal Sensor Error] (T2CF) | Thermal sensor error on AI2
| 112 | [AI3 Th Level Error] (TH3F) | AI3 thermal level error
| 113 | [AI3 Thermal Sensor Error] (T3CF) | Thermal sensor error on AI3
| 114 | [PumpCycle start Error ] (PCPF) | Pump Cycle start error
| 115 | [Out Pressure Low] (OPLF) | Outlet Pressure Low
| 116 | [High Flow Error] (HFPF) | High Flow error
| 117 | [Inlet Pressure Error] (IPPF) | Inlet Pressure detected error
| 119 | [Pump Low Flow Error] (PLFF) | Pump low flow detected error
| 120 | [AI4 Th Level Error] (TH4F) | AI4 thermal level error
| 121 | [AI4 Thermal Sensor Error] (T4CF) | Thermal sensor error on AI4
| 122 | [AI5 Th Level Error] (TH5F) | AI5 thermal level error
| 123 | [AI5 Thermal Sensor Error] (T5CF) | Thermal sensor error on AI5
| 124 | [Anti Jam Error] (JAMF) | Anti Jam detected error
| 125 | [Out Pressure High] (OPHF) | Outlet Pressure High
| 126 | [Dry Run Error] (DRYF) | Dry run detected error
| 127 | [PID Feedback Error] (PFMF) | PID Feedback detected error
| 128 | [Program Loading Error] (PGLF) | Program loading detected error
| 129 | [Program Running Error] (PGRF) | Program running detected error
| 130 | [Lead Pump Error] (MPLF) | Lead pump not available
| 131 | [Low Level Error] (LCLF) | Low Level error
| 132 | [High Level Error] (LCHF) | High Level error
| 142 | [Internal Error 16] (INFG) | Internal Error 16 (IO Module - Relay)
| 143 | [Internal Error 17] (INFH) | Internal Error 17 (IO Module - Standard)
| 144 | [Internal Error 0] (INF0) | Internal Error 0 (IPC)
| 146 | [Internal Error 13] (INFD) | Internal Error 13 (Diff Current)
| 148 | [Motor Stall Error] (STF) | Motor stall detected error
| 149 | [Internal Error 21] (INFL) | Internal Error 21 (RTC)
| 150 | [Embd Eth Com Interrupt] (ETHF) | Embedded Ethernet communication interruption
| 151 | [Internal Error 15] (INFF) | Internal Error 15 (Flash)
| 152 | [Firmware Update Error] (FWER) | Firmware Update Error
| 153 | [Internal Error 22] (INFM) | Internal Error 22 (Embedded Ethernet)
| 154 | [Internal Error 25] (INFP) | Internal Error 25 (Incompatibility CB & SW)
| 155 | [Internal Error 20] (INFK) | Internal Error 20 (option interface PCBA)
| 157 | [Internal Error 27] (INFR) | Internal Error 27 (Diagnostics CPLD)
| 158 | [Internal Error 23] (INFN) | Internal Error 23 (Module link)
| 159 | [AFE ShortCircuit error] (SCF6) | AFE ShortCircuit error
| 160 | [AFE Bus unbalancing ] (OBF2) | AFE Bus unbalancing
| 161 | [Internal Error 28] (INFS) | Internal Error 28 (AFE)
| 162 | [MonitorCircuit A Error] (IFA) | Monitoring circuit A error
| 163 | [MonitorCircuit B Error] (IFB) | Monitoring circuit B error
| 164 | [MonitorCircuit C Error] (IFC) | Monitoring circuit C error
| 165 | [MonitorCircuit D Error] (IFD) | Monitoring circuit D error
| 166 | [CabinetCircuit A Error] (CFA) | Cabinet circuit A error
| 167 | [CabinetCircuit B Error] (CFB) | Cabinet circuit B error
| 168 | [CabinetCircuit C Error] (CFC) | Cabinet circuit C error
| 169 | [MotorWinding A Error] (TFA) | Motor winding A error
| 170 | [MotorWinding B Error] (TFB) | Motor winding B error
| 171 | [MotorBearing A Error] (TFC) | Motor bearing A error
| 172 | [MotorBearing B Error] (TFD) | Motor bearing B error
| 173 | [Cabinet Overheat Error] (CHF) | Cabinet overheat error
| 174 | [AFE Mains Undervoltage ] (URF) | AFE Mains undervoltage
| 175 | [Internal Error 31] (INFV) | Internal Error 31 (Missing brick)
| 176 | [Internal Error 29] (INFT) | Internal Error 29 (Inverter)
| 177 | [Internal Error 30] (INFU) | Internal Error 30 (Rectifier)
| 179 | [AFE IGBT over-heat error] (TJF2) | AFE IGBT over-heat error
| 180 | [AFE contactor feedback error] (CRF3) | AFE contactor feedback error
| 181 | [Pre-settings Transfer Error] (CFI3) | Pre-settings transfer error
| 182 | [Circuit Breaker Error] (CBF) | Circuit breaker error
| 186 | [MultiDrive Link Error] (MDLF) | MultiDrive Link Error
| 190 | [M/P Device Error] (MPDF) | Multipump device error
| 191 | [AFE Modulation Rate Error] (ACF1) | AFE modulation rate error
| 192 | [AFE Current Control Error] (ACF2) | AFE current control error
| 193 | [Mains Freq Out Of Range] (MFF) | Mains frequency out of range
| 200 | [FDR 1 Error] (FDR1) | FDR Eth embedded error
| 201 | [FDR 2 Error] (FDR2) | FDR Eth module error
| 203 | [Cab I/O 24V Error] (P24C) | Cabinet I/O 24V missing error
| 206 | [DC Bus Ripple Error] (DCRE) | DC Bus ripple error
| 208 | [Egy Saving Exit Error] (IDLF) | Idle mode exit error
MDT | 0 | [Digital] (DEC) | Digital values
| 1 | [Bar graph] (BAR) | Bar graph
| 2 | [List] (LIST) | List of values
| 3 | [Vu Meter] (VUMET) | Vu Meter
MPC | 0 | [Mot Power] (NPR) | Nominal motor Power
| 1 | [Mot Cosinus] (COS) | Nominal motor cosinus Phi
MPDT | 0 | [Slave] (SLAVE) | Slave
| 1 | [Master] (MAST) | Master
| 2 | [Master Only] (MAST1) | Master only
| 3 | [Master or Slave] (MAST2) | Master or Slave
MPLA | 0 | [No] (NO) | Deactivated
| 1 | [Standard] (YES) | Standard alternation
| 2 | [Redundancy] (RED) | Redundancy mode
MPPC | 0 | [FIFO] (FIFO) | First In First Out
| 1 | [LIFO] (LIFO) | Last In First Out
| 2 | [Runtime] (RTIME) | Pump runtime
| 3 | [Runtime&LIFO] (RTLF) | Runtime&Last In First Out
MPS | 0 | [None] (NONE) | None
| 1 | [Ready] (READY) | Ready
| 2 | [Running] (RUN) | Running
| 3 | [Warning] (ALARM) | Warning
| 4 | [Error] (FAULT) | Error
| 5 | [Not Available] (NAVL) | Not available
MPSA | 0 | [Mono-Pump] (NO) | Mono-Pump
| 1 | [Single Drive] (VNDOL) | Single Drive
| 2 | [Multi Drives] (NVSD) | Multiple Drives
| 3 | [Multi Masters] (NVSDR) | Multiple Drives with Master redundancy
MPST | 0 | [Standard] (TMC) | Standard multipump speed control mode
| 1 | [Distributed] (DMC) | Distributed multipump speed control mode
| 2 | [Advanced] (AMC) | Advanced multipump speed control mode
| 3 | [Synchronized] (SYNC) | Synchronized multipump speed control mode
NCV | 0 | [Unknown rating] (NO) | Unknown rating
| 1 | [0.12kW] (U010) | 0.10kW - 0.2HP
| 2 | [0.18kW / 0.25Hp] (U018) | 0.18 kW / 0.25 Hp
| 3 | [0.25kW] (U025) | 0.25kW - 0.37HP
| 4 | [0.37 kW / 0.5 Hp] (U037) | 0.37 kW / 0.5 Hp
| 5 | [0.55 kW /0.75 Hp] (U055) | 0.55 kW / 0.75 Hp
| 6 | [0.75 kW / 1 Hp] (U075) | 0.75 kW / 1 Hp
| 7 | [5.5kW / 7.5HP] (U090) | 5.5kW - 7.5HP
| 8 | [1.1 kW / 1.5 Hp] (U110) | 1.1 kW / 1.5 Hp
| 9 | [1.5 kW / 2 Hp] (U150) | 1.5 kW / 2 Hp
| 10 | [1.85kW] (U185) | 1.85kW - 3HP
| 11 | [2.2 kW / 3 Hp] (U220) | 2.2 kW / 3 Hp
| 12 | [3 kW / 4HP] (U300) | 3 kW / 4HP
| 13 | [4kW / 5HP] (U370) | 3.7kW - 5HP
| 14 | [4kW / 5HP] (U400) | 4kW - 5HP
| 15 | [5.5 kW / 7.5 Hp] (U550) | 5.5 kW / 7.5 Hp
| 16 | [7.5 kW / 10 Hp] (U750) | 7.5 kW / 10 Hp
| 17 | [9kW] (U900) | 9kW - 11HP
| 18 | [11 kW / 15 Hp] (D110) | 11 kW / 15 HP
| 19 | [15 kW / 20 Hp] (D150) | 15 kW / 20 HP
| 20 | [18,5kW / 25HP] (D185) | 18.5kW - 25HP
| 21 | [22kW / 30HP] (D220) | 22kW - 30HP
| 22 | [30kW / 40HP] (D300) | 30kW - 40HP
| 23 | [37kW / 50HP] (D370) | 37kW - 50HP
| 24 | [45kW / 60HP] (D450) | 45kW - 60HP
| 25 | [55kW / 75HP] (D550) | 55kW - 75HP
| 26 | [75kW / 100HP] (D750) | 75kW - 100HP
| 27 | [90kW / 125HP] (D900) | 90kW - 125HP
| 28 | [110 kW / 150HP] (C110) | 110kW - 150HP
| 29 | [132kW / 200 HP] (C132) | 132kW - 200HP
| 30 | [160kW / 250HP] (C160) | 160kW - 250HP
| 31 | [200kW / 300HP] (C200) | 200kW - 300HP
| 32 | [220kW / 350HP] (C220) | 220kW - 350HP
| 33 | [250kW / 400HP] (C250) | 250kW - 400HP
| 34 | [280kW / 450HP] (C280) | 280kW - 450HP
| 35 | [315kW / 500HP] (C315) | 315kW - 500HP
| 36 | [355 kW / 450HP] (C355) | 355kW - 450HP
| 37 | [400kW / 600HP] (C400) | 400kW - 600HP
| 38 | [450kW / 750HP] (C450) | 450kW - 750HP
| 39 | [500kW / 800HP] (C500) | 500kW - 800HP
| 40 | [560kW / 850HP] (C560) | 560kW - 850HP
| 41 | [630kW / 900HP] (C630) | 630kW -900HP
| 42 | [710kW / 950HP] (C710) | 710kW -950HP
| 43 | [800kW / 1000HP] (C800) | 800kW - 1000HP
| 44 | [900kW / 900HP] (C900) | 900kW - 900HP
| 45 | [1000kW / 1000HP] (M100) | 1000kW - 1000HP
| 46 | [1100kW / 1100HP] (M110) | 1100kW - 1100HP
| 47 | [1200kW / 1200HP] (M120) | 1200kW - 1200HP
| 48 | [1300kW / 1300HP] (M130) | 1300kW - 1300HP
| 49 | [1400kW / 1400HP] (M140) | 1400kW - 1400HP
| 50 | [1500kW / 1500HP] (M150) | 1500kW - 1500HP
| 51 | [1600kW / 1600HP] (M160) | 1600kW - 1600HP
| 52 | [1700kW / 1700HP] (M170) | 1700kW - 1700HP
| 53 | [1800kW / 1800HP] (M180) | 1800kW - 1800HP
| 54 | [1900kW / 1900HP] (M190) | 1900kW - 1900HP
| 55 | [2000kW / 2000HP] (M200) | 2000kW - 2000HP
| 56 | [2100kW / 2100HP] (M210) | 2100kW - 2100HP
| 57 | [2200kW / 2200HP] (M220) | 2200kW - 2200HP
| 58 | [2300kW / 2300HP] (M230) | 2300kW - 2300HP
| 59 | [2400kW / 2400HP] (M240) | 2400kW - 2400HP
NMTS | 0 | [Boot] (BOOT) | On boot up
| 2 | [Stopped] (STOP) | Stopped
| 1 | [Operation] (OPE) | Operational
| 4 | [Pre-op] (POPE) | Pre operation
NPL | 0 | [1] (POS) | 1
| 1 | [0] (NEG) | 0
N_Y | 0 | [No] (NO) | No
| 1 | [Yes] (YES) | Yes
OPL | 0 | [Function Inactive] (NO) | Function inactive
| 1 | [OPF Error Triggered] (YES) | OPF error Triggered
| 2 | [No Error Triggered] (OAC) | No error triggered
OPPM | 0 | [No] (NO) | No
| 1 | [Switch] (SW) | Switch
| 2 | [Sensor] (SNSR) | Sensor
| 3 | [Both] (BOTH) | Both
OVMA | 0 | [Default] (DEFAULT) | Default
| 255 | [Full] (FULL) | Full
PCM | 0 | [No] (NO) | Disable pump characteristics
| 1 | [HQ] (HQ) | Enable Head vs Flow curve
| 2 | [PQ] (PQ) | Enable Power vs Flow curve
| 3 | [PHQ] (PHQ) | Enable Head vs Flow and Power vs Flow curves
PCPM | 0 | [No] (NO) | Pump Cycle monitoring disabled
| 1 | [Mode 1] (NORM) | Pump Cycle monitoring mode 1
| 2 | [Mode 2] (RTC) | Pump Cycle monitoring mode 2
PCS | 0 | [None] (NONE) | None
| 1 | [Inactive] (NACT) | Inactive
| 2 | [Active] (ACTIVE) | Active
| 3 | [Failed] (FAILED) | Failed
PFM | 0 | [No] (NO) | No
| 1 | [Feedback] (FBK) | Pipe-Fill on PID Feedback
| 2 | [Outlet Pressure] (PS2) | Pipe-Fill on Outlet Pressure
PHR | 0 | [ABC] (ABC) | A - B - C phase rotation
| 1 | [ACB] (ACB) | A - C - B phase rotation
PKTP | 0 | [Product] (PRD) | Product package
| 1 | [Module] (OPT) | Module package
| 2 | [Spare parts] (SPR) | Spare parts package
| 3 | [Customized] (CUS) | Customized package
| 4 | [Indus] (IND) | Indus package
PLFM | 0 | [No] (NO) | No
| 1 | [Switch] (SW) | SW
| 2 | [Flow] (Q) | Q
| 3 | [Flow vs Speed] (QN) | QN
| 5 | [No Flow Power] (NF) | NF
PMDT | 0 | [Parameters List] (NO) | Parameters List
| 1 | [Operating Time] (HOT) | Operating Time Histogram
| 2 | [Nb of Starts] (HNS) | Nb of Starts Histogram
| 3 | [Efficiency] (EFF) | Efficiency Trend view
| 4 | [Power vs Flow] (CPQ) | Power vs Flow curve
| 5 | [Head vs Flow] (CHQ) | Head vs Flow curve
| 6 | [Efficiency vs Flow] (CEQ) | Efficiency vs Flow curve
PNID | 0 | [None] (NONE) | None
| 1 | [Pump 1] (P01) | Pump 1
| 2 | [Pump 2] (P02) | Pump 2
| 3 | [Pump 3] (P03) | Pump 3
| 4 | [Pump 4] (P04) | Pump 4
| 5 | [Pump 5] (P05) | Pump 5
| 6 | [Pump 6] (P06) | Pump 6
PRFL | 0 | [Not Configured] (UNCG) | Not configured
| 1 | [1] (1) | 1
| 100 | [100] (100) | 100
| 101 | [101] (101) | 101
| 102 | [102] (102) | 102
| 106 | [106] (106) | 106
| 107 | [107] (107) | 107
PSA | 0 | [Not Configured] (NO) | Not configured
| 1 | [AI1] (AI1) | AI1 Analog input
| 2 | [AI2] (AI2) | AI2 Analog input
| 3 | [AI3] (AI3) | AI3 Analog input
| 4 | [AI4] (AI4) | AI4 Analog input
| 5 | [AI5] (AI5) | AI5 Analog input
| 129 | [Motor Current] (OCR) | Motor current
| 130 | [Motor Frequency] (OFR) | Motor frequency
| 131 | [Ramp out.] (ORP) | Ramp output
| 132 | [Motor torq.] (TRQ) | Motor torque
| 133 | [Sign. torque] (STQ) | Signed torque
| 134 | [sign ramp] (ORS) | Signed ramp
| 135 | [PID ref.] (OPS) | PID reference
| 136 | [PID feedbk] (OPF) | PID feedback
| 137 | [PID error] (OPE) | PID error
| 138 | [PID output] (OPI) | PID output
| 139 | [Motor Power] (OPR) | Motor power
| 140 | [Mot thermal] (THR) | Motor thermal state
| 141 | [Drv thermal] (THD) | Drive thermal state
| 160 | [Ref Frequency via DI] (UPDT) | Reference frequency via DI
| 163 | [Ref.Freq-Rmt.Term] (LCC) | Reference Frequency via remote terminal
| 164 | [Ref. Freq-Modbus] (MDB) | Reference Frequency via Modbus
| 167 | [Ref. Freq-CANopen] (CAN) | Reference Frequency via CANopen
| 169 | [Ref. Freq-Com. Module] (NET) | Reference Frequency via Com Module
| 171 | [Embedded Ethernet] (ETH) | Embedded Ethernet
| 173 | [Sig. o/p frq.] (OFS) | Signed output frequency
| 180 | [Motor volt.] (UOP) | Motor voltage
| 183 | [AI Virtual 1] (AIV1) | AI Virtual 1
| 185 | [AI Virtual 2] (AIV2) | AI Virtual 2
| 197 | [AI Virtual 3] (AIV3) | AI Virtual 3
| 186 | [DI5 PulseInput Assignment] (PI5) | DI5 PulseInput Assignment
| 187 | [DI6 PulseInput Assignment] (PI6) | DI6 PulseInput Assignment
| 340 | [Est. Pump Flow] (SLPF) | Estimated pump flow
| 341 | [Inlet Pressure Value] (PS1V) | Inlet Pressure Value
| 342 | [Outlet Pressure Value] (PS2V) | Outlet Pressure Value
| 343 | [Installation Flow] (FS1V) | Installation Flow value
| 346 | [Est. System Flow] (SLSF) | Estimated pump system flow
| 347 | [Est. Pump Head] (SLPH) | Estimated pump head
| 348 | [Est. Pump dP] (SLDP) | Estimated pump delta pressure
| 349 | [Est. System dP] (SLSD) | Estimated pump system delta pressure
PSL | 0 | [Not Assigned] (NO) | Not assigned
| 1 | [Operating State Fault] (FLT) | Drive in operating state "Fault"
| 2 | [Drive Running] (RUN) | Drive running
| 3 | [Output cont] (OCC) | Ouput contactor control
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 5 | [High Speed Reached] (FLA) | High speed reached
| 6 | [Current Thd Reached] (CTA) | Current threshold reached
| 7 | [Ref Freq Reached] (SRA) | Reference frequency reached
| 8 | [Motor Therm Thd reached] (TSA) | Motor thermal threshold reached
| 10 | [PID error Warning] (PEE) | PID error Warning
| 11 | [PID Feedback Warn] (PFA) | PID feedback Warning
| 12 | [AI2 4-20 Loss Warning] (AP2) | AI2 4-20 Loss Warning
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 14 | [Drv Therm Thd reached] (TAD) | Drive thermal threshold reached
| 16 | [Ref Freq High Thd reached] (RTAH) | Reference frequency high threshold reached
| 17 | [Ref Freq Low Thd reached] (RTAL) | Reference frequency low threshold reached
| 18 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 19 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 20 | [Low Current Reached] (CTAL) | Low Current Threshold Reached
| 21 | [Process Undld Warning] (ULA) | Process underload Warning
| 22 | [Process Overload Warning] (OLA) | Process Overload Warning
| 23 | [PID High Fdbck Warn] (PFAH) | PID High Feedback Warning
| 24 | [PID Low Fdbck Warn] (PFAL) | PID Low Feedback Warning
| 25 | [Regulation Warning] (PISH) | Regulation Warning
| 26 | [Forced Run] (ERN) | Forced Run
| 28 | [High Torque Warning] (TTHA) | High torque Warning
| 29 | [Low Torque Warning] (TTLA) | Low torque Warning
| 30 | [Forward] (MFRD) | Run forward
| 31 | [Reverse] (MRRS) | Run reverse
| 34 | [Ramp switching] (RP2) | Ramp switching
| 42 | [HMI cmd] (BMP) | HMI command
| 47 | [Neg Torque] (ATS) | Negative torque
| 48 | [Cnfg.0 act.] (CNF0) | Configuration 0 active
| 52 | [set 1 active] (CFP1) | Parameter set 1 active
| 53 | [set 2 active] (CFP2) | Parameter set 2 active
| 54 | [set 3 active] (CFP3) | Parameter set 3 active
| 55 | [set 4 active] (CFP4) | Parameter set 4 active
| 64 | [DC charged] (DBL) | DC bus charged
| 66 | [Power Removal State] (PRM) | Power Removal state
| 73 | [Mains Contactor] (LLC) | Mains contactor control
| 77 | [I present] (MCP) | I present
| 80 | [Warning Grp 1] (AG1) | Warning group 1
| 81 | [Warning Grp 2] (AG2) | Warning group 2
| 82 | [Warning Grp 3] (AG3) | Warning group 3
| 87 | [External Error Warning] (EFA) | External error warning
| 88 | [Undervoltage Warning ] (USA) | Undervoltage Warning
| 89 | [Preventive UnderV Active] (UPA) | Preventive undervoltage active
| 91 | [Drive Thermal Warning] (THA) | Drive thermal state Warning
| 92 | [AFE Mains Undervoltage ] (URA) | AFE Mains undervoltage
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 1
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 104 | [IGBT Thermal Warning] (TJA) | IGBT thermal Warning
| 107 | [AI3 4-20 Loss Warning] (AP3) | AI3 4-20 Loss Warning
| 108 | [AI4 4-20 Loss Warn] (AP4) | AI4 4-20 Loss Warning
| 110 | [Flow Limit Active] (FSA) | Flow Limit active
| 116 | [Function key 1] (FN1) | Graphic display Terminal function key 1
| 117 | [Function key 2] (FN2) | Graphic display Terminal function key 2
| 118 | [Function key 3] (FN3) | Graphic display Terminal function key 3
| 119 | [Function key 4] (FN4) | Graphic display Terminal function key 4
| 123 | [AI1 4-20 Loss Warning] (AP1) | AI1 4-20 loss Warning
| 127 | [Ready] (RDY) | Ready
| 128 | [Yes] (YES) | Yes
| 129 | [DI1] (LI1) | Digital Input 1
| 130 | [DI2] (LI2) | Digital Input 2
| 131 | [DI3] (LI3) | Digital Input 3
| 132 | [DI4] (LI4) | Digital Input 4
| 133 | [DI5] (LI5) | Digital Input 5
| 134 | [DI6] (LI6) | Digital Input 6
| 139 | [DI11] (LI11) | Digital Input 11
| 140 | [DI12] (LI12) | Digital Input 12
| 141 | [DI13] (LI13) | Digital Input 13
| 142 | [DI14] (LI14) | Digital Input 14
| 143 | [DI15] (LI15) | Digital Input 15
| 144 | [DI16] (LI16) | Digital Input 16
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 176 | [C100] (C100) | Bit 0 Modbus ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 192 | [C200] (C200) | Bit 0 CANopen ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 208 | [C300] (C300) | Bit 0 Com Module ctrl word
| 209 | [C301] (C301) | Bit 1 Com Module ctrl word
| 210 | [C302] (C302) | Bit 2 Com Module ctrl word
| 211 | [C303] (C303) | Bit 3 Com Module ctrl word
| 212 | [C304] (C304) | Bit 4 Com Module ctrl word
| 213 | [C305] (C305) | Bit 5 Com Module ctrl word
| 214 | [C306] (C306) | Bit 6 Com Module ctrl word
| 215 | [C307] (C307) | Bit 7 Com Module ctrl word
| 216 | [C308] (C308) | Bit 8 Com Module ctrl word
| 217 | [C309] (C309) | Bit 9 Com Module ctrl word
| 218 | [C310] (C310) | Bit 10 Com Module ctrl word
| 219 | [C311] (C311) | Bit 11 Com Module ctrl word
| 220 | [C312] (C312) | Bit 12 Com Module ctrl word
| 221 | [C313] (C313) | Bit 13 Com Module ctrl word
| 222 | [C314] (C314) | Bit 14 Com Module ctrl word
| 223 | [C315] (C315) | Bit 15 Com Module ctrl word
| 240 | [C500] (C500) | C500
| 241 | [C501] (C501) | C501
| 242 | [C502] (C502) | C502
| 243 | [C503] (C503) | C503
| 244 | [C504] (C504) | C504
| 245 | [C505] (C505) | C505
| 246 | [C506] (C506) | C506
| 247 | [C507] (C507) | C507
| 248 | [C508] (C508) | C508
| 249 | [C509] (C509) | C509
| 250 | [C510] (C510) | C510
| 251 | [C511] (C511) | C511
| 252 | [C512] (C512) | C512
| 253 | [C513] (C513) | C513
| 254 | [C514] (C514) | C514
| 255 | [C515] (C515) | C515
| 272 | [DI1 (Low level)] (L1L) | Digital input DI1 (low level)
| 273 | [DI2 (Low level)] (L2L) | Digital input DI2 (low level)
| 274 | [DI3 (Low level)] (L3L) | Digital input DI3 (low level)
| 275 | [DI4 (Low level)] (L4L) | Digital input DI4 (low level)
| 276 | [DI5 (Low level)] (L5L) | Digital input DI5 (low level)
| 277 | [DI6 (Low level)] (L6L) | Digital input DI6 (low level)
| 282 | [DI11 (Low level)] (L11L) | Digital input DI1 (low level)
| 283 | [DI12 (Low level)] (L12L) | Digital input DI12 (low level)
| 284 | [DI13 (Low level)] (L13L) | Digital input DI13 (low level)
| 285 | [DI14 (Low level)] (L14L) | Digital input DI14 (low level)
| 286 | [DI15 (Low level)] (L15L) | Digital input DI15 (low level)
| 287 | [DI16 (Low level)] (L16L) | Digital input DI16 (low level)
| 302 | [DI50 (High Level)] (D50H) | Digital Input DI50 (High level)
| 303 | [DI51 (High Level)] (D51H) | Digital Input DI51 (High level)
| 304 | [DI52 (High Level)] (D52H) | Digital Input DI52 (High level)
| 305 | [DI53 (High Level)] (D53H) | Digital Input DI53 (High level)
| 306 | [DI54 (High Level)] (D54H) | Digital Input DI54 (High level)
| 307 | [DI55 (High Level)] (D55H) | Digital Input DI55 (High level)
| 308 | [DI56 (High Level)] (D56H) | Digital Input DI56 (High level)
| 309 | [DI57 (High Level)] (D57H) | Digital Input DI57 (High level)
| 310 | [DI58 (High Level)] (D58H) | Digital Input DI58 (High level)
| 311 | [DI59 (High Level)] (D59H) | Digital Input DI59 (High level)
| 312 | [DI50 (Low level)] (D50L) | Digital input DI50 (low level)
| 313 | [DI51 (Low level)] (D51L) | Digital input DI51 (low level)
| 314 | [DI52 (Low level)] (D52L) | Digital input DI52 (low level)
| 315 | [DI53 (Low level)] (D53L) | Digital input DI53 (low level)
| 316 | [DI54 (Low level)] (D54L) | Digital input DI54 (low level)
| 317 | [DI55 (Low level)] (D55L) | Digital input DI55 (low level)
| 318 | [DI56 (Low level)] (D56L) | Digital input DI56 (low level)
| 319 | [DI57 (Low level)] (D57L) | Digital input DI57 (low level)
| 320 | [DI58 (Low level)] (D58L) | Digital input DI58 (low level)
| 321 | [DI59 (Low level)] (D59L) | Digital input DI59 (low level)
| 336 | [DC Bus Ripple Warn] (DCRW) | DC bus ripple warning
| 340 | [Jockey] (JOKY) | Jockey
| 341 | [Priming] (PRIM) | Priming
| 342 | [Anti-Jam Active] (JAMR) | Anti-Jam active
| 344 | [Pipe Fill] (FILL) | Pipe Fill
| 345 | [Priming Pump Active] (PPON) | Priming Pump active
| 346 | [Dry Run Warning] (DRYA) | Dry run warning
| 347 | [Pump Low Flow ] (PLFA) | Pump Low Flow
| 348 | [Proc High Flow Warn] (HFPA) | Process High Flow warning
| 349 | [InPress Warning] (IPPA) | Inlet Pressure Warning
| 350 | [Low OutPres Warning] (OPLA) | Outlet Pressure Low warning
| 351 | [High OutPres Warn] (OPHA) | Outlet Pressure High warning
| 352 | [Pump Cycle Warning] (PCPA) | Pump Cycle warning
| 353 | [Anti-Jam Warning] (JAMA) | Anti-Jam warning
| 354 | [Low Flow Warning] (LFA) | Low Flow Warning
| 355 | [Low Pressure Warn] (LPA) | Low pressure warning
| 356 | [Switch OutPres Warn] (OPSA) | Output Pressure High switch warning
| 357 | [Jockey Pump Active] (JPON) | Jockey Pump Active
| 358 | [Pump 1 Cmd] (MPO1) | Pump 1 command
| 359 | [Pump 2 Cmd] (MPO2) | Pump 2 command
| 360 | [Pump 3 Cmd] (MPO3) | Pump 3 command
| 361 | [Pump 4 Cmd] (MPO4) | Pump 4 command
| 362 | [Pump 5 Cmd] (MPO5) | Pump 5 command
| 363 | [Pump 6 Cmd] (MPO6) | Pump 6 command
| 364 | [MP Capacity Warn] (MPCA) | Multi-Pump available capacity warning
| 365 | [Lead Pump Warn] (MPLA) | Lead pump not available
| 366 | [High Level Warning] (LCHA) | High Level Warning
| 367 | [Low Level Warning] (LCLA) | Low Level Warning
| 368 | [Level Switch Warning] (LCWA) | Level Switch Warning
| 369 | [M/P Device Warn] (MPDA) | Multipump device warning
| 370 | [M/P Master Activated] (MPMA) | Multi-pump master activated
| 475 | [Temp Sens AI2 Warn] (TS2A) | Temperature sensor AI2 warning
| 476 | [Temp Sens AI3 Warn] (TS3A) | Temperature sensor AI3 warning
| 477 | [Temp Sens AI4 Warn] (TS4A) | Temperature sensor AI4 warning
| 478 | [Temp Sens AI5 Warn] (TS5A) | Temperature sensor AI5 warning
| 484 | [Cust Warning 5] (CAS5) | Customer Warning 5
| 488 | [Cabinet Fan Command] (FCC) | Cabinet fan command
| 489 | [CB Start Pulse] (CBEP) | Circuit Breaker start pulse
| 490 | [CB Stop Pulse] (CBDP) | Circuit Breaker stop pulse
| 491 | [Power Cons Warning] (POWD) | Power Consumption Warning
| 492 | [Warning Grp 4] (AG4) | Warning group 4
| 493 | [Warning Grp 5] (AG5) | Warning group 5
| 494 | [Fallback speed] (FRF) | Fallback speed
| 495 | [Speed Maintained] (RLS) | Speed maintained
| 496 | [Per Type of Stop] (STT) | Per type of stop
| 497 | [Life Cycle Warn 1] (LCA1) | Life Cycle Warning 1
| 498 | [Life Cycle Warn 2] (LCA2) | Life Cycle Warning 2
| 499 | [AI2 Th Warning] (TP2A) | AI2 thermal sensor warning
| 500 | [AI3 Th Warning] (TP3A) | AI3 thermal sensor warning
| 501 | [AI4 Th Warning] (TP4A) | AI4 thermal sensor warning
| 502 | [AI5 Th Warning] (TP5A) | AI5 thermal sensor warning
| 503 | [AI5 4-20 Loss Warn] (AP5) | AI5 4-20 Loss Warning
| 504 | [Fan Counter Warning] (FCTA) | Fan Counter Warning
| 505 | [Fan Feedback Warn] (FFDA) | Fan Feedback Warning
| 506 | [Power High Threshold] (PTHA) | Power High Threshold
| 507 | [Power Low Threshold] (PTHL) | Power Low Threshold
| 508 | [Cust Warning 1] (CAS1) | Customer Warning 1
| 509 | [Cust Warning 2] (CAS2) | Customer Warning 2
| 510 | [Cust Warning 3] (CAS3) | Customer Warning 3
| 511 | [Cust Warning 4] (CAS4) | Customer Warning 4
PSLIN | 0 | [Not Assigned] (NO) | Not assigned
| 123 | [AI1 4-20 Loss Warning] (AP1) | AI1 4-20 loss Warning
| 12 | [AI2 4-20 Loss Warning] (AP2) | AI2 4-20 Loss Warning
| 107 | [AI3 4-20 Loss Warning] (AP3) | AI3 4-20 Loss Warning
| 108 | [AI4 4-20 Loss Warn] (AP4) | AI4 4-20 Loss Warning
| 503 | [AI5 4-20 Loss Warn] (AP5) | AI5 4-20 Loss Warning
| 1 | [Operating State Fault] (FLT) | Drive in operating state "Fault"
| 96 | [Ref Freq Channel 1] (FR1) | Reference frequency channel 1
| 97 | [Ref Freq Channel 2] (FR2) | Reference frequency channel 2
| 100 | [ch1B active] (FR1B) | Command ch = ch 1B
| 98 | [Cmd Channel 1] (CD1) | Command channel 1
| 99 | [Cmd Channel 2] (CD2) | Command channel 1
| 128 | [Yes] (YES) | Yes
| 4 | [Mot Freq High Thd] (FTA) | Motor frequency high threshold reached
| 13 | [Mot Freq High Thd 2] (F2A) | Motor frequency high threshold 2 reached
| 18 | [Mot Freq Low Thd] (FTAL) | Motor frequency low threshold reached
| 19 | [Mot Freq Low Thd 2] (F2AL) | Motor frequency low threshold 2 reached
| 129 | [DI1] (LI1) | Digital Input 1
| 130 | [DI2] (LI2) | Digital Input 2
| 131 | [DI3] (LI3) | Digital Input 3
| 132 | [DI4] (LI4) | Digital Input 4
| 133 | [DI5] (LI5) | Digital Input 5
| 134 | [DI6] (LI6) | Digital Input 6
| 139 | [DI11] (LI11) | Digital Input 11
| 140 | [DI12] (LI12) | Digital Input 12
| 141 | [DI13] (LI13) | Digital Input 13
| 142 | [DI14] (LI14) | Digital Input 14
| 143 | [DI15] (LI15) | Digital Input 15
| 144 | [DI16] (LI16) | Digital Input 16
| 272 | [DI1 (Low level)] (L1L) | Digital input DI1 (low level)
| 273 | [DI2 (Low level)] (L2L) | Digital input DI2 (low level)
| 274 | [DI3 (Low level)] (L3L) | Digital input DI3 (low level)
| 275 | [DI4 (Low level)] (L4L) | Digital input DI4 (low level)
| 276 | [DI5 (Low level)] (L5L) | Digital input DI5 (low level)
| 277 | [DI6 (Low level)] (L6L) | Digital input DI6 (low level)
| 282 | [DI11 (Low level)] (L11L) | Digital input DI1 (low level)
| 283 | [DI12 (Low level)] (L12L) | Digital input DI12 (low level)
| 284 | [DI13 (Low level)] (L13L) | Digital input DI13 (low level)
| 285 | [DI14 (Low level)] (L14L) | Digital input DI14 (low level)
| 286 | [DI15 (Low level)] (L15L) | Digital input DI15 (low level)
| 287 | [DI16 (Low level)] (L16L) | Digital input DI16 (low level)
| 160 | [CD00] (CD00) | Bit 0 digital input ctrl word
| 161 | [CD01] (CD01) | Bit 1 digital input ctrl word
| 162 | [CD02] (CD02) | Bit 2 digital input ctrl word
| 163 | [CD03] (CD03) | Bit 3 digital input ctrl word
| 164 | [CD04] (CD04) | Bit 4 digital input ctrl word
| 165 | [CD05] (CD05) | Bit 5 digital input ctrl word
| 166 | [CD06] (CD06) | Bit 6 digital input ctrl word
| 167 | [CD07] (CD07) | Bit 7 digital input ctrl word
| 168 | [CD08] (CD08) | Bit 8 digital input ctrl word
| 169 | [CD09] (CD09) | Bit 9 digital input ctrl word
| 170 | [CD10] (CD10) | Bit10 digital input ctrl word
| 171 | [CD11] (CD11) | Bit11 digital input ctrl word
| 172 | [CD12] (CD12) | Bit12 digital input ctrl word
| 173 | [CD13] (CD13) | Bit13 digital input ctrl word
| 174 | [CD14] (CD14) | Bit14 digital input ctrl word
| 175 | [CD15] (CD15) | Bit15 digital input ctrl word
| 177 | [C101] (C101) | Bit 1 Modbus ctrl word
| 178 | [C102] (C102) | Bit 2 Modbus ctrl word
| 179 | [C103] (C103) | Bit 3 Modbus ctrl word
| 180 | [C104] (C104) | Bit 4 Modbus ctrl word
| 181 | [C105] (C105) | Bit 5 Modbus ctrl word
| 182 | [C106] (C106) | Bit 6 Modbus ctrl word
| 183 | [C107] (C107) | Bit 7 Modbus ctrl word
| 184 | [C108] (C108) | Bit 8 Modbus ctrl word
| 185 | [C109] (C109) | Bit 9 Modbus ctrl word
| 186 | [C110] (C110) | Bit 10 Modbus ctrl word
| 187 | [C111] (C111) | Bit 11 Modbus ctrl word
| 188 | [C112] (C112) | Bit 12 Modbus ctrl word
| 189 | [C113] (C113) | Bit 13 Modbus ctrl word
| 190 | [C114] (C114) | Bit 14 Modbus ctrl word
| 191 | [C115] (C115) | Bit 15 Modbus ctrl word
| 193 | [C201] (C201) | Bit 1 CANopen ctrl word
| 194 | [C202] (C202) | Bit 2 CANopen ctrl word
| 195 | [C203] (C203) | Bit 3 CANopen ctrl word
| 196 | [C204] (C204) | Bit 4 CANopen ctrl word
| 197 | [C205] (C205) | Bit 5 CANopen ctrl word
| 198 | [C206] (C206) | Bit 6 CANopen ctrl word
| 199 | [C207] (C207) | Bit 7 CANopen ctrl word
| 200 | [C208] (C208) | Bit 8 CANopen ctrl word
| 201 | [C209] (C209) | Bit 9 CANopen ctrl word
| 202 | [C210] (C210) | Bit 10 CANopen ctrl word
| 203 | [C211] (C211) | Bit 11 CANopen ctrl word
| 204 | [C212] (C212) | Bit 12 CANopen ctrl word
| 205 | [C213] (C213) | Bit 13 CANopen ctrl word
| 206 | [C214] (C214) | Bit 14 CANopen ctrl word
| 207 | [C215] (C215) | Bit 15 CANopen ctrl word
| 209 | [C301] (C301) | Bit 1 Com Module ctrl word
| 210 | [C302] (C302) | Bit 2 Com Module ctrl word
| 211 | [C303] (C303) | Bit 3 Com Module ctrl word
| 212 | [C304] (C304) | Bit 4 Com Module ctrl word
| 213 | [C305] (C305) | Bit 5 Com Module ctrl word
| 214 | [C306] (C306) | Bit 6 Com Module ctrl word
| 215 | [C307] (C307) | Bit 7 Com Module ctrl word
| 216 | [C308] (C308) | Bit 8 Com Module ctrl word
| 217 | [C309] (C309) | Bit 9 Com Module ctrl word
| 218 | [C310] (C310) | Bit 10 Com Module ctrl word
| 219 | [C311] (C311) | Bit 11 Com Module ctrl word
| 220 | [C312] (C312) | Bit 12 Com Module ctrl word
| 221 | [C313] (C313) | Bit 13 Com Module ctrl word
| 222 | [C314] (C314) | Bit 14 Com Module ctrl word
| 223 | [C315] (C315) | Bit 15 Com Module ctrl word
| 241 | [C501] (C501) | C501
| 242 | [C502] (C502) | C502
| 243 | [C503] (C503) | C503
| 244 | [C504] (C504) | C504
| 245 | [C505] (C505) | C505
| 246 | [C506] (C506) | C506
| 247 | [C507] (C507) | C507
| 248 | [C508] (C508) | C508
| 249 | [C509] (C509) | C509
| 250 | [C510] (C510) | C510
| 251 | [C511] (C511) | C511
| 252 | [C512] (C512) | C512
| 253 | [C513] (C513) | C513
| 254 | [C514] (C514) | C514
| 255 | [C515] (C515) | C515
| 302 | [DI50 (High Level)] (D50H) | Digital Input DI50 (High level)
| 303 | [DI51 (High Level)] (D51H) | Digital Input DI51 (High level)
| 304 | [DI52 (High Level)] (D52H) | Digital Input DI52 (High level)
| 305 | [DI53 (High Level)] (D53H) | Digital Input DI53 (High level)
| 306 | [DI54 (High Level)] (D54H) | Digital Input DI54 (High level)
| 307 | [DI55 (High Level)] (D55H) | Digital Input DI55 (High level)
| 308 | [DI56 (High Level)] (D56H) | Digital Input DI56 (High level)
| 309 | [DI57 (High Level)] (D57H) | Digital Input DI57 (High level)
| 310 | [DI58 (High Level)] (D58H) | Digital Input DI58 (High level)
| 311 | [DI59 (High Level)] (D59H) | Digital Input DI59 (High level)
| 312 | [DI50 (Low level)] (D50L) | Digital input DI50 (low level)
| 313 | [DI51 (Low level)] (D51L) | Digital input DI51 (low level)
| 314 | [DI52 (Low level)] (D52L) | Digital input DI52 (low level)
| 315 | [DI53 (Low level)] (D53L) | Digital input DI53 (low level)
| 316 | [DI54 (Low level)] (D54L) | Digital input DI54 (low level)
| 317 | [DI55 (Low level)] (D55L) | Digital input DI55 (low level)
| 318 | [DI56 (Low level)] (D56L) | Digital input DI56 (low level)
| 319 | [DI57 (Low level)] (D57L) | Digital input DI57 (low level)
| 320 | [DI58 (Low level)] (D58L) | Digital input DI58 (low level)
| 321 | [DI59 (Low level)] (D59L) | Digital input DI59 (low level)
PSS | 0 | [Not locked] (NACT) | Pre-settings not locked
| 1 | [Locked] (ACT) | Pre-settings locked
PSST | 0 | [No password defined] (NO) | No password defined
| 1 | [Password is unlocked] (ULK) | Password is unlocked
| 2 | [Password is locked] (LOCK) | Password is locked
PST | 0 | [Stop Key No Priority] (NO) | Stop key no priority
| 1 | [Stop Key Priority] (YES) | Stop key priority
| 2 | [Stop Key Priority All ] (ALL) | Stop key priority all CMD channels
PVIS | 0 | [Active] (ACT) | Active parameters
| 1 | [All] (ALL) | All parameters
PXCT | 0 | [Undefined] (NONE) | Undefined
| 1 | [Lead] (LEAD) | Lead pump
| 2 | [Lead or Auxiliary] (LAF) | Lead or auxiliary fixed speed pump
| 3 | [Lead or Aux. Variable] (LAV) | Lead or auxiliary variable speed pump
| 4 | [Auxiliary] (AUXF) | Auxiliary fixed speed pump
| 5 | [Auxiliary Variable] (AUXV) | Auxiliary variable speed pump
| 6 | [Error] (ERR) | Error
PXS | 0 | [None] (NONE) | Not configured
| 1 | [Not Available] (NAVL) | Not Available
| 2 | [Ready] (RDY) | Ready
| 3 | [Running] (RUN) | Running
QSTD | 2 | [Fast stop then disable voltage] (FST2) | Fast stop then disable voltage
| 6 | [Fast stop then stay in quick stop state] (FST6) | Fast stop then stay in quick stop state
RDS | 0 | [Auto] (AUTO) | Auto detected
| 1 | [10M. full] (10F) | 10Mbps full duplex
| 2 | [10M. half] (10H) | 10Mbps half duplex
| 3 | [100M. full] (100F) | 100Mbps full duplex
| 4 | [100M. half] (100H) | 100Mbps half duplex
RPR | 0 | [No] (NO) | No
| 2 | [Run Time Reset] (RTH) | Run time reset
| 3 | [Internal Run Time Reset] (RTHI) | Internal runtime reset
| 4 | [Power ON Time Reset] (PTH) | Power ON time reset
| 7 | [Reset Fan Counter] (FTH) | Reset fan counter
| 8 | [In Power ON Time Reset] (PTHI) | Internal Power ON Time Reset
| 9 | [Clear GTHI] (GTHI) | Clear GTHI
| 10 | [Clear LTHI] (LTHI) | Clear LTHI
| 11 | [Clear NSM] (NSM) | Clear NSM
| 12 | [Clear NSMI] (NSMI) | Clear NSMI
| 13 | [Clear AFE Fan] (FBAT) | Clear AFE fan operation time
| 14 | [Clear Cabinet Fan] (FCT) | Clear cabinet fan operation time
| 20 | [Efficiency MAX] (EFYK) | Efficiency MAX
| 21 | [Efficiency MIN] (EFYJ) | Efficiency MIN
| 22 | [Flow Rate MAX] (FS1K) | Flow Rate MAX
| 23 | [Flow Rate MIN] (FS1J) | Flow Rate MIN
| 24 | [Reset Total Quantity] (FS1C) | Reset total quantity
| 30 | [Clear BRTH] (BRTH) | Clear BRTH
| 31 | [Clear BRTI] (BRTI) | Clear BRTI
| 32 | [Clear AFE Power ON Time] (BPTH) | Clear AFE Power ON Time
| 33 | [Clear BPTI] (BPTI) | Clear BPTI
| 34 | [Clear AFE Nb. start] (BNSA) | Clear AFE brick number of start
| 35 | [Clear BNSI] (BNSI) | Clear BNSI
| 36 | [Clear AFE Regen Time ] (BGTH) | Clear AFE regen time
| 37 | [Clear BGTI] (BGTI) | Clear BGTI
| 38 | [Clear BLMI] (BLMI) | Clear BLMI
| 39 | [Clear BLGI] (BLGI) | Clear BLGI
| 64 | [Reset all ] (ALL) | Reset all counters
RPT | 0 | [Linear] (LIN) | Linear ramp
| 1 | [S-Ramp] (S) | S-Ramp
| 2 | [U-Ramp] (U) | U-Ramp
| 3 | [Customized] (CUS) | Ramp customized
SCS | 0 | [No] (NO) | No
| 1 | [Config 0] (STR0) | Save configuration 0
| 2 | [Config 1] (STR1) | Save configuration 1
| 3 | [Config 2] (STR2) | Save configuration 2
| 4 | [Config 3] (STR3) | Config 3
SFDR | 0 | [Initialization] (INIT) | Initialization
| 1 | [Not Active] (IDLE) | Not active
| 2 | [Operational] (OPE) | Operational
| 4 | [Ready] (RDY) | Ready
| 5 | [IP Configuration] (IPC) | IP configuration
| 7 | [Not Configured] (UNCF) | Not configured
| 8 | [Reading Configuration] (GET) | Reading configuration
| 9 | [Writing Configuration] (SET) | Writing Configuration
| 10 | [Applying Configuration] (APP) | Applying configuration
SFT | 1 | [SFR type 1] (HF1) | Switch.frequency type 1
| 2 | [SFR type 2] (HF2) | Switch.frequency type 2
SLPM | 0 | [No] (NO) | No
| 1 | [Switch] (SW) | Switch
| 2 | [Flow] (LF) | Flow
| 3 | [Speed] (SPD) | Speed
| 4 | [Power] (PWR) | Power
| 5 | [Pressure] (HP) | Pressure
| 6 | [Multiple] (OR) | Multiple
SMOT | 0 | [No info.] (NO) | No information
| 1 | [Low salient] (LLS) | Low saliency
| 2 | [Med salient] (MLS) | Medium saliency
| 3 | [High salient] (HLS) | High saliency
SOP | 6 | [6 µs] (6) | 6 µs
| 8 | [8 µs] (8) | 8 µs
| 10 | [10 µs] (10) | 10 µs
SSL | 0 | [Standard] (STD) | Standard
| 1 | [High Perf] (HPF) | High performance
STOS | 0 | [Not active] (IDLE) | Not active
| 1 | [Active] (STO) | Active
| 2 | [Error] (FLT) | Error
STP | 0 | [Inactive] (NO) | Inactive
| 1 | [Maintain DC Bus] (MMS) | Maintain DC Bus
| 2 | [Ramp Stop] (RMP) | Ramp Stop
| 4 | [Freewheel Stop] (LNF) | Locked in freewheel stop without error
STR | 0 | [No Save] (NO) | No save
| 1 | [Save to RAM] (RAM) | Save to RAM
| 2 | [Save to EEPROM] (EEP) | Save to EEPROM
STT | 0 | [On Ramp] (RMP) | On ramp
| 1 | [Fast stop] (FST) | Fast stop
| 2 | [Freewheel Stop] (NST) | Freewheel stop
| 3 | [DC injection] (DCI) | DC injection
STUN | 0 | [Default] (TAB) | Default
| 1 | [Measure] (MEAS) | Measure
| 2 | [Custom] (CUS) | Custom
SUCU | 0 | [Euro] (EURO) | Euro
| 1 | [$] (DOLLAR) | $
| 2 | [£] (POUND) | £
| 3 | [Krone] (KR) | Krone
| 4 | [Renminbi] (RMB) | Renminbi
| 5 | [Other] (OTHER) | Other
SUFR | 0 | [1 L/s] (1LS) | 1 L/s
| 1 | [0.1 l/s] (01LS) | 0.1 l/s
| 2 | [1 L/mn] (1LM) | 1 L/mn
| 3 | [1 L/h] (1LH) | 1 L/h
| 4 | [1 dm3/mn] (1DM3M) | 1 dm3/mn
| 5 | [1 m3/s] (1M3S) | 1 m3/s
| 6 | [0.1 m3/s] (01M3S) | 0.1 m3/s
| 7 | [1 m3/mn] (1M3MN) | 1 m3/mn
| 8 | [0.1 m3/mn] (01M3MN) | 0.1 m3/mn
| 9 | [1 m3/h] (1M3H) | 1 m3/h
| 10 | [0.1 m3/h] (01M3H) | 0.1 m3/h
| 11 | [1 gal/s] (1GPS) | 1 gal/s
| 12 | [1 GPM] (1GPM) | 1 GPM
| 13 | [1 gal/h] (1GPH) | 1 gal/h
| 14 | [1 ft3/s] (1CFS) | 1 ft3/s
| 15 | [1 CFM] (1CFM) | 1 CFM
| 16 | [1 SCFM] (1SCFM) | 1 SCFM
| 17 | [1 ft3/h] (1CFH) | 1 ft3/h
| 18 | [1 Kg/s] (1KGS) | 1 Kg/s
| 19 | [1 Kg/mn] (1KGM) | 1 Kg/mn
| 20 | [1 Kg/h] (1KGH) | 1 Kg/h
| 21 | [1 Lb/s] (1LBS) | 1 Lb/s
| 22 | [1 Lb/mn] (1LBM) | 1 Lb/mn
| 23 | [1 Lb/h] (1LBH) | 1 Lb/h
| 24 | [0.1 %] (01PC) | 0.1 %
| 25 | [0.1] (01WO) | 0.1
SUPR | 0 | [1 Kpa] (1KPA) | 1 Kpa
| 1 | [1 mbar] (1MBAR) | 1 mbar
| 2 | [1 Bar] (1BAR) | 1 Bar
| 3 | [0.1 Bar] (01BAR) | 0.1 Bar
| 4 | [0.01 Bar] (001BAR) | 0.01 Bar
| 5 | [1 Psi] (1PSI) | 1 Psi
| 6 | [0.1 Psi] (01PSI) | 0.1 Psi
| 7 | [1 Psig] (1PSIG) | 1 Psig
| 8 | [0.1 Psig] (01PSIG) | 0.1 Psig
| 9 | [1 inH2O] (1INH20) | 1 inH2O
| 10 | [1 inWg] (1INWG) | 1 inWg
| 11 | [1 inWC] (1INWC) | 1 inWC
| 12 | [1 ftWg] (1FTWG) | 1 ftWg
| 13 | [1 ftWc] (1FTWC) | 1 ftWc
| 14 | [1 ft] (1FT) | 1 ft
| 15 | [1 mWg] (1MWG) | 1 mWg
| 16 | [0.1 mWg] (01MWG) | 0.1 mWg
| 17 | [1 mWC] (1MWC) | 1 mWC
| 18 | [0.1 mWc] (01MWC) | 0.1 mWc
| 19 | [1 m] (1M) | 1 m
| 20 | [0.1 m ] (01M) | 0.1 m
| 21 | [1 inHg] (1INHG) | 1 inHg
| 22 | [0.1 %] (01PC) | 0.1 %
| 23 | [0.1] (01WO) | 0.1
SUTP | 0 | [0.1°C] (01C) | 0.1°C
| 1 | [0.1°F] (01F) | 0.1°F
| 2 | [0.1 %] (01PC) | 0.1 %
| 3 | [0.1] (01WO) | 0.1
TBR | 4 | [Automatic] (AUTO) | Automatic
| 8 | [300 bps] (300) | 300 bps
| 12 | [600 bps] (600) | 600 bps
| 16 | [1.2 Kbps] (1200) | 1.2 Kbps
| 20 | [2.4 Kbps] (2400) | 2.4 Kbps
| 24 | [4800 bps] (4800) | 4800 bps
| 28 | [9600 bps] (9600) | 9600 bps
| 30 | [10 Kbps] (10000) | 10 Kbps
| 32 | [19200 bps] (19200) | 19200 bps
| 34 | [20 Kbps] (20000) | 20 Kbps
| 35 | [28.8 Kbps] (28800) | 28.8 Kbps
| 36 | [38.4 Kbps] (38400) | 38.4 Kbps
| 37 | [45.45 Kbps] (45450) | 45.45 Kbps
| 38 | [50 Kbps] (50000) | 50 Kbps
| 40 | [57.6 Kbps] (57600) | 57.6 Kbps
| 41 | [76.8 Kbps] (76800)
| 42 | [93.75 Kbps] (93750) | 93.75 Kbps
| 44 | [100 Kbps] (100K) | 100 Kbps
| 48 | [115.2 Kbps] (115K2) | 115.2 Kbps
| 52 | [125 Kbps] (125K) | 125 Kbps
| 53 | [156 Kbps] (156K) | 156 Kbps
| 54 | [187.5 Kbps] (187K5) | 187.5 Kbps
| 56 | [230.4 Kbps] (230K4) | 230.4 Kbps
| 60 | [250 Kbps] (250K) | 250 Kbps
| 64 | [460.8 Kbps] (460K8) | 460.8 Kbps
| 68 | [500 Kbps] (500K) | 500 Kbps
| 69 | [625 Kbps] (625K) | 625 Kbps
| 70 | [800 Kbps] (800K) | 800 Kbps
| 72 | [921.6 Kbps] (921K6) | 921.6 Kbps
| 76 | [1 Mbps] (1M) | 1 Mbps
| 80 | [1.5 Mbps] (1M5) | 1.5 Mbps
| 81 | [2.5 Mbps] (2M5) | 2.5 Mbps
| 82 | [3 Mbps] (3M) | 3 Mbps
| 83 | [6 Mbps] (6M) | 6 Mbps
| 84 | [10 Mbps] (10M) | 10 Mbps
| 86 | [5 Mbps] (5M) | 5 Mbps
| 88 | [12 Mbps] (12M) | 12 Mbps
| 92 | [100 Mbps] (100M) | 100 Mbps
TCC | 0 | [2-Wire Control] (2C) | 2-wire control
| 1 | [3-Wire Control] (3C) | 3-wire control
TCT | 0 | [Level] (LEL) | Level
| 1 | [Transition] (TRN) | Transition
| 2 | [Level With Fwd Priority] (PFO) | Level with Forward priority
THT | 0 | [No] (NO) | No thermal monitoring
| 1 | [Self cooled] (ACL) | Self cooled motor
| 2 | [Force-cool] (FCL) | Force cooled motor
TOCT | 0 | [NA] (NA) | NA
| 1 | [PRESSURE] (PRESS) | PRESSURE
| 2 | [FLOW] (FLOW) | FLOW
| 3 | [OTHER] (OTHER) | OTHER
TUNT | 2 | [Standard] (STD) | Standard
| 3 | [Rotation] (ROT) | Rotation
TUNU | 0 | [No] (NO) | No
| 1 | [Therm mot] (TM) | Use the motor thermal evolution
TWO | 0 | [OFF] (LOW) | ModBus Word Order OFF
| 1 | [ON] (HIGH) | Modbus Word Order ON
ULR | 0 | [Permitted] (ULR0) | Upload access allowed
| 1 | [Not allowed] (ULR1) | Upload access not allow
URES | 20 | [200 Vac] (200) | 200 Vac
| 22 | [220 Vac] (220) | 220 Vac
| 23 | [230 Vac] (230) | 230 Vac
| 24 | [240 Vac] (240) | 240 Vac
| 38 | [380 Vac] (380) | 380 Vac
| 40 | [400 Vac] (400) | 400 Vac
| 44 | [440 Vac] (440) | 440 Vac
| 46 | [460 Vac] (460) | 460 Vac
| 48 | [480 Vac] (480) | 480 Vac
| 50 | [500Vac] (500) | 500Vac
| 52 | [525 Vac] (525) | 525 Vac
| 57 | [575 Vac] (575) | 575 Vac
| 60 | [600 Vac] (600) | 600 Vac
| 69 | [690 Vac] (690) | 690 Vac
USB | 0 | [Error Triggered] (0) | Error triggered
| 1 | [Error Triggered w/o Relay] (1) | Error triggered w/o relay
| 2 | [Warning Triggered] (2) | Warning Triggered
VCAL | 0 | [Unknown Voltage] (NO) | Unkown voltage
| 1 | [100-120(1)] (110M) | 100-120 V single phase
| 2 | [100-120(3)] (110T) | 100-120 V three phase
| 3 | [200-240 V single] (220M) | 200-240 V single
| 4 | [200-240 V Three] (220T) | 200-240 V three phase
| 5 | [380-500(1)] (480M) | 380-500 V single phase
| 6 | [380-500 V Three] (480T) | 380-500 V three phase
| 7 | [500-690(1)] (690M) | 500-690 V single phase
| 8 | [500-690 V Three] (690T) | 500-690 V three phase
| 9 | [600(1)] (600M) | 600 V single phase
| 10 | [600 V Three] (600T) | 600 V three phase
WUPM | 0 | [Feedback] (FBK) | Feedback
| 1 | [Error] (ERR) | Error
| 2 | [Pressure] (LP) | Pressure

## Registers
CMI |  | Bit 0 | Factory setting command (active at 1).
|  | Bit 1 | Save configuration to EEPROM non-volatile memory command (active at 1).
This Bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | Bit 2 | Reserved (= 0).
|  | Bit 3 | Reserved (= 0).
|  | Bit 4 | Reserved (= 0).
|  | Bit 5 | Reserved (= 0).
|  | Bit 6 | Reserved (= 0).
|  | Bit 7 | Reserved (= 0).
|  | Bit 8 | Reserved (= 0).
|  | Bit 9 | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0: 0.1 Hz
= 1: Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | Bit 10 | Reserved (= 0).
|  | Bit 11 | Reserved (= 0).
|  | Bit 12 | Reserved (= 0).
|  | Bit 13 | Reserved (= 0).
|  | Bit 14 | Reserved (= 0).
|  | Bit 15 | Parameter consistency check
= 0: The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
CMD | Possible values in CiA402 profile, separate or not separate mode:
CMP0 |  | Bit 0 | Switch on/Contactor command.
CMP1 |  | Bit 1 | Disable voltage/Authorization to supply AC power.
CMP2 |  | Bit 2 | Quick stop.
CMP3 |  | Bit 3 | Enable operation/Run command.
CMP4 |  | Bit 4 | Reserved (set to 0).
CMP5 |  | Bit 5 | Reserved (set to 0).
CMP6 |  | Bit 6 | Reserved (set to 0).
CMP7 |  | Bit 7 | Fault reset/error cleared on transition 0 to 1 .
CMP8 |  | Bit 8 | Halt Stop according to the [Type of stop] (Stt) parameter without leaving the Operation enabled state.
CMP9 |  | Bit 9 | Reserved (set to 0).
CMPA |  | Bit 10 | Reserved (set to 0).
CMPB |  | Bit 11 to 15 | Can be assigned to commands.
CMPC | Possible values in the IO profile on state command [2 wire] (2C).
CMPD |  | Bit 0 | Forward (on state) command
CMPE |  |  | = 0: No forward command
CMPF |  |  | = 1: Forward command
The assignment of Bit 0 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bit 0 (Cd00) is only active if the channel of this control word is active.
|  | Bit 1 to 15 | Can be assigned to commands.
Possible values in the IO profile on edge command [3 wire] (3C).
|  | Bit 0 | Stop (run authorization).
= 0: Stop
= 1: Run is authorized on a forward or reverse command
|  | Bit 1 | Forward (on 0 to 1 rising edge) command.
The assignment of Bits 0 and 1 cannot be modified. It corresponds to the assignment of the terminals. It can be switched. Bits 0 (Cd00) and 1 (Cd01) are only active if the channel of this control word is active.
|  | Bit 2 to 15 | can be assigned to commands.
ETA | Possible values in CiA402 profile, separate or not separate mode:
EP0 |  | Bit 0 | = 1: "Ready to switch on", awaiting power section line supply
EP1 |  | Bit 1 | = 1: "Switched on", ready
EP2 |  | Bit 2 | = 1: "Operation enabled", running
EP3 |  | Bit 3 | = 1: Fault detection
EP4 |  | Bit 4 | "Voltage enabled", power part connected to supply mains
EP5 |  |  | = 0: Power part not connected to supply mains
EP6 |  |  | = 1: Power part connected to supply mains
EP7 |  |  | When the drive is powered by the power section only, this bit is always at 1.
EP8 |  | Bit 5 | Bit 5: = 0: Quick stop
EP9 |  | Bit 6 | Bit 6: = 1: "Switched on disabled", power section line supply locked
EPA |  | Bit 7 | Bit 7: Warning
EPB |  |  | = 0: No warning
EPC |  |  | = 1: Warning active
EPD |  | Bit 8 | Bit 8: Reserved (= 0)
EPE |  | Bit 9 | Bit 9: Remote: command or reference via fieldbus
EPF |  |  | = 0: Command or reference given via the graphic display terminal or remote display terminal
ETAD |  |  | = 1: Command or reference via fieldbus
|  | Bit 10 | Bit 10: Target reference reached
= 0: The reference is not reached
= 1: The reference has been reached
When the drive is in speed mode, this is the reference frequency.
|  | Bit 11 | Bit 11: "Internal limit active", reference outside limits
= 0: The reference is within the limits
= 1: The reference is not within the limits
When the drive is in speed mode, the limits are defined by the [Low speed] (LSP) and [High speed] (HSP) parameters.
|  | Bit 12 | Bit 12: Reserved (= 0)
|  | Bit 13 | Bit 13: Reserved (= 0)
|  | Bit 14 | Bit 14: "Stop key", STOP via stop key
= 0: STOP key not active
= 1: Stop triggered by the STOP key on the graphic display terminal or the remote display terminal
|  | Bit 15 | Bit 15: "Direction", direction of rotation
= 0: Forward rotation at output
= 1: Reverse rotation at output
The combination of Bits 0, 1, 2, 4, 5 and 6 defines the state in the DSP 402 state chart (refer to fieldbus manuals).
ETI |  | Bit 0 | = 1: Access to the EEPROM non-volatile memory in progress
IP0 |  | Bit 1 | = 0: No parameter consistency check
IP1 |  |  | = 1: Parameter consistency check
IP2 |  | Bit 2 | = 0: The drive is not in operating state "Fault" or in operating state "Fault" and the error is active
IP3 |  |  | = 1: The drive is in operating state "Fault" and the error is no longer active (not reset))
IP4 |  | Bit 3 | Bit 3: Reserved (= 0).
IP5 |  | Bit 4 | = 1: The drive is in speed mode
IP6 |  | Bit 5 | = 1: DC injection active
IP7 |  | Bit 6 | = 0: Drive in steady state
IP8 |  |  | = 1: Drive in transient state
IP9 |  | Bit 7 | = 1: Motor thermal state threshold reached for the active motor
IPA |  | Bit 8 | = 1: DC bus overvoltage
IPB |  | Bit 9 | = 1: Acceleration active
IPC |  | Bit 10 | = 1: Deceleration active
IPD |  | Bit 11 | = 1: Current limit active
IPE |  | Bit 12 | = 1: Fast stop active
IPF |  | Bit 13 to 14 | bit 13 = 0 and bit 14 = 0: Drive controled by terminal
bit 13 = 1 and bit 14 = 0: Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1: Drive controled by Modbus
bit 13 = 1 and bit 14 = 1: Drive controled by CANopen or the network card
|  | Bit 15 | = 0: Forward operation applied before the ramp
= 1: Reverse operation applied before the ramp
CRC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | Reserved
|  | Bit 11 | = 1 : Embedded Ethernet
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
CCC |  | Bit 0 | = 1 : Terminal board
|  | Bit 1 | = 1 : Local keypad
|  | Bit 2 | = 1 : Deported keypad
|  | Bit 3 | = 1 : Modbus
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | = 1 : CANopen
|  | Bit 7 | = 1 : Terminal up-Down speed
|  | Bit 8 | = 1 : Deported keypad up-down speed
|  | Bit 9 | = 1 : COM option board
|  | Bit 10 | Reserved
|  | Bit 11 | = 1 : Embedded Ethernet
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | = 1 : Indus
|  | Bit 15 | = 1 : PowerSuite
IL1R |  | Bit 0 | "LI1" logic inputs real image
|  | Bit 1 | "LI2" logic inputs real image
|  | Bit 2 | "LI3" logic inputs real image
|  | Bit 3 | "LI4" logic inputs real image
|  | Bit 4 | "LI5" logic inputs real image
|  | Bit 5 | "LI6" logic inputs real image
|  | Bit 6 | "LI7" logic inputs real image
|  | Bit 7 | "LI8" logic inputs real image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs real image
|  | Bit 11 | "LI12" logic inputs real image
|  | Bit 12 | "LI13" logic inputs real image
|  | Bit 13 | "LI14" logic inputs real image
|  | Bit 14 | "LI15" logic inputs real image
|  | Bit 15 | "LI16" logic inputs real image
OL1R |  | Bit 0 | "R1" relay real image
|  | Bit 1 | "R2" relay real image
|  | Bit 2 | "R3" relay real image
|  | Bit 3 | "R4" relay real image
|  | Bit 4 | "R5" relay real image
|  | Bit 5 | "R6" relay real image
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | "DO1" logic outputs real image
|  | Bit 9 | "DO2" logic outputs real image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | "DO11" logic outputs real image
|  | Bit 13 | "DO12" logic outputs real image
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
CIC |  | Bit 0 | = 1: Change of rating.
|  | Bit 1 | = 1: The fielbus module has been added.
|  | Bit 2 | = 1: The fielbus module has been removed.
|  | Bit 3 | = 1: Loaded config invalid.
|  | Bit 4 | = 1: The fielbus module has been changed.
|  | Bit 5 | Reserved (=0).
|  | Bit 6 | Reserved (=0).
|  | Bit 7 | Reserved (=0).
|  | Bit 8 | = 1: The IO module has been added.
|  | Bit 9 | = 1: The IO module has been removed.
|  | Bit 10 | = 1: The IO module has been changed.
|  | Bit 11 | = 1: The encoder module has been added.
|  | Bit 12 | = 1: The encoder module has been removed.
|  | Bit 13 | = 1: The encoder module has been changed.
|  | Bit 14 | = 1: The control board has been changed.
If one of these events occurs, the drive will trigger an error [Invalid configiguration] (CFI) and then automatically restore the factory settings.
CRP0 | Bit 0 to Bit 7: Active command channels
CRP1 |  |  | =0 : The terminal board is the active channel.
CRP2 |  |  | =1 : The local keypad is the active channel.
CRP3 |  |  | =2 : The remote keypad is the active channel.
CRP4 |  |  | =3 : Modbus is the active channel.
CRP5 |  |  | =4 : Reserved
CRP6 |  |  | =5 : Reserved
CRP7 |  |  | =6 : CANopen is the active channel.
CRP8 |  |  | =7 : The terminals are the active channel in the +/- speed reference.
CRP9 |  |  | =8 : The remote keypad is the active channel (up-down speed)
CRPA |  |  | =9 : The fieldbus module is the active channel.
CRPB |  |  | =10 : Reserved
CRPC |  |  | =11 : Reserved
CRPD |  |  | =12 : Reserved
CRPE |  |  | =13 : Reserved
CRPF |  |  | =14 : Reserved
=15 : SoMove software is the active channel.
Bit 8 to Bit 15: Active reference channels
=0 : The terminals are the active channel via an analog input.
=1 : The local keypad is the active channel.
=2 : The remote keypad is the active channel.
=3 : Modbus is the active channel.
=4 : Reserved
=5 : Reserved
=6 : CANopen is the active channel.
=7 : The terminals are the active channel in the +/- speed reference.
=8 : The remote keypad is the active channel (up-down speed)
=9 : The fieldbus module is the active channel.
=10 : Reserved
=11 : Reserved
=12 : Reserved
=13 : Reserved
=14 : Reserved
=15 : SoMove software is the active channel.
FRY |  | Bit 0 | = 1 : All parameters
|  | Bit 1 | = 1 : Drive configuration
|  | Bit 2 | Reserved
|  | Bit 3 | = 1 : Motor parameters
|  | Bit 4 | = 1 : Communication menu
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | = 1 : Display menu
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | = 1 : Communication option parameters
EWE |  | Bit 0 | = 1 : Enable Web
|  | Bit 1 | = 1 : Enable Email
IL1I |  | Bit 0 | "LI1" logic inputs physical image
|  | Bit 1 | "LI2" logic inputs physical image
|  | Bit 2 | "LI3" logic inputs physical image
|  | Bit 3 | "LI4" logic inputs physical image
|  | Bit 4 | "LI5" logic inputs physical image
|  | Bit 5 | "LI6" logic inputs physical image
|  | Bit 6 | "LI7" logic inputs physical image
|  | Bit 7 | "LI8" logic inputs physical image
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | "LI11" logic inputs physical image
|  | Bit 11 | "LI12" logic inputs physical image
|  | Bit 12 | "LI13" logic inputs physical image
|  | Bit 13 | "LI14" logic inputs physical image
|  | Bit 14 | "LI15" logic inputs physical image
|  | Bit 15 | "LI16" logic inputs physical image
PEV1 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV2 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV3 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
PEV4 |  | Bit 0 | = 1 : first mapped Object
|  | Bit 1 | = 1 : second mapped Object
|  | Bit 2 | = 1 : third mapped Object
|  | Bit 3 | = 1 : fourth mapped Object
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST00 |  | Bit 0 | (JAMP) : An anti-jam request is pending
|  | Bit 1 | (JAMR) : An anti-jam sequence is running
|  | Bit 2 | (FILL) : Pipe fill sequence is running
|  | Bit 3 | (IPPC) : Inlet pressure compensation is running
|  | Bit 4 | (SLM) : Stop asked by a "sleeping" function
|  | Bit 5 | (LDA) : Low demand active (Wave 2)
|  | Bit 6 | (PPON) : Priming pump is running
|  | Bit 7 | (JPON) : Jockey pump is running
|  | Bit 8 | (SLPP) : Sleep is pending
|  | Bit 9 | (SLPB) : Sleep Boost phase is running
|  | Bit 10 | (SLP) : Application Sleeping
|  | Bit 11 | (ASLC) : Advanced Sleep Checking is active
ST02 |  | Bit 0 | (CNF0) : Configuration 1 is used
|  | Bit 8 | (CFP1) : Parameter set 1 is used
|  | Bit 9 | (CFP2) : Parameter set 2 is used
|  | Bit 10 | (CFP3) : Parameter set 3 is used
|  | Bit 11 | (CFP4) : Parameter set 4 is used
ST03 |  | Bit 0 | (FLO) : Drive in forced local mode
|  | Bit 1 | (FR2) : Reference channel is channel 2
|  | Bit 2 | (FR1B) : Reference channel is channel 1, and FR1B is used
|  | Bit 3 | (FR1) : Reference channel is channel 1 (FR1 or FR1B is used)
|  | Bit 4 | (CD1) : Command channel is channel 1
|  | Bit 5 | (CD2) : Command channel is channel 2
|  | Bit 6 | (RFC) : Reference channel : 0-> channel1, 1-> channel 2
|  | Bit 7 | (RCB) : 0: FR1, FR1B ?
|  | Bit 8 | (CCS) : Command channel : 0-> channel 1, 1-> channel 2
|  | Bit 9 | (BMP) : Bump Less Channel
ST04 |  | Bit 0 | (FLT) : Drive is in fault state
|  | Bit 1 | (AUTO) : Automatic restart attempts in progress
|  | Bit 2 | (RDY) : Drive is in ready state
|  | Bit 3 | (RUN) : A gating order is set (there is potentially current in the motor)
|  | Bit 4 | (DBL) : Powerstage is supply (DC bus charged)
|  | Bit 5 | (CTL) : Controlled stop on power loss in progress
|  | Bit 6 | (STO) : STO function activated
|  | Bit 7 | (FST) : A fast stop request is on going
|  | Bit 8 | (FRF) : Reaction on event / fallback speed
|  | Bit 9 | (RLS) : Reaction on event / maintain speed
|  | Bit 10 | (STT) : Reaction on event / Stop on STT without tripping in fault
|  | Bit 11 | (IDLE) : Stop and Go idle state (FF343)
ST05 |  | Bit 0 | (LLC) : The drive asks to close the line contactor
|  | Bit 1 | (OCC) : The drive asks to close the output contactor (Controlled downstream contactor)
|  | Bit 2 | (SOC) : The drive has detected that the output contactor is open (Uncontrolled downstream contactor)
|  | Bit 6 | (CBEP) : The drive asks to close the circuit breaker
|  | Bit 7 | (CBDP) : The drive asks to open the circuit breaker
|  | Bit 11 | (DCRW) : DC Bus Ripple Warning
ST06 |  | Bit 0 | (ACC) : Drive in acceleration
|  | Bit 1 | (DEC) : Drive in deceleration
|  | Bit 2 | (SRA) : Frequency reference reached
|  | Bit 3 | (MFRD) : Motor running in Forward
|  | Bit 4 | (MRRS) : Motor running in Reverse
|  | Bit 5 | (ATS) : Torque on the motor is negative
|  | Bit 6 | (IDC) : DC injection is running (automatic or by order)
|  | Bit 9 | (TUN) : Autotune in progress
|  | Bit 10 | (MCP) : Motor current present
|  | Bit 11 | (RP2) : Ramp switching state : 0-> ramp 1, 1-> ramp 2
ST07 |  | Bit 0 | (AG1) : One of the alarm of alarm group 1 is active
|  | Bit 1 | (AG2) : One of the alarm of alarm group 2 is active
|  | Bit 2 | (AG3) : One of the alarm of alarm group 3 is active
|  | Bit 3 | (AG4) : One of the alarm of alarm group 4 is active
|  | Bit 4 | (AG5) : One of the alarm of alarm group 5 is active
|  | Bit 8 | (LCA1) : Life Cycle Alarm 1 alarm
|  | Bit 9 | (LCA2) : Life Cycle Alarm 2 alarm
ST08 |  | Bit 0 | (DRYA) : Dry Running Alarm
|  | Bit 1 | (PLFA) : Pump Low Flow Alarm
|  | Bit 2 | (HFPA) : High Flow Alarm
|  | Bit 3 | (IPPA) : Inlet Pressure Protection Alarm
|  | Bit 4 | (OPLA) : Outlet Pressure Low Alarm
|  | Bit 5 | (OPHA) : Outlet Pressure High Alarm
|  | Bit 6 | (PCPA) : Cyclic Start Protection Alarm
|  | Bit 7 | (JAMA) : Antijam alarm is raised
|  | Bit 8 | (LFA) : Low Flow Alarm
|  | Bit 9 | (LPA) : Low pressure alarm is raised
|  | Bit 10 | (FSA) : Flow limit function activated (FL_Mode_On)
|  | Bit 11 | (OPSA) : Outlet Pressure High Switch Alarm
|  | Bit 12 | (MPCA) : Multi-pumps Capacity Alarm
|  | Bit 13 | (MPLA) : Multi-pumps Lead Alarm
|  | Bit 14 | (LCHA) : Level Control High Level Alarm
|  | Bit 15 | (LCLA) : Level Control Low Level Alarm
ST09 |  | Bit 0 | (PFA) : alarm on PID Feedback
|  | Bit 1 | (PFAH) : PID feedback high threshold reached
|  | Bit 2 | (PFAL) : PID feedback low threshold reached
|  | Bit 3 | (PISH) : PI feedback monitoring alarm is raised
|  | Bit 4 | (LCWA) : Level Control Switch Failure Alarm
|  | Bit 11 | (PEE) : alarm on PID error
ST11 |  | Bit 0 | (TP2A) : Temperature Protection AI2 Alarm
|  | Bit 1 | (TP3A) : Temperature Protection AI3 Alarm
|  | Bit 2 | (TP4A) : Temperature Protection AI4 Alarm
|  | Bit 3 | (TP5A) : Temperature Protection AI5 Alarm
|  | Bit 9 | (TS2A) : Temperature Sensor AI2 Alarm
|  | Bit 10 | (TS3A) : Temperature Sensor AI3 Alarm
|  | Bit 11 | (TS4A) : Temperature Sensor AI4 Alarm
|  | Bit 12 | (TS5A) : Temperature Sensor AI5 Alarm
ST12 |  | Bit 0 | (AP1) : 4-20 loss alarm on AI1
|  | Bit 1 | (AP2) : 4-20 loss alarm on AI2
|  | Bit 2 | (AP3) : 4-20 loss alarm on AI3
|  | Bit 3 | (AP4) : 4-20 loss alarm on AI4
|  | Bit 4 | (AP5) : 4-20 loss alarm on AI5
ST13 |  | Bit 0 | (THA) : drive overheating alarm is raised
|  | Bit 1 | (TJA) : alarm on IGBT thermal state
|  | Bit 2 | (FCTA) : Fan Counter Speed alarm
|  | Bit 3 | (FFDA) : Fan feedback alarm is raised
|  | Bit 5 | (EFA) : external alarm is raised
|  | Bit 6 | (USA) : undervoltage alarm is raised
|  | Bit 7 | (UPA) : controlled stop on power loss threshold id reached
|  | Bit 8 | (OBR) : Impossible to follow the customer ramp during deceleration
|  | Bit 9 | (URA) : Intelligent Rectifier alarm is raised
|  | Bit 10 | (ERN) : Emergency
ST14 |  | Bit 0 | (FTA) : Motor frequency high threshold 1 reached
|  | Bit 1 | (FTAL) : Motor frequency low threshold 1 reached
|  | Bit 3 | (F2AL) : Motor frequency low threshold 2 reached
|  | Bit 4 | (FLA) : HighSpeedReached function result
|  | Bit 5 | (RTAH) : Reference frequency high threshold reached
|  | Bit 6 | (RTAL) : Reference frequency low threshold reached
|  | Bit 7 | (F2A) : Motor frequency high threshold 2 reached
|  | Bit 15 | (INWM) : Ethernet Internal Warning
ST15 |  | Bit 0 | (CTA) : Motor current high threshold reached
|  | Bit 1 | (CTAL) : Motor current low threshold reached
|  | Bit 2 | (TTHA) : Motor torque high threshold reached
|  | Bit 3 | (TTLA) : Motor torque low threshold reached
|  | Bit 4 | (ULA) : Underload is detected
|  | Bit 5 | (OLA) : Overload is detected
|  | Bit 6 | (CLI) : current or torque limitation is running
|  | Bit 9 | (POWD) : Electrical Power Drift alarm
|  | Bit 10 | (PTHA) : Power high threshold reached
|  | Bit 11 | (PTHL) : Power Low threshold reached
ST16 |  | Bit 1 | (TAD) : DriveThermalThresholdReached function result
|  | Bit 2 | (TSA) : MotorThermalThresholdReached function result (motor 1)
ST17 |  | Bit 0 | (CAS1) : Customer Alarm 1 active
|  | Bit 1 | (CAS2) : Customer Alarm 2 active
|  | Bit 2 | (CAS3) : Customer Alarm 3 active
|  | Bit 3 | (CAS4) : Customer Alarm 4 active
|  | Bit 4 | (CAS5) : Customer Alarm 5 active
ST18 |  | Bit 0 | (FCBA) : AFE : Fan running time
|  | Bit 1 | (FFBA) : AFE : Fan frequency
|  | Bit 2 | (CLIM) : AFE : Current or power limitation is running in motor mode
|  | Bit 3 | (CLIG) : AFE : Current or power limitation is running in generator mode
|  | Bit 4 | (THSA) : AFE : Sensor thermal state
|  | Bit 5 | (THJA) : AFE : IGBT thermal state
|  | Bit 6 | (FFCA) : MCE : Cabinet fan alarm state
|  | Bit 7 | (FCCA) : MCE : Cabinet fan alarm running time
|  | Bit 8 | (CHA) : MCE : Cabinet over-heating alarm
|  | Bit 9 | (CMIJ) : MCE : CMI jumper is closed
ST19 |  | Bit 0 | (IWA) : IO function : Digital warning A
|  | Bit 1 | (IWB) : IO function : Digital warning B
|  | Bit 2 | (IWC) : IO function : Digital warning C
|  | Bit 3 | (IWD) : IO function : Digital warning D
|  | Bit 4 | (CWA) : IO function : Cabinet warning A
|  | Bit 5 | (CWB) : IO function : Cabinet warning B
|  | Bit 6 | (CWC) : IO function : Cabinet warning C
|  | Bit 7 | (TWA) : IO function : Thermal input warning A
|  | Bit 8 | (TWB) : IO function : Thermal input warning B
|  | Bit 9 | (TWC) : IO function : Thermal input warning C
|  | Bit 10 | (TWD) : IO function : Thermal input warning D
|  | Bit 11 | (CBW) : Circuit breaker : Error state (not in accordance to the start and stop pulse)
|  | Bit 12 | (P24C) : Cabinet IO supply (24V) missing
ILCI |  | Bit 0 | "DI50" logic inputs physical image
|  | Bit 1 | "DI51" logic inputs physical image
|  | Bit 2 | "DI52" logic inputs physical image
|  | Bit 3 | "DI53" logic inputs physical image
|  | Bit 4 | "DI54" logic inputs physical image
|  | Bit 5 | "DI55" logic inputs physical image
|  | Bit 6 | "DI56" logic inputs physical image
|  | Bit 7 | "DI57" logic inputs physical image
|  | Bit 8 | "DI58" logic inputs physical image
|  | Bit 9 | "DI59" logic inputs physical image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ILCR |  | Bit 0 | "DI50" logic inputs real image
|  | Bit 1 | "DI51" logic inputs real image
|  | Bit 2 | "DI52" logic inputs real image
|  | Bit 3 | "DI53" logic inputs real image
|  | Bit 4 | "DI54" logic inputs real image
|  | Bit 5 | "DI55" logic inputs real image
|  | Bit 6 | "DI56" logic inputs real image
|  | Bit 7 | "DI57" logic inputs real image
|  | Bit 8 | "DI58" logic inputs real image
|  | Bit 9 | "DI59" logic inputs real image
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCI |  | Bit 0 | "R60" relay physical image
|  | Bit 1 | "R61" relay physical image
|  | Bit 2 | "R62" relay physical image
|  | Bit 3 | "R63" relay physical image
|  | Bit 4 | "R64" relay physical image
|  | Bit 5 | "R65" relay physical image
|  | Bit 6 | "R66" relay physical image
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
OLCR |  | Bit 0 | "R60" relay real image
|  | Bit 1 | "R61" relay real image
|  | Bit 2 | "R62" relay real image
|  | Bit 3 | "R63" relay real image
|  | Bit 4 | "R64" relay real image
|  | Bit 5 | "R65" relay real image
|  | Bit 6 | "R66" relay real image
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
BPI0 |  | Bit 0 | Fault in power brick 1
|  | Bit 1 | Fault in power brick 2
|  | Bit 2 | Fault in power brick 3
|  | Bit 3 | Fault in power brick 4
|  | Bit 4 | Fault in power brick 5
|  | Bit 5 | Fault in power brick 6
|  | Bit 6 | Fault in power brick 7
|  | Bit 7 | Fault in power brick 8
|  | Bit 8 | Fault in power brick 9
|  | Bit 9 | Fault in power brick 10
|  | Bit 10 | Fault in power brick 11
|  | Bit 11 | Fault in power brick 12
BFI0 |  |  | Bit0 : Fault in AFE brick 1
Bit1 : Fault in AFE brick 2
Bit2 : Fault in AFE brick 3
Bit3 : Fault in AFE brick 4
Bit4 : Fault in AFE brick 5
Bit5 : Fault in AFE brick 6
Bit6 : Fault in AFE brick 7
Bit7 : Fault in AFE brick 8
Bit8 : Fault in AFE brick 9
Bit9 : Fault in AFE brick 10
Bit10 : Fault in AFE brick 11
Bit11 : Fault in AFE brick 12
CIC2 |  |  | On power-up, read CIC :
If CIC and CIC2 = 0 -> Ok
If CIC or CIC2 not 0 -> malfunction
Write FCS = "INI" to return to factory setting
|  | Bit 0 | = 1 : SFTY option card added
|  | Bit 1 | = 1 : SFTY option card removed
|  | Bit 2 | = 1 : SFTY option card changed
|  | Bit 3 | Reserved
|  | Bit 4 | Reserved
|  | Bit 5 | Reserved
|  | Bit 6 | Reserved
|  | Bit 7 | Reserved
|  | Bit 8 | Reserved
|  | Bit 9 | Reserved
|  | Bit 10 | Reserved
|  | Bit 11 | Reserved
|  | Bit 12 | Reserved
|  | Bit 13 | Reserved
|  | Bit 14 | Reserved
|  | Bit 15 | Reserved
ST20 |  | Bit 1 | (MPDA) : Master Slave : Device loss